## Sheet1
LER Number | Plant Name | Event Date | Report Date | Accession # | Title
2192013001 | Oyster Creek | 10/03/2013 | 02/06/2014 | ML14051A54 | <strong>Automatic Reactor Scram due to an Invalid Intermediate Range Monitor (IRM) Scram Signal</strong><br /><i>Abstract:&nbsp;</i>On 10/3/13 at 0643 EDT, during reactor startup, with the reactor critical and power in the intermediate range, an automatic reactor scram occurred due to an invalid (noise) intermediate range monitor (IRM) scram signal processed on both RPS trip systems. The SCRAM was caused by both Reactor Protection Systems (RPS) channels receiving simuttaneous IRM Hi-Hi signals on IRM channels 12, 13, 14, 17, and 18.<br /><br /> Testing conducted by Analysis and Measurement Services (AMS) identified low shield to ground insulation resistances on multiple channels of the IRM system. This condition allowed significant noise coupling to occur which resulted in the erratic behavior of the IRM channels that led to the full reactor SCRAM. The noise which was received by the IRM channels has been determined to be caused by a shorted SRM 22 detector. The short circuit provided a path to ground for the high voltage potential used to bias the SRM detector.<br /><br /> The root cause of the SCRAM was the susceptibility of the Intermediate Range Monitor (IRM) channels to electrical noise due to low shield to ground insulation resistance. Contributing to this event was an internal fault of Source Range Monitor (SRM) detector 22 which caused a significant amount of noise to propagate onto the IRM channels resulting in spiking. SRM-22 was replaced during a subsequent maintenance outage on November 20, 2013.<br /><br /> There were no safety consequences as a result of this event. All control rods fully inserted and plant response was as expected. This event is being reported pursuant to: 10CFR50.73(a)(2)(iv)(A) due to an automatic actuation of the Reactor Protection System (RPS).
2192013002 | Oyster Creek | 10/06/2013 | 12/05/2013 | ML14008A09 | <strong>Manual Scram due to Lowering Vacuum</strong><br /><i>Abstract:&nbsp;</i>On October 6, 2013 at approximately 1040 EDT, during a planned reactor power ascension with reactor power at approximately 20% of rated thermal power, main condenser vacuum began to lower. In accordance with the abnormal operating procedure for degrading vacuum, Operators inserted a manual scram of the reactor at 1130 EDT.<br /><br /> Following the reactor SCRAM, operations and maintenance personnel identified an approximate 1" hole on Y-1-26, 'B' Condenser Steam Inlet Expansion Joint on the south side of 'B' Condenser. It was confirmed to be an active leak and subsequently the source of condenser vacuum degradation. A temporary leak repair was performed.<br /><br /> All control rods fully inserted and plant response was as expected. This event is being reported pursuant to 10CFR50.73(a)(2)(iv)(A) due to an actuation of the Reactor Protection System (RPS).
2192013003 | Oyster Creek | 11/17/2013 | 01/16/2014 | ML14035A06 | <strong>Secondary Containment Integrity Momentarily Declared Inoperable</strong><br /><i>Abstract:&nbsp;</i>On 11/17/13 at 1725 EST station personnel simultaneously opened the inner and outer air lock doors from the Reactor Building to the reactor control enclosure (Reactor Building 23 foot elevation North West airlock). Reactor Building secondary containment integrity was momentarily declared inoperable per Technical Specification (TS) 3.5.B.2 due to both containment airlock doors being simultaneously open at the same time. Reactor Building D/P (differential pressure) remained less than negative 0.25 inches water column. The doors were immediately closed within 10 seconds and the Technical Specification condition was exited. The cause was a degraded airlock door interlock. <br /><br /> The secondary containment interlock doors were open for less than ten seconds. Based upon the short duration of the secondary containment doors being opened simultaneously, individuals present in the airlock to close the doors and that the Reactor Building D/P remained less than negative 0.25 inches water column during the course of this event, the safety function was met and this event is of low safety significance. <br /><br /> This event is being reported in accordance with 10 CFR 50.73(a)(2)(v)(C), any event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to control the release of radioactive material.
2192013004 | Oyster Creek | 12/14/2013 | 02/12/2014 | ML14055A32 | <strong>Manual Scram due to Rise in Reactor Pressure During Turbine Valve Testing</strong><br /><i>Abstract:&nbsp;</i>On 12/14/13 at approximately 0336 EST, during quarterly turbine valve testing with reactor power at 95% of rated thermal power, the plant experienced reactor pressure control abnormalities. Turbine Control Valves 2 and 3 failed closed due to the Servo Motor Feedback Support Bracket bolts backing out and falling out thereby requiring a scram. Operators initiated a manual reactor scram due to reactor pressure rising to 1042 psig which approached the scram set point.<br /><br /> These conditions were corrected during 1F33. These were determined during complex troubleshooting as the failures that drove the event. The root cause determined that the manufacturer failed to assemble the Control Valve Hydraulic Enclosure per their design.<br /><br /> There were no safety consequences impacting the plant or public safety as a result of this event. All control rods fully inserted and plant response was as expected. This event is being reported pursuant to 10CFR50.73(a)(2)(iv)(A) due to an actuation of the Reactor Protection System (RPS).
2192013005 | Oyster Creek | 12/17/2013 | 04/11/2014 | ML14118A16 | <strong>Reactor Protection System (RPS) Actuation with the Reactor in Hot Shutdown</strong><br /><i>Abstract:&nbsp;</i>On December 17, 2013 at 1958 EST, while shut down, the plant experienced a reactor SCRAM when taking the Mode Switch from REFUEL to SHUTDOWN. The jumpers required to prevent a full SCRAM for this Mode Switch change were not installed as required by procedure. The actuation was a result of the reactor mode switch being placed from the refuel position to the shutdown position without the scram bypass jumpers installed.<br /><br /> The root cause determined that an unvalidated assumption by the supervisors resulted in a reactor scram while shut down.<br /><br /> Corrective actions include evaluation on requirements, through an Out-of-box Evaluation, to ensure operators understand and can demonstrate the proper use of the human performance fundamental tools that broke down in this instance. In addition, procedures will be enhanced to clarify verification requirements.<br /><br /> There were no safety consequences impacting the plant or public safety as a result of this event. The reactor was subcritical with all rods inserted at the time of the actuation. All systems functioned as designed. This event is being reported pursuant to 10CFR50.73(a)(2)(iv)(B) due to a valid actuation of the Reactor Protection System (RPS).
2202013001 | Nine Mile Point 1 | 05/14/2013 | 07/12/2013 | ML13212A16 | <strong>Emergency Condenser 11 High Steam Flow Isolation Instrumentation Loss During Plant Startup</strong><br /><i>Abstract:&nbsp;</i>On May 14, 2013, at 1145 hrs, with the reactor in the startup mode and at 3 percent thermal power, channel 11 high steam flow instrumentation for Emergency Condenser (EC) System Loop 11 alarmed due to a gross failure trip. Gross failure is a design feature to monitor for off normal electronic instrument loop component output. The failure of channel 11 high steam flow instrumentation occurred concurrently with channel 12 inoperable, resulting in the loss of EC System Loop 11 isolation capability on high steam flow.<br><br> This event is reportable in accordance with 10 CFR 50.73(a)(2)(v)(D) as a condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident.<br><br> The cause of this event is leakage from the shared high pressure sensing line for transmitters DPT-36-06C and DPT-36-06D. The apparent cause of the leakage from the sensing line is leak by on instrument blowdown valves VLV-36-374 and VLV-89-72. Corrective actions include replacement of the instrument blowdown valves during the next refueling outage, equalizing the associated transmitters and allowing steam condensation to fill the lines, and the monitoring of output signals to ensure that the sensing lines remained full.
2202013002 | Nine Mile Point 1 | 10/22/2013 | 12/20/2013 | ML14008A09 | <strong>Unanalyzed Condition Caused by Unfused Control Room DC Ammeters</strong><br /><i>Abstract:&nbsp;</i>On October 22, 2013 it was discovered that unfused ammeter indication circuits associated with the Nine Mile Point Unit 1 (NMP1) safety-related Direct Current (DC) buses could short circuit due to a fire in the circuit cable routing. This ground fault equivalent hot short could cause the cable to self-heat and lead to secondary fires. The unanalyzed secondary fires could adversely affect safe shutdown equipment and potentially cause the loss of the ability to safely shutdown as required by 10 CFR 50 Appendix R.<br /><br /> This event is reportable in accordance with 10 CFR 50.73(a)(2)(ii)(B) as a condition that resulted in the nuclear plant being in an unanalyzed condition that significantly degraded plant safety, and 10 CFR 50.73(a)(2)(ix)(A) as a condition that as a result of a single cause could have prevented the fulfillment of a safety function for two or more trains or channels in different systems.<br /><br /> The cause of this event is that the equipment design issue was not recognized as an unacceptable configuration. The design issue is associated with an evolving industry understanding of the 10 CFR 50 Appendix R common enclosure scope.<br /><br /> Corrective actions include the isolation of the affected circuits at the DC bus in order to prevent the condition from occurring, and the development, issuance and installation of a plant modification to install fuses on the safety-related DC ammeters at NMP1 to ensure adequate circuit protection to prevent the propagation of fires in additional areas due to overcurrent conditions.
2372013001 | Dresden 2, Dresden 3 | 06/28/2013 | 12/20/2013 | ML14002A12 | <strong>Secondary Containment Inoperable due to Two Interlock Doors Being Open Simultaneously</strong><br /><i>Abstract:&nbsp;</i>On 6/28/2013, from 07:49:07 to 07:49:14, control room operators received a control room alarm indicating that the unit 2/3 emergency diesel generator (EDG) interlock doors were open simultaneously. Individuals were able to enter the interlock, from two directions, at the same time. With two interlock doors open simultaneously, Technical Specifications 3.6.4.1, Surveillance Requirement 3.6.4.1.2, was not met. With the Surveillance Requirement not met, Secondary Containment was declared inoperable, and entry into Technical Specifications 3.6.4.1 Condition A was made. The doors were immediately closed and the Technical Specifications Condition was exited.<br /><br /> Based upon the investigation performed, the failure mechanism for this event was determined to be an isolated and rare premature failure of the latch bolt monitor. Based upon the short duration of the secondary containment doors being opened simultaneously and that the Secondary Containment differential pressure remained negative during the course of this event, this event is of low safety significance.<br /><br /> This event is being reported in accordance with 10 CFR 50.73(a)(2)(v)(C), any event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to control the release of radioactive material.
2372013002 | Dresden 2 | 07/20/2013 | 09/27/2013 | ML13283A01 | <strong>Movement of Control Rods with Control Rod Block Monitor Inoperable</strong><br /><i>Abstract:&nbsp;</i>On July 20, 2013, at 1630 hours CDT, Operations personnel were performing Dresden Operating Surveillance (DOS) 0700-07, Rod Block Monitor Functional Test, for Rod Stock Monitor 8. The procedure instructed personnel to lower the Rod Block Monitor (RBM) indicated power using the PWR knob until the associated downscale indicating light illuminates which indicates a downscale trip of the monitor. However, while lowering the potentiometer, the lower stop was reached before the downscale trip was received. The malfunction was discussed and it was concluded that the inability to achieve the downscale was due to a malfunction in the testing circuitry. Therefore RBM 8 was considered operable, returned to service and was planned. Prior to troubleshooting being completed, three controls rods were withdrawn. A subsequent engineering evaluation of the RBM determined that the RBM should have been declared inoperable due a failed card on July 20, 2013. The withdrawal old control rods with the RBM inoperable, constituted a noncompliance with Limiting Condition for Operation Applicability 3.0.4. <br /><br /> Step I.24 of procedure DOS 0700-07 was not annotated as an Acceptance Criteria. This resulted in the Shift Operations personnel not recognizing that the RBM was inoperable. Therefore control rods were withdrawn while the RBM was not meeting all operability requirements. The failed card was replaced. Plant procedures are being revised to ensure that the testing of the downscale function is recognized as acceptance criteria. Additionally, the results of the event investigation are being presented to appropriate plant personnel. <br /><br /> The redundant Channel, RBM 7, was operable during this event and was capable of providing the control rod block function if the monitor settings were exceeded.<br /><br /> This event is being reported in accordance with 10 CFR 50.73(a)(2)(iX8), “Any operation or condition which was prohibited by the plants Technical Specifications."
2372013003 | Dresden 2, Dresden 3 | 09/23/2013 | 11/22/2013 | ML13338A41 | <strong>Secondary Containment Inoperable due to Two Interlock Doors Being Open Simultaneously</strong><br /><i>Abstract:&nbsp;</i>From 16:55:59 to 16:58:04 on September 23, 2013, control ram operators received a control room alarm indicating that the unit 2/3 emergency diesel generator (EDG) interlock doors were open simultaneously. Individuals were able to enter the interlock, from two directions, at the same time. With two interlock doors open simultaneously, Technical Specifications 3.6.4.1, Surveillance Requirement 3.6.4.1.2, was not met. With the Surveillance Requirement not met, Secondary Containment was declared inoperable, and entry into Technical Specifications 3.6.4.1 Condition A was made. The doors were immediately closed and the Technical Specifications Condition was exited. The apparent cause evaluation identified that the most probable cause was due to a relay malfunction.<br /><br /> Based upon the short duration of the secondary containment doors being opened simultaneously and that the Secondary Containment differential pressure remained negative during the course of this event, this event is of low safety significance.<br /><br /> This event is being reported in accordance with 10 CFR 50.73(a)(2)(v)(C), any event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to control the release of radioactive material.
2372013004 | Dresden 2, Dresden 3 | 11/05/2013 | 01/06/2014 | ML14030A04 | <strong>Secondary Containment Inoperable Due to Two Interlock Doors Being Open Simultaneously</strong><br /><i>Abstract:&nbsp;</i>On November 05, 2013, control room operators received a control room alarm indicating that the Unit 2 interlock doors were open simultaneously. A door operator operated the turbine side door hand switch allowing personnel traffic to enter the interlock. Simultaneously, the reactor building side door swung open. With two interlock doors open simultaneously, Technical Specifications 3.6.4.1, Surveillance Requirement 3.6.4.1.2, was not met. With the Surveillance Requirement not met, Secondary Containment was declared inoperable, and entry into Technical Specifications 3.6.4.1 Condition A was made. The doors were immediately closed and the Technical Specifications Condition was exited. The apparent cause evaluation identified that the apparent cause of this event was an inadequate design specification of a limit switch. <br /><br /> Based upon the short duration of the secondary containment doors being opened simultaneously and that the Secondary Containment differential pressure remained negative during the course of this event, this event is of low safety significance. <br /><br /> This event is being reported in accordance with 10 CFR 50.73(a)(2)(v)(C), any event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to control the release of radioactive material.
2372013005 | Dresden 2 | 11/14/2013 | 01/13/2014 | ML14037A20 | <strong>Primary Containment Inboard and Outboard Feed Water Isolation Valves Exceed Leakage Limits</strong><br /><i>Abstract:&nbsp;</i>On November 14, 2013, with Unit 2 shutdown for refueling outage D2R23, both the 2-0220-58B Feed Water Inboard Check Valve and the 2-0220-62B Feed Water Outboard Check Valve failed Local Leak Rate Testing (LLRT) acceptance criteria. Specifically, the "as-found" leak rate for both valves was above the administrative acceptance criteria of 45.0 scfh, and based upon the leakage rate observed, leakage was also determined to exceed the limits for primary containment leakage as specified in TS 5.5.12.c. <br /><br /> During testing, the in-series Feed Water "B" Loop Containment Isolation valve volumes could not be pressurized with full flow service air through the test tap configuration. The injected air immediately passed through the check valve and out the test vent tap, indicating that the valve disc was not fully seated. The cause of this event was determined to be that best practices, for installation and testing of the valves in order to maximize reliability, had not been implemented. The station has subsequently developed and implemented valve maintenance and testing best practices. Additionally, the station is evaluating long term actions to enhance the design and testing of the Feed Water check valves. <br /><br /> This event is being reported in accordance with 10 CFR 50.73(a)(2)(ii)(A) and 10 CFR 50.73(a)(2)(v)(C).
2372013006 | Dresden 2 | 11/14/2013 | 01/13/2014 | ML14037A11 | <strong>LPCI Swing Bus Auto Did Not Transfer as Expected</strong><br /><i>Abstract:&nbsp;</i>On November 14, 2013, during the of the Division 2 under voltage test, the Low Pressure Cooling Infection (LPCI) Swing Bus Automatic Transfer Scheme did not operate as expected. Specifically, while conducting the under voltage test, the LPCI swing bus Motor Control Center MCC 28-7/29-7 did not automatically transfer from Bus 29 to Bus 28. Technical Specification (TS) Surveillance Requirement (SR) 3.5.1.11 states “Verify automatic transfer capability of the LPCI swing bus power supply from the normal source to the backup source" The Bases for this requirement states “The swing bus automatic transfer scheme must be OPERABLE for both LPCI subsystems to be OPERABLE.” <br /><br /> The apparent cause of this event, based upon the design of the automatic transfer scheme, was a high resistance in the control circuit portion of the control switch. Corrective actions have been initiated to schedule the replacement of the control switch and to verify wiring connections associated with the control switch circuit. <br /><br /> Because the Division 2 Diesel would have needed to fail concurrent with the Loss of Offsite Power (LOOP) and a Loss of Coolant Accident (LOCA), in order for this function to be required, this event is of low safety significance. This event is being reported in accordance with 10 CFR 50.73(a)(2)(v)(B) and 10 CFR 50.73(a)(2)(v)(D).
2372013007 | Dresden 2, Dresden 3 | 11/16/2013 | 01/15/2014 | ML14030A04 | <strong>Secondary Containment Inoperable Due to Two Interlock Doors Being Open Simultaneously</strong><br /><i>Abstract:&nbsp;</i>At 10:19:02 CST on November 16, 2013, indication was received in the Control Room that two Secondary Containment doors, in one access opening, were open simultaneously. A worker, staged in the interlock, reported that while opening the Reactor Building side door the Turbine Building side door opened several inches. With two interlock doors open simultaneously, Technical Specifications 3.6.4.1, Surveillance Requirement 3.6.4.1.2, was not met. With the Surveillance Requirement not met, Secondary Containment was declared inoperable, and entry into Technical Specifications 3.6.4.1 Condition A was made. The doors were immediately closed and the Technical Specifications Condition was exited. <br /><br /> The apparent cause evaluation identified that the apparent cause of this event was an interlock circuit relay malfunction. Dresden engineering has completed the engineering change, and the modification is currently awaiting installation. <br /><br /> This event is being reported in accordance with 10 CFR 50.73(a)(2)(v)(C), any event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to control the release of radioactive material.
2372013008 | Dresden 2 | 11/25/2013 | 06/06/2014 | ML14188C05 | <strong>Leak Identified on a Relief Valve During Pressure Test Resulting in a Degraded Principal Safety Barrier</strong><br /><i>Abstract:&nbsp;</i>On 11/25/2013, Dresden Station was performing a Reactor Pressure Vessel (RPV) Class 1 System Leakage Test to verify no pressure boundary leakage in preparation for exiting D2R23. During the inspection of the second floor of the Drywell, a leak was identified on an Electromatic Relief Valve (ERV). The leak was approximately one drop per second from the weld of the pilot valve sensing line to the main valve body. The apparent cause of the leak was determined to be due to weld defects/porosity associated with the quality of the original weld.<br /><br /> Based upon the Drywell Radiation indications during the last operating cycle, the failure of the ERV does not appear to have been present during the last operating cycle. Therefore, this event is of low safety significance.<br /><br /> This event is being reported in accordance with 10 CFR 50.73(a)(2)(ii)(A), any event or condition that resulted in the condition of the nuclear power plant, including its principal safety barriers, being seriously degraded.
2372013009 | Dresden 2 | 11/30/2013 | 01/29/2014 | ML14043A11 | <strong>HPCI Failed to Achieve Rated Flow Due to Failure of Stop Valve to Open</strong><br /><i>Abstract:&nbsp;</i>On November 30, 2013, Operations was performing a fast start of the Unit 2 High Pressure Coolant Injection (HPCI) system. When the initiation signal was given, the HPCI Turbine Stop Valve failed to go full open. The apparent cause of the U2 HPCI system failing to reach rated flow was failure of a spare cover plate within the control valve manifold. <br /><br /> A failure analysis was completed which attributed the failure to a 360 degree circumferential fracture due to thermal fatigue cracking as demonstrated by a relatively brittle appearance and multiple crack origins around the spare cover plate circumference. The fracture occurred on a grooved lip that was designed to allow for thermal expansion during system warm up. As a result of the failure, the spare cover plate was replaced and additional future inspections are being planned. <br /><br /> This event is being reported in accordance with 10 CFR 50.73(a)(2)(v)(D), any event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident" and 10 CFR 50.73(a)(2)(i)(B), "Any operation or condition prohibited by the plants Technical Specifications."
2442013001 | Ginna | 04/12/2013 | 05/31/2013 | ML13157A04 | <strong>Unanalyzed Condition due to Missing Barrier</strong><br /><i>Abstract:&nbsp;</i>On April 12, 2013, a system engineer performing a walkdown of backflow prevention devices discovered that the check valve that was expected to be found installed in a floor drain in the Intermediate Building Basement had been removed. The check valve was designed as a barrier to prevent the flow of flammable liquid from the Turbine Building Basement to the Intermediate Building Basement where safe shutdown equipment is located.<br><br> In accordance with the Technical Requirements Manual (TRM), immediate compensatory actions were initiated. These actions were a fire detector operability verification and an hourly fire watch inspection. Additionally, a plug was installed in the floor drain to prevent the backflow of flammable liquid.<br><br> The apparent cause of this event is removal of the check valve due to housekeeping issues because it would not allow water to pass due to the unique design of the valve. The check valve appears to have been removed at some point in the past to prevent water accumulation in the floor drain without sufficient review of the impact. This event was entered into the Station's Corrective Action Program and a plant modification will be performed to replace the valve, addressing the original design deficiencies.
2442013002 | Ginna | 07/24/2013 | 09/17/2013 | ML13262A09 | <strong>Reactor Trip due to Generator Trip During Main Generator Reactive Power Testing</strong><br /><i>Abstract:&nbsp;</i>On July 24, 2013 at 1419, the R.E. Ginna Nuclear Power Plant (Ginna) experienced an automatic Reactor Trip from full power during Main Generator Reactive Power Testing.<br /><br /> The Reactor Trip was caused by a reactor protection system (RPS) actuation signal from a Turbine Trip, which was caused by a Generator Trip. All Control Rods inserted on the trip, and Auxiliary Feedwater started automatically, as expected. The cause of the generator trip was determined to be an incorrect configuration of two generator protection digital relays while implementing a modification during the 2012 refueling outage. An alarm was expected while raising voltage during reactive power testing, but due to the incorrect configuration of the relays, a trip signal was received which tripped the main generator. The protective relays' outputs were configured incorrectly to trip at the alarm setpoint.<br /><br /> The trip functions of the digital relays were removed, returning Ginna to the alarm indication and trip protections prior to the 2012 refueling outage.
2442013003 | Ginna | 09/20/2013 | 09/12/2014 | ML14268A07 | <strong>Unanalyzed Condition for Potential Floodwater Intrusion into Vital Battery Rooms</strong><br /><i>Abstract:&nbsp;</i>On September 20, 2013, R.E. Ginna Nuclear Power Plant determined that there was a potential for flooding of both battery rooms during a design basis flood due to unqualified wall penetration material. A flow test was performed to verify functionality of cable vault drains. Accumulation of water in the cable vault could potentially challenge unqualified penetration barriers between the manhole and "B" Battery Room, leading to flooding of the "A" Battery Room under the normally closed fire door. Flooding from these penetrations has not been previously evaluated. In addition, during the extent of condition review, two smaller conduit penetrations were discovered that were not sealed.<br /><br /> The apparent cause of this condition is inadequate re-evaluation of new flood level impacts during the 1981-1983 Systematic Evaluation Program review. The penetrations into the battery room have since been sealed watertight. Additionally, the drain line in the cable vault has been cleared of obstruction.
2472013001 | Indian Point 2 | 02/13/2013 | 04/15/2013 | ML13114A26 | <strong>Manual Reactor Trip as a Result of Decreasing Steam Generator Water Levels Caused by the Trip of Both Heater Drain Tank Pumps During AOV Diagnostic Testing</strong><br /><i>Abstract:&nbsp;</i>On February 13, 2013, operators initiated a manual reactor trip (RT) as a result of lowering steam generator (SG) levels. All control rods fully inserted and all required safety systems functioned properly. The plant was stabilized in hot standby with decay heat being removed by the main condenser {SG}. The Auxiliary Feedwater System automatically started as expected due to SG low level from shrink effect. An investigation determined the decreasing SG levels was due to reduced main feedwater (FW) flow from a loss of Heater Drain Tank (HDT) pumps. The HDT pumps tripped during valve diagnostics on HDT level control valve LCV-1127B which resulted in HDT Large Dump valves failing open. The open HDT large dump valves resulted in low HDT level and trip of the HDT pumps. The HDT large Dump valves failed open when the current/pressure (I/P) lead was lifted during air operated valve (AOV) diagnostics per procedure 0-IC-PC- AOV. Loss of HDT flow to the main feedwater pumps (FWPs) caused the FWPs speed controller cutback to reduce FW flow to the SGs. The root cause (RC) was inadequate procedure design and content. Corrective actions from the RC will be to revise Maintenance procedures 0-IC-PC-AOV and 0-VLV-404-AOV to: 1) Eliminate conditional steps for equipment setup that allows changes to work scope to be made in the field without proper review prior to performing work, 2) Eliminate the subject Caution block, and 3) Include signature blocks for review of drawings and validation that lifting a I/P lead or disconnecting the instrument tubing will not affect any other valve or component. The event had no effect on public health and safety.
2472013002 | Indian Point 2 | 04/16/2013 | 06/13/2013 | ML13176A11 | <strong>Safety System Functional Failure of the Onsite Emergency Diesel Generators due to Maintenance on the Emergency Fuel Oil Supply Line During Tagout of the Normal Line</strong><br /><i>Abstract:&nbsp;</i>On April 16, 2013, Operations personnel discovered that internal inspection work on the 23 Emergency Diesel Generator (EDG) Day Tank fuel oil (FO) fill stop valve DF-17-4 had been performed on April 15 without tagout protection by maintenance. Valve DF-17-4 is in the emergency FO supply line and was intrusively inspected concurrently with the normal FO supply line header tagged out for approved work on valve DF-17-5. This condition could potentially allow EDG makeup FO to escape out of the disassembled valve DF-17-4 bonnet and result in inadequate FO flow to the 21 and 22 EDG FO day tanks. Two root causes (RC) were identified: 1) Maintenance personnel did not follow the protective tagging (PTO) procedure and 2): Inadequate implementation of maintenance from a work readiness standpoint. Corrective actions to prevent recurrence included implementation of the performance management process for the tagout holder and WO holders, each maintenance supervisor and above will conduct at least two pre-job briefings or field observations of tagout holders per quarter until the end of 2013 or later as determined by the Maintenance Manager, and a Maintenance Department policy or WILL sheet will be issued and communicated that reinforces specific expectations for conducting quality walkdowns and readiness for online maintenance activities. The event had no significant effect on public health and safety.
2472013003 | Indian Point 2 | 07/03/2013 | 08/27/2013 | ML13247A17 | <strong>Manual Reactor Trip Due to Decreasing Steam Generator Water Levels Due to Loss of Main Feedwater (FW) Flow Caused by a Loss of Instrument Air to the FW Regulating Valves</strong><br /><i>Abstract:&nbsp;</i>On July 3, 2013, operators initiated a manual reactor trip as a result of lowering steam generator (SG) levels due to the loss of feedwater (FW) from the trip of both main FW pumps. A11 control rods fully inserted and all required safety systems functioned properly. The plant was stabilized in hot standby with decay heat being removed by the main condenser. The Auxiliary Feedwater System automatically started as expected. Investigations determined the decreasing SG levels were due to a loss of main FW flow as a result of the closure of the FW regulating valves. The FW regulating valves closed due to a loss of instrument air (IA) pressure. The IA pressure was lost when a two inch copper IA tubing in the 22 Main Transformer moat separated at a soldered coupling. Prior to the event piping lines including the IA line buried in the main transformer moat were excavated and temporary supports installed. The apparent cause was poor legacy workmanship assembling the IA tubing coupling during original plant construction. The IA tubing was not fully inserted into the coupling resulting in reduced joint strength. Corrective actions included reassembly and soldering of the IA joint with full insertion, acoustic emission and snoop testing on repaired coupling. Axial and thrust restraints were installed on the IA line in the moat. A caution was placed in the Buried Piping Program database associated with buried copper tubing identifying the potential for the separation of soldered joints when the line is excavated and the need for restraints or other contingencies to minimize the probability of a line separation. The event had no effect on public health and safety.
2472013004 | Indian Point 2 | 09/11/2013 | 11/12/2013 | ML13319B08 | <strong>Technical Specification (TS) Prohibited Condition due to an Inoperable Essential Service Water (SW) Header as a Result of Pin Hole Leaks in Code Class 3 SW Piping</strong><br /><i>Abstract:&nbsp;</i>On September 11, 2013, during an engineering walkdown of service Water (SW) temperature control valve SWN-TCV-1103, eight pin hole leaks were discovered in SW piping that supports three Radiation Monitors (RM). All leaks had minor corrosion product buildup as well as staining of the piping and staining of the floor. Seven leaks were on socket welds and one on an elbow and all located in ASME Section XI Code boundary. The affected SW piping and the essential SW header were declared inoperable and Technical Specification (TS) 3.7.8 (SW System) was declared not met which required entry into TS 3.0.3. The leaking piping was isolated restoring operability of the SW header. The apparent cause was procedure EN-DC-336 (Plant Health Committee) was not followed to document a risk assessment or mitigating (bridging) strategy when the pipe replacement was rescheduled. The corrective actions are to weld repair the affected piping followed by replacing piping with highly corrosion resistant material (AL6XN). Full pipe replacement is scheduled for the 2014 refueling outage. A review and assessment of the Site Integrated Project Database (SIPD) will be performed to identify any additional potential risks for not having documented risk assessments of items meeting the risk criteria. The Modification Project Review Committee (MPRC), Engineering Change Review Group (ECRG), Plant Health Committee (PHC), and System Engineering staff will be briefed on the need to consider requesting a bridging strategy when required high or medium risk ranked work is rescheduled beyond the operating cycle. The event had no significant effect on public health and safety.
2492013001 | Dresden 3 | 11/28/2013 | 01/27/2014 | ML14037A21 | <strong>Secondary Containment Inoperable due to Two Interlock Doors Being Open Simultaneously</strong><br /><i>Abstract:&nbsp;</i>On 11/28/13, at 0258 hours, the Control room received a Unit 2 interlock door alarm. Operations sent an equipment operator to investigate; and found a Radiation Protection Technician (RPT) and laborers in the area of the alarming interlock removing lead blankets. <br /><br /> With the Surveillance Requirement 3.6.4.1.2 not met, Secondary Containment was declared inoperable, and Unit 3 entered into Technical Specifications 3.6.4.1 Condition A. The doors were closed and the Technical Specifications Condition was exited. <br /><br /> The cause of this event was determined to be a failure to recognize a hazard while proceeding in the face of uncertainty. Specifically, the RPT did not recognize that there was a change in plant conditions (i.e., the restoration of the X-Area as part of the Secondary Containment boundary) and decided that it was permissible to override the door interlocks by using an emergency manual push-button. As a result of this event, Radiation Protection will be reviewing the proper use of human performance tools and will be revising procedures to enhance the notifications made to the Radiation Protection Department. <br /><br /> This event is being reported in accordance with 10 CFR 50.73(a)(2)(v)(C), any event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to control the release of radioactive material.
2502013001 | Turkey Point 3 | 01/03/2013 | 03/01/2013 | ML13072A29 | <strong>Procedure Noncompliance Causes Incorrect Instrument Setting and Condition Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On January 3, 2013, it was discovered that an incorrect meter was used to test two Pressurizer High Water Level reactor trip instrument channels. Technicians used an incorrect multimeter for a Channel I operational test and subsequently adjusted the setpoint prior to returning it to service. Technicians performed the same test on Channel II and when they saw that it was also displaying similar values, they stopped the surveillance and Channel II was placed in trip to comply with a TS Action. The result was that Channel I was inoperable and not tripped for approximately 30.5 hours. TS requirements were exceeded for Channel I being inoperable and not tripped greater than 6 hours (Action duration) and Channel II taken out of service during the same period, which placed the unit in TS 3.0.3. However, that condition was not recognized and the required actions were not completed. The direct cause of the event is procedure noncompliance. Corrective actions include procedure revisions for use of multimeters on the EAGLE 21 system, revision of the Maintenance and Test Equipment (M&TE) procedure to address the use of replacement M&TE, and measures to strengthen Maintenance Department procedure use and adherence. Safety significance is considered low because Channel III remained operable and Channel II was subsequently determined to be functional, so that the safety function was not lost in the 2 out of 3 logic.
2502013002 | Turkey Point 3 | 02/11/2013 | 04/11/2013 | ML13114A25 | <strong>Automatic Reactor Trip due to Low Condenser Vacuum</strong><br /><i>Abstract:&nbsp;</i>On February 11, 2013, a turbine gland sealing steam spillover valve was being bypassed in preparation for calibration of the actuator. Opening the bypass valve created a flow path for gland steam to the condenser, which caused a reduction in gland sealing steam pressure and decrease in main condenser vacuum. Main condenser vacuum reached the turbine trip setpoint, which caused an automatic reactor trip. The Auxiliary Feedwater (AFW) System actuated automatically due to low steam generator (SG) levels following the reactor trip. Recovery from the reactor trip was uncomplicated. AFW was secured and main feedwater was used for SG water level control. Decay heat removal was to atmosphere via the steam dump valves.<br><br> The root cause was determined to be ineffective implementation of the operational standards as demonstrated by: 1) improper monitoring of plant parameters during the manipulation of the spillover bypass valve, and 2) utilizing an equipment clearance order in lieu of an operating procedure when bypassing the gland seal spillover valve. Corrective actions include: 1) Revise procedural guidance for bypassing spillover valves, and 2) Implement an improvement plan to reinforce operational standards.
2502013003 | Turkey Point 3 | 02/18/2013 | 04/19/2013 | ML13128A31 | <strong>Manual Reactor Trip due to Increasing Reactor Coolant Pump Seal Leakage</strong><br /><i>Abstract:&nbsp;</i>On February 17, 2013, with the Unit 3 reactor in Mode 1 at approximately 99% power, the 3A Reactor Coolant Pump (RCP) No. 1 seal leak-off became elevated and erratic. A unit shutdown was commenced on February 18, 2013 at approximately 0055 when seal leak-off increased to 5.5 gpm. At approximately 0130, the reactor was manually tripped at approximately 72% power when seal leak-off flow reached 6 gpm. The 3A RCP was then secured and No. 1 seal leak-off was isolated. The Auxiliary Feedwater (AFW) System actuated as designed based on low steam generator (SG) levels as a result of the reactor trip. At approximately 0316, AFW was secured with main feedwater supplying the SGs and decay heat removed via the atmospheric relief valves. There were two causes: 1) The seal runner o-ring was damaged during installation. 2) The RCP shaft shoulder critical criterion of 60% minimum mating surface area was not attained after manual machining (stoning). Corrective actions include replacing the 3A RCP seal, review of performance of other RCP seals at both Turkey Point units, and revision of the RCP maintenance procedure to provide additional guidance for proper seal installation and post-machining inspections.
2502013004 | Turkey Point 3 | 02/27/2013 | 04/29/2013 | ML13128A31 | <strong>Safety Injection Flow Path Not Isolated due to Manual Valve Out of Position</strong><br /><i>Abstract:&nbsp;</i>On February 27, 2013 at approximately 1750, with Unit 3 in Mode 5 power was restored to Reactor Coolant System hot leg injection isolation valve MOV-3-866A in preparation for inservice testing (IST). On February 28, 2013 commencing at approximately 0047 normally closed MOV-3-866A and MOV-3-866B (parallel injection valves) were individually stroked for IST during which Pressurizer level increases were noted. Investigation revealed that recently installed remote manual valve 3-990 was not closed due to failure of a connection in the reach rod assembly. The remote operator had been used to close the valve and local verification was not employed. Valve 3-990 was being relied on for safety injection flow path isolation during the IST. MOV-3-866A and MOV-3-866B were verified closed with power removed at approximately 0230. Flow path isolation did not meet Technical Specification requirements for longer than the allowed four hours. Causes of this event include: 1) Reach rod universal joint connection failed as a result of failure to complete final installation steps at that location, and 2) The 3-990 valve was not verified to be closed locally. Corrective actions include: 1) Revising Operations procedures to provide additional guidance to verify reach rod valve operation, and 2) Establishing a means to better control work in the field that ensures critical installation steps are verified complete.
2502013005 | Turkey Point 3 | 03/12/2013 | 05/10/2013 | ML13182A01 | <strong>Reactor Trip Due to Turbine Header Pressure Spike While Testing Turbine Control Valves</strong><br /><i>Abstract:&nbsp;</i>On March 12, 2013 at approximately 1431 with Unit 3 in Mode 2 at approximately 3% rated thermal power, an automatic reactor trip occurred due to a turbine inlet pressure spike during turbine control valve (TCV) testing. Turbine inlet pressure enables the Reactor Protection System (RPS) at power reactor trips. One at power reactor trip is a turbine trip initiated by closure of both turbine stop valves (TSV). The pressure spike enabled the at power trips while the TSVs were closed causing the reactor trip. All control rods inserted and plant parameter response was as expected. The event is reportable in accordance with 10 CFR 50.73(a)(2)(iv)(A). The cause of the reactor trip was the unexpected pressure spike resulting from a quick opening of the No. 3 TCV of sufficient magnitude to satisfy the P-7 interlock with the TSVs closed. Corrective actions include the following procedure changes: 1) Close main steam isolation valves and turbine stop drain valves when testing TCVs, 2) Caution that TCV testing can lead to turbine inlet pressure spikes which could result in reactor trip, and 3) Ensure that the main steam header is depressurized prior to cycling a TCV during post maintenance testing. With plant response as expected, the risk associated with this low power trip is judged very low.
2502013006 | Turkey Point 3 | 03/13/2013 | 05/13/2013 | ML13182A01 | <strong>Reactor Protection and Auxiliary Feed Water System Actuations Due to Trip of Operating Feedwater Pump</strong><br /><i>Abstract:&nbsp;</i>On March 13, 2013 at approximately 1120 with Unit 3 in Mode 3, the Auxiliary Feed Water (AFW) System actuated. Subsequently, at approximately 1131 operators initiated a manual reactor trip. Just prior to these events, one Condensate Pump (CP) and one Steam Generator Feed Pump (SGFP) were in operation, when a field operator started a second SGFP for a one minute run to vent the supply header and casing. The plant is designed to only allow a single SGFP to operate with a single CP operating. This condition resulted in automatic trip of the running SGFP and AFW actuation. Operators then secured the just-started SGFP. AFW injected cooler water into the SGs reducing reactor coolant system temperature. Operators opened the reactor trip breakers via the manual reactor trip switch to obtain additional shut down margin, as a conservative measure. Operators started a Standby Steam Generator Feed Pump to maintain level in the SGs and secured both trains of AFW. The cause of the event is that licensed unit operators did not maintain adequate command and control of activities outside the control room allowing a decision to start the second SGFP to be made at the wrong organizational level. Corrective action will include implementation and assessment of the effectiveness of the improvement plan to reinforce operational standards.
2502013007 | Turkey Point 3 | 05/10/2013 | 07/08/2013 | ML13199A22 | <strong>Manual Reactor Trip due to Generator Load Drop</strong><br /><i>Abstract:&nbsp;</i>On May 10, 2013, Unit 3 reactor was manually tripped in response to a sudden loss of turbine load at approximately 25% reactor power. Plant power was being reduced during a controlled shutdown for planned maintenance. The operating crew observed generator megawatts suddenly reduced to zero, with no operator action. The crew manually tripped the reactor. All systems responded as expected, except for source range nuclear instrument N-3-32 which experienced a loss of detector voltage. <br><br> The root cause was determined to be an incorrect deadband pressure value of the Load Drop Anticipatory (LDA) circuit in the turbine control system. <br><br> Corrective actions included reducing the dead band of the LDA pressure arming setpoint and adding indicator lights to the turbine control system display to identify armed status.
2502013008 | Turkey Point 3 | 06/19/2013 | 08/19/2013 | ML13248A45 | <strong>Through-Wall Leak in 3A CCW Pump Threaded Fitting Caused Pump to be Inoperable Longer than AOT</strong><br /><i>Abstract:&nbsp;</i>On June 7, 2013, with the Unit 3 reactor at 100% power, leakage at a threaded vent line connection on the 3A Component Cooling Water (CCW) pump casing was identified. A condition report and work request were initiated. By June 19, 2013, the leakage had increased from approximately 100 drops per minute to a steady stream and the pump was removed from service and isolated for repair. Examination of the 3/4 inch nipple removed from the pump casing revealed a through-wall flaw whose length exceeded structural integrity requirements. The pump was determined to be inoperable from intial observation of leakage on June 7. This 12 day period exceeded the allowed outage time permitted by the Technical Specifications and the attendant shutdown actions were not met. The cause of the fitting flaw is high cycle fatigue. Corrective actions include: 1) Repair the threaded connection, and 2) Modify the design to increase margin. Safety significance is considered to be low because the other two CCW pumps were available and capable of being powered by independent power supplies. The CCW safety function is accomplished with one pump operating.
2502013009 | Turkey Point 3 | 09/28/2013 | 11/27/2013 | ML14008A19 | <strong>Loose Breaker Control Power Fuse Holder Caused 3B ICW Pump to be Inoperable Longer than AOT</strong><br /><i>Abstract:&nbsp;</i>On September 28, 2013 at approximately 1929 hours, with the Unit 3 reactor at 100% power, Operations personnel discovered that power to the 3B Intake Cooling Water (ICW) pump breaker closing circuit and charging springs was lost. The UC (closing circuit) fuse holder was noted to be slightly backed out about 1/8 inch. Control power was restored after the fuse holder was pressed back in place. Further investigation determined that the 3B ICW pump was inoperable for a period longer (approximately 4 days) than the allowed outage time of 72 hours because the pump could not have performed its intended function to help mitigate a loss of coolant accident coincident with a loss of offsite power (LOOP). The breaker would not have been able to open on a LOOP then close for diesel generator loading. The causes are attributed to improper fuse installation and wear on the fuse holder stabs and clips. Corrective actions include: 1) Revise 4160 volt breaker operating procedure to provide guidance for ensuring UC fuse holders are tight after installation, and 2) Establish UC fuse holding force inspection acceptance criteria for 4160 volt breakers, perform inspections, and replace fuse holder assemblies as required. Only one of three provided ICW pumps is required to perform the safety function. The other two ICW pumps were available during the time the 3B ICW pump was inoperable, therefore, the safety significance of this event is considered to be low.
2512013001 | Turkey Point 4 | 03/23/2013 | 05/22/2013 | ML13156A33 | <strong>Power Operated Relief Valve Inoperable for Greater Than Allowed Outage Time due to Lifted Leads</strong><br /><i>Abstract:&nbsp;</i>On March 23, 2013 with Unit 4 in Mode 5, while restoring Residual Heat Removal (RHR) System interlocks, it was discovered that an isolation signal was present due to two lifted leads, which also rendered one power operated relief valve (PORV) inoperable. As result, one of two required PORVs for the Overpressure Mitigating Systems (OMS) was inoperable for a period exceeding the Technical Specification (TS) allowed outage time, which is reportable in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by TS. The root cause is inadequate procedure compliance by supplemental personnel during performance of a modification. Also, the review to establish PORV operability for OMS credited a surveillance requirement that was current but performed prior to the lifting of the leads. Corrective actions include: 1) Revising site training for supplemental personnel to better emphasize the importance of configuration management and the procedural controls employed to maintain it, 2) Revising the alarm response procedure for a related annunciator to include a check that fuses for OMS PORVs are installed and control power to pressure comparators is in service, 3) Verifying status of PORV actuation instrumentation prior to declaring OMS operable.
2512013002 | Turkey Point 4 | 04/19/2013 | 06/18/2013 | ML13183A06 | <strong>Reactor Trip Due to Loss of Offsite Power Resulting From Generator Testing</strong><br /><i>Abstract:&nbsp;</i>On April 19, 2013 with Unit 4 in Mode 1 at approximately 29% of rated power, a reactor trip occurred as a result of degraded voltage at the 480V load centers. Upon receipt of the degraded voltage signal, loads were shed on the vital buses, and both Emergency Diesel Generators started and repowered the buses. The reactor tripped due to the loss of the Reactor Coolant Pumps during bus load shedding. All control rods inserted. The unit stabilized via natural circulation in Mode 3. The Auxiliary Feedwater System initiated to maintain water level in the steam generators. Offsite power was restored to the vital buses in approximately 30 minutes. The event was initiated by lowered exciter voltage during generator testing after an extended power uprate outage to obtain data to establish generator protection relay settings. The use of a test instruction instead of a plant test procedure for the test, and inadequate risk recognition by station personnel were detemined to be the root causes. Corrective actions include eliminating the option to use test instructions for controlling plant operation, and developing and implementing a comprehensive program on risk recognition and management.
2542013001 | Quad Cities 1 | 02/28/2013 | 04/30/2013 | ML13141A28 | <strong>Emergency Diesel Generator Cooling Water System Not Aligned</strong><br /><i>Abstract:&nbsp;</i>On March 1, 2013, during restoration of the 1B Core Spray (CS) logic test, the lineup for the 1/2 Emergency Diesel Cooling Water Pump (1/2 EDGCWP) was to be restored to normal. It was discovered that the 1/2 EDGCWP was lined up to Unit 2 instead of the required Unit 1. At the time of discovery all required systems were operable. However, prior to discovery, the Unit 1 Emergency Core Cooling System (ECCS) room coolers were inoperable since Technical Specifications (TS) 3.7.2, Diesel Generator Cooling Water (DGCW) System, Action B.1, was not met because an operable EDGCW subsystem was not "aligned" to the ECCS room coolers, and associated ECCS were not alternatively declared inoperable per Action B.2.<br><br> During the time the 1/2 EDGCWP isolation valve to Unit 1 ECCS room cooling (1/2-3999-89) was improperly aligned, it was however, available to be opened via Operator manual actions had an ECCS initiation occurred. The safety significance of this event was minimal since the Unit 1 EDGCWP and the 1/2 EDGCWP were available and capable of supporting Unit 1 ECCS Room cooling.<br><br> The cause of the event was the individual worker's lack of execution of proper human performance tools.<br><br> Corrective actions included the addition of immediate oversight of operations briefs and direct documented supervision of equipment operators during the upcoming refueling outage. Planned corrective actions include implementation of the process of focused intervention directed at the crew level based on Employee Observation System trending and analysis data, and documenting the performance of the human performance "Out-of-the-Box" (OBE) Evaluations pertaining to use of human performance tools.<br><br> Given the impact of the misaligned 1/2 EDGCWP on the operability of Unit 1 ECCS Room cooling for CS, Residual Heat Removal (RHR), and High Pressure Coolant Injection (HPCI) systems, this report is submitted in accordance with the requirements of 10 CFR 50.73(a)(2)(i)(B), which requires the reporting of any operation or condition which was prohibited by the plant's Technical Specifications.
2542013002 | Quad Cities 1 | 03/11/2013 | 05/10/2013 | ML13141A40 | <strong>Outboard Main Steam Isolation Valves (MSIVs) Stroke Times Exceeded</strong><br /><i>Abstract:&nbsp;</i>On March 11, 2013, during refueling outage Q1R22 at approximately 0750 hours, the Unit 1 Main Steam Isolation Valve (MSIV) as-found stroke time test results indicated that all four outboard MSIVs failed to close within the required Technical Specification (TS) time of less than or equal to five (5) seconds. The four inboard MSIVs, tested just prior to the outboard MSIVs, all closed within the required TS time of less than or equal to five (5) seconds. The safety significance of this event was minimal.<br><br> The cause of the Unit 1 outboard MSIV slow closure timing is the actuator seals had degraded due to age and wear.<br><br> Corrective actions included replacing the 1-0203-2B MSIV actuator, readjusting as-left closure times on all outboard MSIVs, and satisfactory retesting prior to startup. Follow-up corrective actions include replacing the 1-0203-2A, 2C, and 2D MSIV actuators and increasing the preventive maintenance frequency.<br><br> Since all four outboard MSIVs failure to stroke within the required times was attributed to degraded actuator seals, it is likely the degradation occurred over time since the last successful refueling outage testing and during power operations when the required TS 3.6.1.3, Primary Containment Isolation Valves (PCIVs), was applicable. Therefore this condition is being reported in accordance with 10 CFR 50.73(a)(2)(i)(B), which requires reporting of any operation or condition that was prohibited by the plant's Technical Specifications.
2542013003 | Quad Cities 1 | 03/26/2013 | 05/28/2013 | ML13156A34 | <strong>Reactor Vessel Head Vent Line Leak due to Weld Defect</strong><br /><i>Abstract:&nbsp;</i>On March 26, 2013, at 1541 hrs, while Unit 1 was shutdown for refueling outage Q1R22, leakage was identified exiting from the 2-inch reactor vessel head vent piping during a Reactor Pressure Vessel (RPV) pressure test. The leakage rate was approximately 20 drops per minute (dpm). The RPV head vent line provides a connection from the RPV upper steam dome volume to provide a vent path to the drywell sumps during shutdown conditions and to the main steam lines to vent noncondensable gasses during power operation.<br><br> The leakage originated from a socket weld (designated as FW14) between the pipe and a 90 degree fitting. The RPV pressure test was stopped and the reactor vessel depressurized to allow additional inspections and necessary repairs.<br><br> The most probable cause of the leakage was determined to be a defect in the socket weld attributed to porosity and/or slag, originating from initial construction in 1970, prior to the initial start-up of Unit 1.<br><br> Corrective actions included repairing the weld by removal of the existing weld material and application of a new weld. Future corrective actions include inspecting other similar RPV head vent welds and repairing/evaluating as necessary.<br><br> The safety significance of this event was minimal since the leakage rate was very small and was found while the reactor was shutdown. Given the impact on the reactor coolant pressure boundary, this report is submitted in accordance with the requirements of 10 CFR 50.73 (a)(2)(ii)(A), which requires the reporting of any event or condition that resulted in the condition of the nuclear power plant, including its principal safety barriers, being seriously degraded.
2552013001 | Palisades | 02/14/2013 | 04/15/2013 | ML13100A01 | <strong>Technical Specification Required Shutdown Due to a Component Cooling Water System Leak</strong><br /><i>Abstract:&nbsp;</i>On February 10, 2013, due to a slowly lowering level trend in the component cooling water (CCW) surge tank, investigations began to identify a potential CCW leakage path. On February 14, 2013, at 2030 hours, the right train of the CCW system was declared inoperable due to the identification of an approximate 40 gallons per hour CCW leak into the service water system section of the "A" CCW heat exchanger. The "A" CCW heat exchanger is one of two essentially identical ASME Section 111 class 3 heat exchangers installed in the CCW system. <br /><br /> Technical Specification 3.7.7.A.1 requires restoration of an inoperable CCW system train within 72 hours. Due to the inability to repair the leak within the required 72 hour time frame, a plant shutdown was initiated at 1300 hours on February 15, 2013. The plant entered Mode 3 at 1649 hours on February 15, 2013. At 1111 hours on February 16, 2013, the plant entered Mode 5 to execute repairs.<br /><br /> The majority of CCW leakage was attributed to one tube, located in the center of the tubesheet, within the CCW heat exchanger. Very minor leakage was identified from the tube plug area of seven previously plugged tubes. Due to the inability to fully isolate CCW system flow into the heat exchanger, the failed tube could not be inspected to determine a definitive failure mechanism. Mechanical type tube plugs were installed in the tubes where leakage was identified.
2552013002 | Palisades | 05/05/2013 | 06/25/2013 | ML13176A41 | <strong>Technical Specification Required Shutdown eue to Safety Injection/Refueling Water Tank Leak</strong><br /><i>Abstract:&nbsp;</i>At 0027 on May 5, 2013, the safety injection/refueling water (SIRW) tank was declared inoperable in accordance with the operational decision-making issue (ODMI) process. Water leakage from the tank had exceeded the pre-established limit of the ODMI process that directed the tank be declared inoperable. Leakage from the tank was quantified at approximately ninety gallons per day. Technical Specification (TS) 3.5.4.B requires restoration of an inoperable SIRW tank within one hour. If the tank is not returned to an operable status within one hour, TS 3.5.4.0 requires the plant be placed in Mode 3 within six hours and in Mode 5 within the subsequent thirty-six hours.<br><br> Due to the inability to repair the leak within the required one-hour time frame, a plant shutdown was initiated at approximately 0100 hours on May 5, 2013. The plant entered Mode 3 at 0457 hours on May 5, 2013. At 2358 hours on May 5, 2013, the plant entered Mode 5 to execute repairs.<br><br> Testing identified an approximate 3/16-inch through-wall crack in a nozzle reinforcing collar to floor plate weld of the tank. Follow-up analysis determined there was significant lack of fusion in the weld that resulted in the failure of the weld and subsequent water leakage. The welder that fabricated the weld did not ensure adequate fusion at the weld root.<br><br> The entire SIRW tank floor was replaced with the exception of an annulus ring around the perimeter. Several initiatives were implemented to preclude potential weld issues during the fabrication of the new tank floor, including welder proficiency training on revised welding techniques and utilization of several types of weld testing methods.
2552013003 | Palisades | 08/13/2013 | 10/11/2013 | ML13288A13 | <strong>Both Control Room Ventilation Filtration Trains Declared Inoperable</strong><br /><i>Abstract:&nbsp;</i>At 1102 on August 13, 2013, both control room ventilation filtration system trains were declared inoperable in accordance with Technical Specification (TS) 3.7.10, Condition B, due to the inability to fully close control room envelope (CRE) boundary door-15. At 1111 on August 13, 2013, door-15 was closed and TS 3.7.10, Condition B, was exited. TS 3.7.10 allows CRE boundary doors to be opened intermittently, under administrative control for preplanned activities, provided the doors can be rapidly restored to the design condition. <br /><br /> During preplanned maintenance activities, workers attempting to exit the CRE area were unable to open door-15 via normal operation of the door's hand wheel. Recent frequent operation of door-15 may have caused deformation of a cotter pin within the door's normal operating mechanism. Deformation of the cotter pin could cause the normal operation of door-15 to function intermittently. To allow exiting, workers opened door-15 using the emergency egress latch that activated an alarm condition on the door. During exiting, inadvertent operation of the door's hand wheel in the closed direction caused the door's latching pins to extend out causing interference between the door and the door frame preventing door-15 from fully closing. Due to the door being in an alarmed condition, the door's latching pins were unable to be immediately retracted. After approximately nine minutes, the door's latching pins were retracted by use of the emergency egress latch and the door was restored to the design condition, i.e., closed. <br /><br /> The cotter pin was replaced. Future potential corrective actions include increased preventative maintenance frequency to replace the cotter pin and restricting the use of the emergency egress latch.
2552013004 | Palisades | 11/07/2013 | 01/06/2014 | ML14007A13 | <strong>Discovery of Latent Design Deficiency Results in Non-Compliance with 10CFR 50 Appendix R</strong><br /><i>Abstract:&nbsp;</i>On November 7, 2013, during an operating experience applicability review, a latent design deficiency was discovered. The design deficiency represents an unanalyzed condition during a postulated fire event. Potential fire induced cable faults could result in a loss of capability to safely shutdown the plant.<br /><br /> Palisades' station batteries contain shunts in the positive leg of output current flow. The shunts provide a voltage signal to ammeters located in the adjacent cable spreading room area. In the unlikely event of the postulated fire scenario, which is a primary fire in the cable spreading room or in a station battery room, the ammeter circuit wiring could experience fire-induced cable faults, allowing current flow greater than the rating of the wires. Current flow exceeding the rating of the wires would likely result in the wires overheating, potentially causing a secondary fire at some point along the path of the wires or causing damage to adjacent cables/wires. That is, a secondary fire could be created in an additional fire area as well as the originating fire area.<br /><br /> The cause of the unanalyzed condition for the postulated fire event was a failure to recognize the described failure mode and identify the fault consequences for the cables of concern during previous design reviews required for 10 CFR 50 Appendix R. Planned corrective actions to address this condition include the design and implementation of a permanent plant modification to install fuses in the ammeter indication circuits.
2592013001 | Browns Ferry 1, Browns Ferry 2, Browns Ferry 3 | 02/06/2013 | 06/12/2013 | ML13169A24 | <strong>Latent Design Input Inconsistencies Adversely Affect Probable Maximum Flood Analysis</strong><br /><i>Abstract:&nbsp;</i>On July 28, 2009, the Tennessee Valley Authority (TVA) identified latent design input inconsistencies in hydrological computer modeling used for probable maximum flood (PMF) calculations. <br><br> The root causes of the condition were an organizational behavior which allowed the latent input inconsistencies to go undetected and management failure to provide oversight of the impact of river system changes on the calculated value of the PMF. The corrective actions to prevent recurrence are to procedurally require a Flood Protection Program, develop formal Flood Protection Program Management Implementing Procedure(s) and Design Standards/Guides, create a formal documented risk management process for all engineering products, formalize the elements of engineering technical rigor, and implement an upper tier integrated risk management process. Upon discovery, WA implemented both immediate and interim corrective actions to ensure the Fort Loudoun, Cherokee, Tellico and Watts Bar Dams would not overtop during an assumed PMF event. <br><br> On May 30, 2013, a new analysis regarding PMF elevations at Browns Ferry Nuclear Plant (BFN), Units 1, 2, and 3 was completed. Although this condition was considered to be unanalyzed, the analysis concluded that it did not result in BFN being in a condition that significantly degraded plant safety with respect to the PMF elevation prior to the HESCO modular flood barriers being placed on top of the dams.
2592013002 | Browns Ferry 1 | 03/19/2013 | 05/20/2013 | ML13144A57 | <strong>Manual Reactor Shutdown due to Decreasing Condenser Vacuum</strong><br /><i>Abstract:&nbsp;</i>On March 19, 2013, at approximately 0402 hours Central Daylight Time, the Browns Ferry Nuclear Plant (BFN), Unit 1, reactor was manually scrammed due to decreasing condenser vacuum caused by a significant leak from the 1C feedwater heater level control line. Condenser vacuum was deteriorating and was approaching the turbine trip setpoint, at which time the reactor was manually scrammed. The main steam isolation valves remained open, reactor pressure was controlled with the main turbine bypass valves, and the reactor feedwater pumps were used to control reactor water level. All systems responded as expected to the scram. All control rods inserted into the core during the scram.<br><br> The root causes for this event were a combination of vibration from the dump valve opening with the vibration in the 4 inch drain line from leaking drain valves, and station personnel did not consistently consider risk when making decisions to replace the BFN, Unit 1, feedwater heater vent and drain valves.<br><br> The corrective actions to prevent recurrence are to design and implement a design change for the feedwater heater vent and drain header piping to provide increased support, and establish initial and continuing training requirements for leaders and craft that support their roles and responsibilities. Also, BFN has implemented a Strategic Performance Management process to reinforce and institutionalize conservative decision making principles.
2592013004 | Browns Ferry 1 | 07/20/2013 | 09/18/2013 | ML13263A01 | <strong>High Pressure Coolant Injection System Declared Inoperable due to Exceeding the Allotted Time Frame for Instrument Inoperability</strong><br /><i>Abstract:&nbsp;</i>On July 20, 2013, at 0338 hours Central Daylight Time (CDT), Operations personnel entered Technical Specification (TS) 3.3.5.1 Condition D due to the performance of surveillance procedure 1-SR-3.3.5.1.3(D), High Presture Coolant Injection System Condensate Header Low Level Switch Calibration and Functional Test, requiring the High Pressure Coolant Injection (HPCI) System to be declared inoperable within one hour. At 0438 hours CDT due to not meeting the required Completion Time, Browns Ferry Nuclear Plant, Unit 1, made an unplanned entry into TS 3.5.1 Condition C, due to the HPCI System being declared inoperable.<br /><br /> The root cause of this event was determined to be the failure to declare the HPCI System inoperable as part of the planned surveillance testing on the HPCI System condensate header low level switches.<br /><br /> Corrective actions to prevent recurrence were to revise surveillance procedures "High Pressure Coolant Injection System Condensate Header Low Level Switch Calibration and Functional Test" and "HPCI Suppression Chamber High Level Calibration and Functional Test" to require the HPCI System be declared inoperable prior to the performance of these surveillance procedures.
2592013005 | Browns Ferry 1, Browns Ferry 2, Browns Ferry 3 | 10/03/2013 | 02/27/2014 | ML14077A31 | <strong>Inadequate Shift Staffing to Support Implementation of the Safe Shutdown Instructions</strong><br /><i>Abstract:&nbsp;</i>On September 6, 2013, the Tennessee Valley Authority completed an evaluation of Browns Ferry Nuclear Plant (BFN) Operations minimum shift staffing for response to a fire in the Control Bay that ultimately leads to entry into Appendix R Safe Shutdown Instructions (SSIs). The result of this evaluation revealed that the Operations minimum shift staffing does not provide sufficient staffing to meet current licensing basis requirements. On October 3, 2013, this condition was determined to be reportable.<br /><br /> The root causes for this condition were determined to be the following: (1) there was no formal process available that provided the necessary detail to ensure all appropriate source documents were considered for the Operations minimum shift staffing evaluation, and (2) ineffective implementation of the corrective action program.<br /><br /> A summary of the corrective actions to prevent recurrence are: (1) Hire and direct an external contractor with the expertise and formal process to perform an evaluation of operations minimum shift staffing, (2) Document the formal process used for the evaluation of operations minimum shift staffing, including basis, and (3) Revise OPDP-1, Conduct of Operations, to include the results of the Operations minimum shift staffing evaluation; including a reference to the formal process used, basis of the evaluation, and the licensing bases requirements.
2592013007 | Browns Ferry 1 | 10/16/2013 | 12/16/2013 | ML13354B84 | <strong>High Pressure Coolant Injection System Declared Inoperable due to an Inadvertent Actuation of the Primary Containment Isolation System</strong><br /><i>Abstract:&nbsp;</i>On October 16, 2013, at 1032 hours Central Daylight Time, the Browns Ferry Nuclear Plant, Unit 1, High Pressure Coolant Injection (HPCI) System unexpectedly received a Group 4, Primary Containment Isolation System (PCIS) signal during the performance of surveillance procedure 1-SR-3.3.5.1.2(ATU D), Core and Containment Cooling Systems Analog Trip Unit Functional Test. Operations personnel declared the HPCI System inoperable and entered Technical Specification 3.5.1, Emergency Core Cooling System-Operating, Condition C.<br /><br /> The Group 4, PCIS signal isolated the steam flow path to the HPCI turbine, resulting in the HPCI System being unavailable for approximately 14 minutes. The HPCI System isolation and unavailability is considered a safety system functional failure of a single-train system preventing accident mitigation and residual heat removal.<br /><br /> The root cause of this event was determined to be the workers not applying human error reduction tools appropriately, resulting in a procedure step not being completed as written.<br /><br /> The corrective action to prevent recurrence was to perform appropriate disciplinary action with the workers involved in the HPCI isolation in accordance with Human Resource process and procedures.
2592013008 | Browns Ferry 1, Browns Ferry 2, Browns Ferry 3 | 12/16/2013 | 02/14/2014 | ML14055A39 | <strong>Fire Damage to Cables in Fire Areas Could Cause Residual Heat Removal Pumps to Spuriously Start</strong><br /><i>Abstract:&nbsp;</i>On December 16, 2013, an extent of condition review related to an Appendix R Operator Manual Action deficiency, identified that fire damage to a non-isolated 250 VDC control cable could cause Residual Heat Removal (RHR) Pump 2C to spuriously start when its associated 4kV Shutdown Board B is credited by Appendix R analysis. The control cable is routed from the 4kV Shutdown Board to the RHR Loop I drain valve/limit switch interlock. An undesired spurious start of RHR Pump 2C could overload the credited Emergency Diesel Generator (EDG) or take away the necessary load capacity to allow operation of other Appendix R fire safe shutdown credited loads. A similar condition exists for RHR Pumps 1A, 1B, 1D, 2A, 2B, 3A, and 3C.<br /><br /> Safe Shutdown Instructions (SSTs) follow a single safe shut down path that consists of one train of credited equipment including one EDG, one 4kV Shutdown Board, and one RHR pump. This condition resulted in an unanalyzed condition that significantly degraded plant safety because fire damage could cause a spurious start of a non-credited RHR pump resulting in the unavailability of the associated credited 4kV Shutdown Board.<br /><br /> Compensatory actions include an Operator Work Around (OWA) to prevent spurious RHR pump starts, a caution order on the transfer switches referencing the OWA, and roving fire watches to mitigate this condition.<br /><br /> The root cause of this condition was identified as legacy human performance errors that occurred during the resolution of Appendix R cable routing failures. Corrective actions include implementing modifications to resolve cable routing issues for RHR pumps to eliminate potential EDG overloading due to RHR pump spurious starts.
2602013001 | Browns Ferry 2 | 03/02/2013 | 05/01/2013 | ML13127A00 | <strong>Inoperable Stop-Check Valve Results in Condition Prohibited by Technical Specifications and Reactor Shutdown Required by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On March 2, 2013, radiography results for the Browns Ferry Nuclear Plant (BFN), Unit 2, Reactor Core Isolation Cooling (RCIC) system stop-check valve, 2-HCV-071-0014, showed the valve to be in the fully open position; therefore, not meeting its function as a primary containment isolation valve. The RCIC Steam Line Outboard Isolation valve, 2-FCV-071-0003, was closed and deactivated to meet Technical Specification (TS) 3.6.1.3 for Primary Containment Isolation. This caused the RCIC system to become inoperable. The TS 3.5.3 requires the RCIC system to be returned to service within 14 days. Because valve 2-HCV-071-0014 is unisolable to primary containment, a unit shutdown was required to perform repairs. Actions to initiate reactor shutdown began on March 14, 2013, at 0800 Central Daylight Time.<br><br> The root cause of this condition is valve 2-HCV-071-0014 was improperly classified as a Run-to-Failure hand valve when it should have been classified as a Critical check valve.<br><br> The corrective action to prevent recurrence is to submit preventive maintenance change requests to open, inspect, clean, and replace valve disc, dashpot, and stem, as necessary, for RCIC Turbine Exhaust Hand Control Valves, RCIC Vacuum Pump Discharge Shutoff Valves, and High Pressure Coolant Injection Turbine Exhaust Valves.
2602013002 | Browns Ferry 2 | 09/24/2013 | 11/25/2013 | ML13333A16 | <strong>High Pressure Coolant Injection System Declared Inoperable due to an Unqualified Electrical Splice</strong><br /><i>Abstract:&nbsp;</i>On September 24, 2013, during an Environmental Qualification (EQ) review of a work order, it was discovered that the motor leads for the valve actuator on the High Pressure Coolant Injection (HPCI) main pump minimum flow valve had an unqualified electrical splice; and as a result, Operations personnel declared the valve inoperable and entered Technical Specification (TS) 3.6.1.3 Condition C. At 1530 hours Central Daylight Time, as a result of the inoperability of the HPCI main pump minimum flow valve, Operations personnel declared the HPCI System inoperable, and Browns Ferry Nuclear Plant, Unit 2, made an unplanned entry into TS 3.5.1 Condition C.<br /><br /> The root cause of this event was determined to be a lack of clear and specific procedural guidance related to: (1) overt direction on locating and determining the component classification relative to 10 CFR 50.49 requirements, and (2) guidance on changes to EQ components and associated work orders.<br /><br /> Corrective actions to prevent recurrence are to revise the work control planning procedure to include: (1) the requirement that changes to EQ work orders are considered major changes, (2) the requirement that revisions to EQ work orders are reviewed and concurred with by the EQ program manager or designee, and (3) the location of the EQ classification information.
2612013001 | Robinson 2 | 10/06/2013 | 08/05/2014 | ML14225A77 | <strong>Non-Environmentally-Qualified Splice Rendered Post Accident Monitoring Instrumentation Channel Inoperable</strong><br /><i>Abstract:&nbsp;</i>On 10/6/2013, with the plant de-fueled and vessel head removed, it was discovered that a non-environmentally-qualified butt-splice was installed in a wire connected to the 'closed' limit switch for a containment isolation valve, which rendered the Post-Accident Monitoring (PAM) Instrumentation function - Containment Isolation Valve Position Indication - inoperable. This condition has been present for an extended period of time, and it is presumed that on multiple occasions this function was inoperable for a period of time greater than allowed by Technical Specifications (TS) 3.3.3, PAM Instrumentation Limiting Conditions for Operation.<br /><br /> The initial investigation into the cause of this event indicates this was an isolated human performance event in which the non-licensed air-operated valve (AOV) technician failed to use proper material specified for the task per the procedure directing the task. Immediate corrective action consisted of the removal of non-environmentally-qualified splice and subsequent installation of an environmentally-qualified splice, which returned the component to operable condition.<br /><br /> This event did not impact the health and safety of the public.
2612013002 | Robinson 2 | 11/05/2013 | 06/19/2014 | ML14188B01 | <strong>Automatic Actuation of the Auxiliary Feedwater System due to Main Feed Pump Trip</strong><br /><i>Abstract:&nbsp;</i>At 0041 hours EST on 11/05/2013, with the Unit in Mode 2 and startup low-power physics testing in progress, there was an inadvertent automatic actuation of the Auxiliary Feedwater System due to an 'A' Main Feed Pump trip. While placing the Condensate Polishers in service, a secondary-side perturbation occurred resulting in the loss of the running 'A' Main Feedwater Pump on low suction pressure coincident with low flow. There was no plant damage or personnel injury as a result of this event. An 8-hour, non-emergency notification was made to the NRC per 10 CFR 50.72(b)(3)(iv)(A) due to the valid actuation of the Auxiliary Feedwater System (EN# 49502).<br /><br /> The root cause evaluation has concluded that the cause of this event was an operating error by one individual involving procedure use and adherence.<br /><br /> Corrective actions consist of completion of confidential personnel actions for the Makeup Water Treatment/Condensate Polisher Auxiliary Operator responsible for the event, and enhancement of expectations for supervisory oversight of risk significant evolutions will be employed.
2612013003 | Robinson 2 | 11/05/2013 | 08/05/2014 | ML14225A77 | <strong>Reactor Trip on 4KV Bus Undervoltage During Load Transfer</strong><br /><i>Abstract:&nbsp;</i>At 1801 hours EST on 11/5/2013, with the Unit in Mode 1 at 19% power, H. B. Robinson Steam Electric Plant, Unit No. 2 (HBRSEP2) experienced an automatic reactor trip while operators were transferring loads from the Startup Transformer to the Unit Auxiliary Transformer (UAT), as part of activities associated with coming on line and increasing power following Refueling Outage 28. During the coordinated breaker operation, the reactor tripped when an anomaly occurred that resulted in the actuation of two undervoltage relays associated with the loss of 2 of 3 4KV buses. The 'A' Emergency Diesel Generator (EDG) auto-started and supplied the E-1 emergency bus as a result of the undervoltage transient. The event was reported as a 4 hour Non-Emergency report per 10 CFR 50.72 (b)(2)(iv)(B) due to the valid Reactor Protection System Actuation, and as an 8 hour Non-Emergency report per 10 CFR 50.72(b)(3)(iv)(A) due to the valid actuation of Auxiliary Feed Water and EDG auto-start and subsequent starting of required undervoltage loads, save `A' Service Water Pump.<br /><br /> The investigation into the cause of this event determined that advanced aging/fatigue of the phenolic operating rods of the UAT breaker (52/7) caused the failure of the 'B' phase operating rod, which prevented closure of the 'B' phase of the breaker. The cause of the failure of the 'A' Service Water Pump to sequence onto the E-1 bus during the blackout sequence was attributed to a loose wire termination in the Emergency Control Station (ECS). Immediate corrective actions consisted of assessment of the switchyard and E-1 Bus, inspection of Breaker 52/7, and securing the loose wire termination in the ECS. This event did not impact the health and safety of the public.
2632013001 | Monticello | 04/12/2013 | 06/07/2013 | ML13158A27 | <strong>E SRV Low-Low Set Tailpipe dP Root Valve Found Closed</strong><br /><i>Abstract:&nbsp;</i>On April 12, 2013 at 2200, during investigation into the inability to complete a Safety Relief Valve (SRV) discharge line excess flow check valve test, a relief valve discharge monitoring instrument valve was discovered to have been inappropriately closed since June 2011. The closed valve isolated two differential pressure switches that impact the operation of E Low-Low Set Valve.<br><br> The apparent cause was determined to be a procedure change that had been made in 2005, including venting steps, which did not reflect differences in tailpipe configurations on the SRVs.<br><br> The immediate corrective action was to return the valve to the open position. Long-term corrective actions include revising the procedure to incorporate differences in SRV tailpipe configurations.
2632013002 | Monticello | 05/24/2013 | 07/23/2013 | ML13204A30 | <strong>Essential Bus Transfer During 2R Transformer Testing</strong><br /><i>Abstract:&nbsp;</i>On May 24, 2013, during performance of 4kV load testing on the new 2R-Transformer, operations was unable to observe red light indication for a 4 kV breaker either locally or in the Control Room following closure of the breaker. The lack of red light indication with the breaker closed is indication that the breaker will not be able to be tripped electrically, thus rendering all breaker protective trips and remote tripping from the Control Room unavailable. This resulted in the operators taking procedurally directed action to trip the breaker manually using the mechanical trip button, leading to the Essential Bus transfer. At the time, all credited safety systems were lined up to Division 2-4kV Essential Bus which was not affected by the event, as a defense-in-depth measure. <br><br> The apparent cause of the event was damage to a 4kV breaker which was the result of inadequate protection of the breaker during temporary storage. <br><br> A spare breaker was successfully tested and installed. Other breakers in temporary storage were inspected for potential damage. The long term corrective action is to revise the operations manual to provide additional guidance regarding the appropriate storage of breakers and to specify items requiring inspection prior to installation into switchgear cubicles.
2632013004 | Monticello | 06/13/2013 | 08/12/2013 | ML13225A50 | <strong>Loss of Normal Off-Site Power as a Result of Switchgear Fault</strong><br /><i>Abstract:&nbsp;</i>On June 13, 2013, at 14:31, the 2R Auxiliary Transformer unexpectedly locked-out resulting in a loss of normal offsite power. The lockout occurred due to a three phase arc fault in the 13.8kV switchgear to 11 bus. The 1R Transformer, Alternate power supply to station loads, was out of service at the time of the event. Essential loads were transferred automatically to the backup 4kV 1AR Transformer. <br><br> Emergency Diesel Generators started automatically as a result of the Loss of Normal Off-Site Power, but were not loaded as offsite power was available to the essential loads through 1AR Transformer. They were then shut down rendering them inoperable until the Fast Start capability was reset. The loss of normal off-site power caused a Group II Containment Isolation signal resulting in the loss of shutdown cooling. <br><br> No conclusive evidence has been found that would explain the cause of the 13.8kV arc fault; however, the most likely cause of the arc fault was a result of multiple, independent conditions. Operations was able to stabilize the plant, reset the containment isolation and restore shutdown cooling. <br><br> Immediate Actions taken following the event: <br> The 13.8kV room was quarantined until equipment investigation was complete. The 1AR Transformer, Emergency Diesel Generators and switchyard were protected under the Protected Equipment Program. The 1R Transformer was returned to service providing 4kV power.
2632013006 | Monticello | 08/21/2013 | 12/20/2013 | ML13353A69 | <strong>Unanalyzed Condition for Emergency Diesel Generator Fuel Oil Pumps Train Separation</strong><br /><i>Abstract:&nbsp;</i>On August 21, 2013, it was determined following receipt and review of NRC Task Interface Agreement 2012-03, that the design of the Monticello Nuclear Generating Plant (MNGP) diesel fuel oil supply system was not consistent with current and historical licensing and design basis documents. This condition affected the fuel oil supply from the diesel fuel oil storage tank to both emergency diesel generators. As a result, Northern States Power Minnesota submitted Event Notification 49293 for an unanalyzed condition.<br /><br /> The root cause for this event is that MNGP personnel institutionalized the acceptability of manual operator actions to meet single failure requirements in the diesel fuel oil system without formalizing it into an NRC docketed licensing basis.<br /><br /> The corrective action to address the root cause requires the Fleet Design Engineering Manager to review and revise the existing 10 CFR 50.59 and Time Critical Operator Action processes to ensure robust barriers are in place to prevent incorporating manual operator actions that do not comply with current licensing bases.
2632013007 | Monticello | 08/28/2013 | 01/27/2015 | ML15029A63 | <strong>Unanalyzed Condition due to Inadequate Flooding Procedures</strong><br /><i>Abstract:&nbsp;</i>On August 28, 2013, Northern States Power Minnesota (NSPM) was notified of the NRC's final significance determination for a finding involving the failure to maintain for the Monticello Nuclear Generating Plant (MNGP) a procedure addressing all of the effects of an external flooding scenario. Specifically, NSPM failed to maintain flood Procedure A.6, "Acts of Nature," for MNGP such that it could support the timely implementation of flood protection activities within the 12-day timeframe credited in the design basis as stated in the Updated Safety Analysis Report.<br /><br /> The finding is not a current safety concern. Actions have been completed to reduce the flood mitigation plan timeline to less than 12 days by developing an alternate plan for flood protection features, pre-staging equipment and materials, improving the quality of the Procedure A.6, and preplanning work orders necessary to carry out Procedure A.6 actions. Compliance was restored on January 31, 2014.<br /><br /> The root cause of this event was determined to be that, management did not ensure proper validation of the external flooding mitigation strategy design bases commensurate with safety significance which led to non-conservative decisions. The Corrective Actions to Prevent Recurrence are included in the body of this Licensee Event Report.
2632013008 | Monticello | 09/18/2013 | 03/12/2014 | ML14072A17 | <strong>Both Secondary Containment Access Doors Briefly Opened Simultaneously</strong><br /><i>Abstract:&nbsp;</i>On September 18, 2013, while performing the secondary containment airlock door interlock surveillance test, the interlock to the main plenum room did not prevent the opening of both doors to the plenum room airlock (DOOR-85 and DOOR-86). With the outer door to the main plenum room open, the inner door was able to be opened. The plenum airlock doors were then closed. The operator attempted a second time to verify the interlock functionality. This time the inner door was opened, and again the interlock did not prevent the opening of the outer door. The plenum airlock doors were immediately closed. <br /><br /> With both doors open, Technical Specification surveillance requirement 3.6.4.1.3 was not met and secondary containment was declared inoperable. Secondary containment was declared operable after independently verifying that at least one secondary containment access door was closed. There were no radiological releases associated with this event.
2662013001 | Point Beach 1 | 02/06/2013 | 04/05/2013 | ML13095A18 | <strong>Loss of Offsite Power to Unit 1 Safeguards Buses</strong><br /><i>Abstract:&nbsp;</i>On February 6, 2013 at 1132 CST, an undervoltage condition occurred on Unit 1, 1A-05 and 1A-06 safety-related buses, which was caused by a loss of 1X-03 high voltage station auxiliary transformer (HVSAT). The four emergency diesel generators (EDGs) started. The G01 and G03 EDGs loaded onto buses 1A-05 and 1A-06. Unit 2 maintained offsite power throughout the event. Unexpected operation of the 1F89-112 circuit switcher resulted in de-energization of the 1X-03 transformer causing a low voltage condition, which started the standby EDGs. The opening of the circuit switcher did not cause a lockout of 1X-03. As a result, the automatic transfer to the redundant offsite power supply in the switchyard was not initiated, and G01 and G03 EDGs automatically loaded onto Unit 1 safety-related buses 1A-05 and 1A-06, once they had reached operating voltage and frequency. This event is being reported pursuant to 10 CFR 50.73(a)(2)(iv)(A), any event or condition that resulted in a manual or automatic actuation of any of the systems listed in 10 CFR 50.73(a)(2)(iv)(B), including any event or condition that results in the actuation of the emergency AC electrical power system.
2662013002 | Point Beach 1 | 04/14/2013 | 06/13/2013 | ML13163A21 | <strong>Condition Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On April 13, 2013 at 23:39 PBNP Unit 1 entered Mode 4 during start up from a refueling outage. On April 14, 2013 at 0620, approximately 6 hours after entering into MODE 4, the Unit 1 sodium hydroxide tank outlet valve (1SI-831A) was found to be closed. This valve isolated the flow path for both trains of spray additive equipment and resulted in not meeting LCO 3.6.7, Spray Additive System. That mode change resulted in a violation of LCO 3.0.4.<br><br> The incorrect valve position was discovered when a senior reactor operator identified a caution tag on the 1SI-831A valve. Operations investigated the unexpected condition then immediately placed the valve in its proper position to meet the Technical Specification requirements.<br><br> This event is being reported pursuant to 10 CFR 50.73(a)(2)(v)(D) and 10 CFR 50.73(a)(2)(i)(B).
2692013001 | Oconee 1, Oconee 2, Oconee 3 | 02/06/2013 | 04/08/2013 | ML13101A30 | <strong>Inadequate HVAC Load Analysis and Design Impacts on Emergency Power Equipment</strong><br /><i>Abstract:&nbsp;</i>On 2/6/2013, with all three Oconee Units at 100 percent power, Oconee Nuclear Station (ONS) personnel concluded that emergency power equipment could be adversely impacted by a licensee identified original design issue involving inadequate analysis of electrical equipment heat loads and weaknesses in the Heating Ventilation & Air Conditioning (HVAC) system design. <br /><br /> The investigation determined that the principle causes were associated with inadequate and incomplete inputs and methods in development of HVAC systems during original plant design and HVAC system design practices that left the equipment in the Unit 1 and 2 Blockhouse, the Unit 3 Blockhouse, and the 230kV Switchyard Relay House susceptible to single failures. <br /><br /> Compensatory measures were put into place. Corrective actions include modifications to resolve the inadequacies with the original plant design issues. <br /><br /> This event is reportable under the following criteria: Operations Prohibited by Technical Specifications, Unanalyzed Condition, Event that could have prevented Fulfillment of a Safety Function, and Common Cause.
2692013002 | Oconee 1 | 06/26/2013 | 08/26/2013 | ML13242A08 | <strong>LPI and RBS Trains Inoperable When 1LP-21 Was Closed Due To Human Error</strong><br /><i>Abstract:&nbsp;</i>On June 26, 2013, Oconee Unit 1 was operating at 100% power in Mode 1 with the 1B train Low Pressure Injection (LPI) and Reactor Building Spray (RBS) out of service for scheduled maintenance and testing. Maintenance was performing Motor Operated Valve (MOV) testing on 1LP-22, which is the 1B train LPI and RBS pump suction valve from the Borated Water Storage Tank (BWST). With 1B train of LPI and RBS already declared inoperable, a licensed operator inadvertently closed 1LP-21 (the 1A train LPI and RBS pump suction valve), rendering both trains of LPI and RBS inoperable, and resulting in an unplanned Tech Spec 3.0.3 entry. The inadvertent action was immediately recognized by the licensed operator and after appropriate assessment and communication with shift personnel, the valve was reopened. <br /><br /> Tech Specs 3.5.3 and 3.6.5 require two trains of LPI and RBS to be operable in Mode 1. The duration of inoperability of 1A train LPI and RBS was approximately 13 minutes. This event was reported as an 8-hour notification to the NRC on June 26, 2013, in Event Notification (EN) number 49149 under 10 CFR 50.72(b)(3)(v)(A-D), "Event or Condition that Could Have Prevented Fulfillment of a Safety Function."
2692013003 | Oconee 1, Oconee 2, Oconee 3 | 09/04/2013 | 11/04/2013 | ML13312A00 | <strong>Keowee Hydroelectric Station Unit 2 - Emergency Power Lockout</strong><br /><i>Abstract:&nbsp;</i>On September 4, 2013, the Keowee Hydroelectric Station Unit 2 (KHU-2) experienced an emergency lockout that rendered it inoperable. The Keowee Hydroelectric Station is one of Oconee Nuclear Station's (ONS) emergency power sources. Following troubleshooting activities it was determined that from August 17, 2013 until September 4, 2013, KHU-2 had previously been susceptible to this type of emergency lockout resulting in a condition that exceeded the allowed outage time given in the plant's technical specifications.<br /><br /> An investigation of the event determined that the cause of the event was vibration from a Governor Oil pump that caused relay 86E2X to "chatter." The chatter generated a spurious signal that activated the emergency lockout relay.<br /><br /> A completed corrective action included the replacement of relay 86E2X and relocating it to an environment not susceptible to vibration.<br /><br /> This event is reportable under 10 CFR 50.73(a)(2)(i)(B) as an operation or condition prohibited by the plant's technical specifications. This event is considered to have minimal safety significance and no consequences with respect to the health and safety of the public.
2692013004 | Oconee 1 | 11/11/2013 | 02/19/2015 | ML15055A59 | <strong>High Cycle Fatigue Resulted in Reactor Coolant Leak and Unit Shutdown</strong><br /><i>Abstract:&nbsp;</i>On November 8, 2013, the Oconee Unit 1 Control Room received an alarm associated with the containment atmosphere particulate radiation monitor. Reactor Coolant System (RCS) leakage of <0.1 gpm was identified. On November 11, 2013, upon verification of un-isolable reactor coolant system pressure boundary leakage on the 1B2 High Pressure Injection (HPI) Injection line, Oconee Unit 1 was shut down as required by Technical Specifications. The shutdown was orderly and without complication. The cause evaluation determined that mechanical, high-cycle fatigue resulted in a through wall crack in the stainless steel butt weld between the HPI nozzle safe end and HPI piping. Ownership and oversight of the augmented examination program was inadequate, as was guidance to the examiners for actions to be taken when full weld volume coverage could not be achieved.<br /><br /> This event is reportable under 10 CFR 50.73(a)(2)(i)(A), as completion of a shutdown required by Technical Specifications, 10 CFR 50.73(a)(2)(i)(B), operation or condition prohibited by Technical Specifications, and 10 CFR 50.73(a)(2)(ii)(A), degradation of a principal safety barrier. High pressure injection capability was maintained, and containment integrity was not impacted. This report has been revised to reflect the results of the completed root cause evaluation.
2712013001 | Vermont Yankee | 03/19/2013 | 05/16/2013 | ML13141A40 | <strong>Potential to Flood Switchgear Rooms due to Missing Conduit Flood Seal</strong><br /><i>Abstract:&nbsp;</i>On March 19, 2013, with the plant in the cold shutdown condition during a refueling outage, Vermont Yankee discovered water from dredging operations inside two electrical manholes located in the Vital Switchgear Rooms. On March 23, 2013, it was identified that the water had entered the two manholes through a partially dislodged flood seal in an underground spare conduit that communicates with the Switchgear Room manholes. On March 27, 2013, during an extent of condition review, an additional water intrusion pathway into the Switchgear Rooms via an abandoned sump pump discharge line was discovered. The dislodged flood seal and sump pump discharge line compromised the interior flood design controls for the Switchgear Rooms. The causes of the dislodged flood seal were due to the seal not being conservatively sized or tested for the application it was used in and failure to take timely corrective actions following a similar event reported in LER 2012-001-01. The sump pump discharge line is a legacy issue. The conditions were corrected by installing a new flood seal of a different design and capping the sump pump discharge line, thus removing the potential flood paths. Plant procedure requires inspection of the Switchgear Rooms during a flood event and includes actions that would have mitigated any flooding; therefore, this event did not pose a threat to public health and safety.
2712013002 | Vermont Yankee | 11/07/2013 | 12/31/2013 | ML14010A07 | <strong>Potential to Flood Switchgear Rooms due to Missing Conduit Flood Seal</strong><br /><i>Abstract:&nbsp;</i>On November 6, 2013, with the plant at 100% Reactor Power, Vermont Yankee Nuclear Power Station (VY) identified a conduit containing a loose screw type conduit seal plug and another conduit with a missing seal inside electrical manhole MH-S2 located outside the Administrative Building. This was discovered during a routine preventative maintenance surveillance of flood seals. On November 7, 2013, it was identified that the missing flood seal compromised the flood design controls for the Switchgear Rooms. The conditions were corrected by installing silicone elastomer seals in the two affected spare conduits, thus removing the potential flood paths. The causes of the incorrect and missing flood seals were due to not completing the appropriate corrective actions following a similar event reported in LER 2013-001-00, dated May 16, 2013. Plant procedure requires inspection of the Switchgear Rooms during a flood event and includes actions that would have mitigated any flooding; therefore, this event did not pose a threat to public health and safety.
2722013001 | Salem 1 | 08/22/2013 | 10/21/2013 | ML13295A01 | <strong>Technical Specification Required Shutdown due to Exceeding Reactor Coolant System Unidentified Leakage Limit</strong><br /><i>Abstract:&nbsp;</i>This event is being reported under the requirements of 10 CFR 50.73(a)(2)(i)(A) for the completion of a nuclear plant shutdown required by the plant's Technical Specifications.<br /><br /> On August 22, 2013, at 1029, Salem Unit 1 was operating in Mode 1 at 100% power when operators responded to indications of reactor coolant leakage inside Containment. Reactor Coolant System unidentified leakage was subsequently estimated to be approximately 3.5 gallons per minute. Operators entered Technical Specification 3.4.6.2 Action Statement (b) which requires that unidentified leakage be reduced to within the limit of 1 gallon per minute within 4 hours or the plant be in at least Hot Standby within the next 6 hours and in Cold Shutdown within the following 30 hours.<br /><br /> A containment walkdown revealed the leakage source as packing leakage on Pressurizer Spray Valve 1PS1. Unit 1 commenced reducing load in accordance with operating procedures at 1628.<br /><br /> A 4-hour notification was made to the NRC at 1708, under 10 CFR 50.72(b)(2)(i) for "The initiation of any nuclear plant shutdown required by the plant's Technical Specifications." Unit 1 entered Hot Standby conditions at 2005.<br /><br /> Pressurizer Spray Valve 1PS1 was isolated at 2212 and a subsequent Reactor Coolant System water inventory balance indicated that unidentified leakage had reduced to 0.08 gallons per minute. Unit 1 exited Technical Specification 3.4.6.2 (b) on August 23, 2013 at 0159.
2722013003 | Salem 1 | 08/15/2013 | 10/10/2013 | ML13284A10 | <strong>1 Hour Security Event Report for Individual's Termination of Unescorted Access (60 Day Report)</strong><br /><i>Abstract:&nbsp;</i>On August 15, 2013, at 17:07, an individual's access authorization was "Terminated unfavorably and denied" in the Personnel Access Data System (PADS). The denial of access and termination was the result of validation of undisclosed medical information provided by an individual on August 12, 2013, at 09:30, on an individual employed by PSEG as an ILOT (Initial License Operator Training) candidate. This information, had it been disclosed at the time of the initial access investigation, would have resulted in denial of access. <br /><br /> As a result of validation of the information provided to PSEG, a one hour security event report was made to the NRC on August 15, 2013 at 12:07. Based on guidance contained in NRC Generic Letter 91-03, the report was made in accordance with 10 CFR 73.71 (b)(1) due to termination of an individual's unescorted access. This sixty day follow-up report is being submitted pursuant to the requirements of 10 CFR 73 Appendix G.l.
2722013004 | Salem 1, Salem 2 | 11/14/2013 | 01/10/2014 | ML14013A09 | <strong>Unfused DC Ammeter Circuits Result in an Unanalyzed Condition</strong><br /><i>Abstract:&nbsp;</i>On November 14, 2013, a review of industry operating experience identified a postulated fire induced circuit failure involving unfused DC ammeter circuits leading to a non-compliance with 10 CFR 50, Appendix R requirements. A review of Salem Unit 1 and Unit 2 DC ammeter circuits concluded that a similar configuration exists at both units in which the original plant wiring design and associated analyses for ammeters are not provided with overcurrent protection to limit fault current in the 250 Volt, 125 Volt and 28 Volt DC systems.<br /><br /> A postulated fire that results in a short to ground concurrent with an opposite polarity short from the same battery could result in excessive current flow in the ammeter wiring. This excessive current could result in a secondary fire in another fire area. The secondary fire could adversely affect safe shutdown equipment and cause a loss of alternate shutdown capability contrary to 10 CFR 50, Appendix R, Section III.G requirements.<br /><br /> Compensatory measures have been implemented in the affected areas of the plant and will remain in effect until the deficiency is corrected.
2752013001 | Diablo Canyon 1, Diablo Canyon 2 | 01/03/2013 | 04/04/2013 | ML13094A36 | <strong>Noncompliance with TS 3.4.12, "Low Temperature Overpressure Protection System" due to Human Error</strong><br /><i>Abstract:&nbsp;</i>On January 3, 2013, at 19:32 PST, with Units 1 and 2 in Mode 1 and at 100 percent power, Diablo Canyon Power Plant (DCPP) determined that the Limiting Condition for Operation of Technical Specification (TS) 3.4.12, low temperature overpressure protection system, was not met during Unit 1 and Unit 2 refueling outages over the past 3 years. Specifically, when TS 3.4.12 was applicable, DCPP operated with more than one centrifugal charging pump (CCP) capable of injecting into the reactor coolant system. DCPP determined this condition was reportable pursuant to 10 CFR 50.73(a)(2)(i)(B). The noncompliance was identified based on a Nuclear Regulatory Commission TS Interpretation letter dated January 3, 2013, to Wolf Creek Nuclear Operating Company. DCPP concluded that it had not complied with TS 3.4.12 since it replaced the positive displacement pump (PDP) with a CCP in Unit 1 (2005) and in Unit 2 (2007). Immediate corrective actions in response to this event included revising the affected procedures to ensure compliance with TS 3.4.12. The apparent cause for this event includes a deficiency in DCPP's 10 CFR 50.59 procedure and human error. The procedure did not provide guidance regarding proposed design changes that may maintain the original intent but create new literal compliance issues. The human error occurred when DCPP staff interpreted the operability requirements outlined in TS 3.4.12 as being equivalent with respect to the PDP to CCP design change. Corrective actions included revising the associated 10 CFR 50.59 procedure, revising the Current Licensing Basis Determination Procedure and providing a lessons-learned discussion to the staff. This event did not adversely affect the health and safety of the public.
2752013003 | Diablo Canyon 1, Diablo Canyon 2 | 06/23/2013 | 10/17/2013 | ML13291A12 | <strong>Actuation of Six Emergency Diesel Generators due to Loss of Offsite Power</strong><br /><i>Abstract:&nbsp;</i>On June 23, 2013, at 21:20 PDT, Pacific Gas and Electric Company (PG&E) lost its 230 kV offsite power source at the Diablo Canyon Power Plant (DCPP) when an offsite transmission system relay actuated. This resulted in the valid start of all Unit 1 and 2 emergency diesel generators (EDGs), three per unit. All EDGs successfully started, but did not load since all associated buses remained energized by auxiliary power. All systems operated as designed with no problems observed. The 230 kV offsite power source is the only offsite power system designed to be immediately available following an accident. However, the safety-related onsite EDGs would have provided power to mitigate the consequences of an accident while the 230 kV system was unavailable. On June 24, 2013, at 01:35 PDT, PG&E made an 8-hour nonemergency report to the NRC. <br /><br /> PG&E completed a root cause evaluation and determined that insulation, contamination, and weather issues at a grid substation located 11 miles North of DCPP caused the event. <br /><br /> This event did not adversely affect the health or safety of the public.
2752013004 | Diablo Canyon 1 | 06/23/2013 | 08/22/2013 | ML13235A10 | <strong>All Three Unit 1 Emergency Diesel Generators Momentarily Inoperable</strong><br /><i>Abstract:&nbsp;</i>On June 23, 2013, at 22:01 PDT, Pacific Gas and Electric Company (PG&E) Diablo Canyon Power Plant (DCPP) Unit 1 control room operators used an annunciator response procedure to address the loss of startup power. Contrary to Technical Specification, 3.8.1, plant operators made all three Unit 1 emergency diesel generators inoperable when they simultaneously placed all three emergency diesel generator control switches into manual control. On June 24, 2013, at 22:07 PDT, PG&E made an 8-hour, non-emergency report to the NRC (reference NRC Event Notification Number 49147). <br><br> DCPP determined that this was the result of inattention by control room operators, lack of oversight by the Shift Foreman, and an absence of cautionary instructions in the annunciator response procedure. <br><br> Plant management issued an Operations Shift Order that reinforces guidance and expectations for oversight, processed personnel accountability as appropriate, and will revise plant procedures for oversight and annunciator response. All actions are scheduled to be complete by September 26, 2013. <br><br> This event did not adversely affect the health or safety of the public.
2752013005 | Diablo Canyon 1 | 06/25/2013 | 08/22/2013 | ML13235A10 | <strong>Both Trains of Residual Heat Removal Inoperable Due to Circumferential Crack on a Socket Weld</strong><br /><i>Abstract:&nbsp;</i>On June 25, 2013, during a walkdown of the Diablo Canyon Power Plant (DCPP) Unit 1 containment, maintenance personnel noted an accumulation of boric acid on the inlet pipe to residual heat removal system relief valve RHR-1-RV-8708. Subsequent cleanup of the boric acid accumulation revealed an active leak of 3 drops per minute. A visual inspection identified that the source of the leak was a circumferential crack on the socket weld. <br><br> DCPP determined that system vibration induced a low-stress, high-cycle fatigue which caused the socket weld to fail. DCPP replaced the socket weld. The new weld has improved fatigue resistance over the original, equal-leg socket weld. Additionally, DCPP will install a new support to reduce the chances of piping vibration amplification by increasing its natural frequencies to significantly higher than the current resonant frequencies. <br><br> This condition did not adversely affect the health and safety of the public.
2752013006 | Diablo Canyon 1 | 08/15/2013 | 01/30/2014 | ML14030A48 | <strong>Emergency Diesel Generators Valid Start Signal Due to Loss of Startup Power</strong><br /><i>Abstract:&nbsp;</i>On August 15, 2013, at 18:24 PDT, Pacific Gas and Electric lost the 230 kV offsite power source to its Diablo Canyon Power Plant (DCPP), Unit 1, when the Startup Transformer (SUT) 1-1 load tap changer (LTC) diverter switch failed. This resulted in the valid start of all three Unit 1 emergency diesel generators (EDGs). The EDGs successfully started, but did not load, because the associated buses remained energized by the 500 kV auxiliary offsite power source. On August 16, 2013, at 02:36 EDT, DCPP made an 8-hour report to the NRC (NRC Event Notification Number 49287). <br /><br /> A failed bolted connection between a flex link and a stationary contact caused the SUT LTC diverter switch to fail. It was determined that the bolted connection failed because the vendor did not adequately torque the connection during assembly and installation. Corrective action includes the revision of SUT LTC maintenance instructions to include bolted termination torque specifications. Additionally, DCPP will include replacement parts material checks in procurement or work planning documents for future LTC maintenance. <br /><br /> This event did not adversely affect the health or safety of the public.
2752013007 | Diablo Canyon 1 | 10/14/2013 | 12/12/2013 | ML13350A58 | <strong>Licensee Event Report 1-2013-007-00, Auxiliary Feedwater Actuation due to a Main Feedwater Pump Trip</strong><br /><i>Abstract:&nbsp;</i>On October 14, 2013, at 15:11 PDT, with Diablo Canyon Power Plant (DCPP) Unit 1 in Mode 1 at 100 percent power, Main Feedwater Pump 1-1 tripped. This event began when a 480 V bus overcurrent relay tripped during relay maintenance and caused a loss of control oil pressure which resulted in a main feedwater pump trip. In response, plant operators controlled a ramp from 100 percent to 50 percent power and manually started the auxiliary feedwater pumps per plant procedures and conditions. The auxiliary feedwater system actuation was reported in accordance with 10 CFR 50.72(b)(3)(iv)(a) in NRC Event Notification 49442.<br /><br /> DCPP determined that the cause of the relay trip was failure to incorporate operating experience in the relay maintenance procedure. Similar inservice relay testing was halted until the procedure is updated. DCPP determined that the main feedwater pump trip occurred due to loss of power to the in-service control pump (caused by the 480 V bus deenergization) and the inability of the backup control oil system to respond quickly enough due to nitrogen pre-charge leakage from an accumulator bladder. The bladder was replaced and the system tested. Other corrective actions are also being implemented. This event did not adversely affect the health or safety of the public.
2752013008 | Diablo Canyon 1 | 11/19/2013 | 01/16/2014 | ML14016A50 | <strong>Technical Specification 3.3.4 Not Met due to Inoperable Remote Shutdown System Function</strong><br /><i>Abstract:&nbsp;</i>On November 19, 2013, Diablo Canyon Power Plant (DCPP) maintenance technicians were conducting relay testing on Emergency Diesel Generator (EDG) 1-3 Output Breaker 52HF7, and discovered the breaker could not be closed locally. Maintenance personnel found the US fuses in the 52HF7 cubicle in the OFF position. With the US fuses in the OFF position, operators would not be able to close EDG 1-3 output breaker at the breaker cubicle unless they opened the breaker cubicle and manually closed the breaker. This manual operation is not proceduralized, so successful performance of this task could not be guaranteed. Local breaker closure capability is required to satisfy Technical Specification 3.3.4 remote shutdown functionality.<br /><br /> DCPP determined a failure to maintain adequate configuration control of the US fuses in the 52HF7 cubicle during refueling outage maintenance activities allowed the fuses to be installed in the incorrect position. DCPP restored the US fuses to the correct position and checked the positions of the US fuses in the other EDG output breaker cubicles.<br /><br /> This condition did not adversely affect the health and safety of the public.
2752013009 | Diablo Canyon 1 | 12/14/2013 | 05/14/2014 | ML14135A00 | <strong>Unanalyzed Condition Affecting Unit 1 Emergency Diesel Generators</strong><br /><i>Abstract:&nbsp;</i>On December 14, 2013, at 15:03 PST, with Diablo Canyon Power Plant (DCPP) Unit 1 operating in Mode 1 at approximately 100 percent power, engineers identified a vulnerability to extreme weather. A combination of sustained high winds over 60 miles per hour and ambient air temperatures exceeding 97°F could reduce cooling capacity such that the emergency diesel generators would exceed design limits, contrary to the requirements of General Design Criteria (GDC) 2. On December 14, 2013, at 16:32 PST, DCPP made an 8-hour, non-emergency report to the NRC (reference NRC Event Notification Number 49634) per 10 CFR 50.72(b)(3)(ii)(B).<br /><br /> Upon identification of this condition, shift orders were issued that require, when conditions warrant, the implementation of existing procedural guidance to open plant doors. This will allow additional air flow, shown to provide adequate emergency diesel generator cooling to support continuous operation of the Unit 1 emergency diesel generators.<br /><br /> An apparent cause evaluation concluded that PG&E did not have a design process requirement in place to evaluate GDC-2 design criteria relative to SSC functional requirements other than for structural integrity issues. Plant procedures were revised to include this requirement and PG&E will issue a design change to permanently modify the plant to resolve the wind issue.<br /><br /> This event did not adversely affect the health or safety of the public.
2752013010 | Diablo Canyon 1 | 12/19/2013 | 02/18/2014 | ML14049A41 | <strong>Two Emergency Diesel Generators Inoperable due to Operator Error</strong><br /><i>Abstract:&nbsp;</i>On December 19, 2013, Diablo Canyon Power Plant was conducting post maintenance testing on Emergency Diesel Generator (EDG) 1-2. While EDG 1-2 was still inoperable, a field operator inspected EDG 1-3 in order to familiarize himself with the location of a drive belt he would be inspecting at the next step of EDG 1-2 testing. At approximately 0752 PDT, the operator inadvertently caught his foot on the fuel oil priming pump fuel line which snagged and broke. This resulted in a second inoperable EDG on Unit 1, and constituted a reportable unanalyzed condition that significantly degraded plant safety and a condition that could have prevented the fulfillment of a safety function that is needed to mitigate the consequences of an accident. Reference EN 49663. On December 19, 2013, at 0953 PST, operators completed EDG 1-2 testing and declared it operable. At the time of the event, both offsite power circuits were operable.<br /><br /> The cause of the event was identified as a knowledge gap - Operators did not have adequate knowledge of the published standards to prevent inadvertent operational events. Corrective actions included issuing Operations Standing Orders and Shift Orders emphasizing the standards as they apply to operators.<br /><br /> This condition did not adversely affect the health and safety of the public.
2782013001 | Peach Bottom 3 | 10/01/2013 | 11/22/2013 | ML13326B06 | <strong>Laboratory Analysis Identifies Safety Relief Valves and Safety Valve Set Point Deficiencies</strong><br /><i>Abstract:&nbsp;</i>Based on information received from a laboratory performing Main Steam Safety Relief Valve (SRV) / Safety Valve (SV) as-found testing, Site Engineering personnel determined on 10/01/13 that SRV / SV setpoint deficiencies existed with four SRVs and one SV that were in place during the Unit 3 19th operating cycle. The SRVs / SV were determined to have their as-found setpoints outside of the Technical Specification allowable ± 1% tolerance. All relief valves outside of their Technical Specification (TS) allowable setpoint range were within the ASME Code allowable ± 3% tolerance. The cause of the SRVs / SV being outside of their allowable as-found setpoints is due to setpoint drift. The SRVs / SV have been replaced with refurbished SRVs / SV for the 20th Unit 3 operating cycle. There have been previous LERs identified involving SRVs / SVs exceeding their Technical Specification ± 1% setpoint requirement. A license amendment request (LAR) was submitted to the NRC in June 2013 to modify the allowable setpoint from ± 1% to ± 3%, which is consistent with the setpoint typically used in the industry.<br /><br /> There were no actual safety consequences associated with this event.
2802013001 | Surry 1, Surry 2 | 12/06/2012 | 01/30/2013 | ML13042A40 | <strong>Lack of Established Method Results in Detached Lead and Inoperable Emergency Diesel Generator</strong><br /><i>Abstract:&nbsp;</i>On December 6, 2012 at 11:15, with Surry Power Station Unit 1 at 100 and Unit 2 at 98 percent power, the monthly start test for Emergency Diesel Generator (EDG) 3 found the incoming voltage higher than expected. Following an unsuccessful attempt to lower voltage, the diesel was secured at 11:37. A lead associated with a relay in the voltage regulator circuit was found detached. The lead was reconnected, the generator tested satisfactorily, and EDG 3 was declared operable at 03:39 on December 7, 2012. The most probable cause was the inadvertent disconnection of the lead during removal of a data acquisition system after the previous run of EDG 3 on November 3, 2012. An evaluation determined EDG 3 could not perform its function with the lead detached. Therefore, EDG 3 was considered to be inoperable from November 3 until December 7, 2012, exceeding the Technical Specification limiting condition for operation (LCO). This report is being submitted pursuant to 10CFR50.73(a)(2)(i)(B), any operation or condition prohibited by the plant's Technical Specifications. In addition, the second train of emergency power for each unit was inoperable for testing while EDG 3 was inoperable and is reportable pursuant to 10CFR50.73(a)(2)(v)(D). This event did not affect the health and safety of the public.
2812013001 | Surry 2, Surry 1 | 12/29/2012 | 02/15/2013 | ML13056A41 | <strong>Bird Contacting Power Lines Results in Emergency Diesel Generator Auto-Start</strong><br /><i>Abstract:&nbsp;</i>At 08:03 on December 29, 2012, with both Unit 1 and Unit 2 operating at 100%, the supply breaker to the B reserve station service transformer (RSST) tripped open on an instantaneous over-current of the B and C phases due to a pelican contacting the overhead lines from the switchyard to the B RSST. This resulted in a lockout of the B RSST and loss of power to the E transfer bus and the Unit 2 H emergency bus from its normal off-site power supply. An under-voltage auto start signal was generated, and emergency diesel generator (EDG) 2 started and loaded on the Unit 2 H emergency bus as designed. Equipment performed as expected during the event, and there were no unexplained occurrences. Visual inspections verified there was no damage to the lines, supply breaker, or B RSST. The E transfer bus was reenergized at 12:23, and the normal source of power was restored to Unit 2 H emergency bus at 12:42. EDG 2 was returned to auto at 15:18. All electrical distribution systems were restored to a normal alignment. The work management process has been initiated to install bird diverters on the lines. This report is being submitted, pursuant to 10 CFR 50.73 (a)(2)(iv)(A), for automatic actuation of EDG 2. This event did not affect the health and safety of the public.
2812013002 | Surry 2 | 06/23/2013 | 08/16/2013 | ML13239A43 | <strong>Partially Open Valve Results in Pump Inoperability that Exceeded Technical Specifications Actions</strong><br /><i>Abstract:&nbsp;</i>At 21:00 on June 23, 2013, with both Unit 1 and Unit 2 operating at 100%, an operator identified a discrepancy with the valve position on the Unit 2 Turbine Driven Auxiliary Feedwater Pump turbine trip throttle valve. The apparent cause of the Unit 2 trip throttle valve abnormal position is thread wear between the screw spindle (stem) and sliding nut. The vibrations from infrequently running adjacent equipment caused the valve to move in a closed direction. The trip throttle valve was returned to open and the handwheel secured in the open position. Due to partial closure of the trip throttle valve, the Unit 2 Turbine Driven Auxiliary Feedwater Pump was determined to be inoperable for greater than the Technical Specification limiting condition of operation and therefore, this report is being submitted, pursuant to 10 CFR 50.73(a)(2)(i)(B) for operation prohibited by Technical Specifications. Based on an assessment of this event, the risk impact was determined to be very small and, as a result, the health and safety of the public were not affected.
2822013001 | Prairie Island 1, Prairie Island 2 | 08/09/2013 | 10/08/2013 | ML13282A56 | <strong>Control Room Envelope Inoperable</strong><br /><i>Abstract:&nbsp;</i>In December 2010, Control Room Envelope (CRE) testing was conducted to satisfy Surveillance Requirements (SR) 3.7.10.5. At that time, as a prequisite, the surveillance procedure contained a step to add water to two floor drains loop seals located in the 121and 122 Safeguards Chiller Room that penetrated the CRE. <br /><br /> On August 9, 2013, this practice was determined to be unacceptable preconditioning. Because the December 2010, surveillance test was the first performance of this surveillance, the unacceptable preconditioning resulted in a never performed surveillance, failure to meet the associated surveillance requirement, and an inoperable CRE. <br /><br /> On September 13, 2013, the CRE was tested and failed due to excessive in-leakage from Control Damper CD-34177. This condition is reportable per 10 CFR 50.73(a)(2)(v)(C), event or condition that could have prevented fulfillment of a safety function and 10 CFR 50.73(a)(2)(i)(B), operation or condition prohibited by Technical Specification. <br /><br /> Based on engineering's past operability evaluation with the equipment history of CD-34177, the CRE was inoperable from December 10, 2010. The Technical Specification Required Action Statement for 3.7.10 Condition B was exited on September 18, 2013.
2852013001 | Fort Calhoun | 12/21/2012 | 03/19/2013 | ML13078A05 | <strong>Mounting of GE HFA Relays Does Not Meet Seismic Requirements</strong><br /><i>Abstract:&nbsp;</i>On January 15, 2013, while reviewing a previous condition report, it was identified that a previous operability determination (OD) completed for General Electric (GE) model HFA relays was incorrect in that it did not appear to fully address the condition of the mounting screws that required torqueing. The seismic test results stated that the GE HFA relays passed the seismic testing, but the relays required two screws to be torqued to 5 foot-pounds. This condition of the additional required torqueing was initially entered into the corrective action program on December 21, 2012. Currently, approximately 136 relays, that provide various indication and control functions in systems such as high pressure safety injection, charging, containment ventilation, and the emergency diesel generator, have been identified as potentially affected. Relay replacement/torqueing is in progress. A cause analysis is in progress, the results of which will be published in a supplement to this LER.
2852013002 | Fort Calhoun | 01/25/2013 | 06/28/2013 | ML13182A68 | <strong>CVCS Class 1 & 2 Charging Supports are Unanalyzed</strong><br /><i>Abstract:&nbsp;</i>On January 25, 2013, while developing the modification to replace a portion of the Chemical and Volume Control System (CVCS) piping in containment, it was identified that the original piping supports had no calculations of record. When the calculations for the replacement piping were completed using the original support configuration, an overstress condition of the new piping was identified that directly related to the old piping. This condition would have made the original piping susceptible to failure during a seismic event. Portions of the Class 1 charging and letdown lines were affected. The plant was shutdown and defueled at the time of discovery. <br><br> The causal analysis determined that station construction project management failed to ensure that initial construction procedures for design and installation of small bore piping systems and supports were in compliance with USA Standard B31.7, Nuclear Power Piping. <br><br> Fort Calhoun Station will analyze and modify the supports as required to conform to the piping load requirements of the various operational Modes prior to entering that Mode.
2852013003 | Fort Calhoun | 01/30/2013 | 04/01/2013 | ML13091A22 | <strong>Calculations Indicate the HPSI Pumps will Operate in Run-out During a DBA</strong><br /><i>Abstract:&nbsp;</i>At approximately 1721 Central Standard Time, on January 30, 2013, during hydraulic evaluations for the alternate hot leg injection project, Design Engineering determined that design basis calculations indicated that the high pressure safety injection (HPSI) pumps would operate in a run-out condition under worst case design basis accident conditions. Previous changes to the operation of the HPSI pumps and the containment spray pumps have resulted in an increase in the injection phase time and an increase in HPSI pump flow during the accident. This could have resulted in the HPSI pumps operating in run-out for longer than the one hour manufacturer's recommended time limit. A preliminary causal analysis identified that the station failed to obtain vendor technical information on HPSI pump performance in a 10 CFR 50, Appendix B, Quality Assurance validated format. An analysis of HPSI pump performance during the injection phase will be performed and design or procedural actions to prevent HPSI pump operation in the extended flow region and to ensure that sufficient net positive suction head is available will be taken.
2852013004 | Fort Calhoun | 02/22/2013 | 04/23/2013 | ML13114A16 | <strong>Inverters Inoperable During Emergency Diesel Generator Operation</strong><br /><i>Abstract:&nbsp;</i>On February 22, 2013, while performing testing of the diesel generators in accordance with OP-ST-ESF-0002, the Ametek inverters “A” and “C,” instrument bus “A” and “C” Low Voltage/Ground alarms came in and cleared repeatedly. A slight smell of smoke was detected by several personnel in the Control Room in the vicinity of AI-40A. The following equipment had failed and/or was damaged: LIC-2802, PIC-2802, A/PIA-102X, C-VOPT and possibly one or more of the CCW HX/RW temperature meters.<br><br> Fort Calhoun had replaced the original Elgar inverters with new Ametek SCI inverters during the 2008 refueling outage. After installation continuing intermittent inverter trouble alarms and instrument bus low voltage/ground alarms occurred when loads are placed on or removed from various a-c buses. A design change completed in April of 2011 removed a ground connection between two capacitors in the inverters. However, testing of the modification was not completed before the 2011 flood and the station did not operate with the modification installed. A causal analysis is in progress and the results of the analysis will be published in a supplement to this LER.
2852013005 | Fort Calhoun | 02/27/2013 | 07/31/2013 | ML13213A06 | <strong>Control Room HVAC Modification Not Properly Evaluated</strong><br /><i>Abstract:&nbsp;</i>On February 27, 2013, while reviewing a response to an NRC question, an issue was identified where the modification which moved the control room air conditioners condensers from inside the control room to the auxiliary building roof should have obtained prior NRC approval. The condensers are located in close proximity to one another and are protected by a grating that is not rated to withstand a tornado missile. Therefore, it is possible that both the A and B trains could be struck and rendered inoperable by the same missile. The review determined that prior NRC approval had not been obtained for the modification and the condition was entered in to the station's corrective action program. At the time of discovery, the unit was shutdown with fuel removed.<br><br> In 1995, organizational work practices lacked technical rigor, resulting in FCS personnel incorrectly concluding that an NRC approved probability methodology for tornado missile protection could be applied to an FCS plant modification via the 50.59 process without obtaining a license amendment.<br><br> Missile will be provided to comply with the station’s license, as recently amended, prior to plant heatup. Additional corrective actions will be administered by the corrective action process.
2852013006 | Fort Calhoun | 03/02/2013 | 08/26/2013 | ML13239A12 | <strong>Use of Teflon in LPSI and CS Pump Mechanical Seals</strong><br /><i>Abstract:&nbsp;</i>On March 04, 2013, at approximately 1400 CST, while researching requirements for the replacement parts, it was identified that the mechanical seals used in the two low pressure safety injection pumps and the three containment spray pumps are made of a material (Teflon®) that may not maintain the designed integrity of the systems under certain accident conditions. This design has been installed since original plant construction. This issue was discovered while the core was off-loaded.<br /><br /> A causal analysis determined that Omaha Public Power District and its consulting engineering firm failed to specify a compatible material for the pump seals in the original construction specifications.<br /><br /> Replacement of pump seals is scheduled to be completed prior to startup. A review of PED-GEI-10, Material Compatibility Review, will be performed to ensure the restrictions placed on the use of Teflon® are appropriate and a review of engineering change checklists will be performed to ensure the PED-GEI-10 restrictions are preserved.
2852013007 | Fort Calhoun | 04/06/2013 | 08/16/2013 | ML13231A01 | <strong>Containment Air Cooling Units (VA-16A/B) Seismic Criteria</strong><br /><i>Abstract:&nbsp;</i>Condition Report (CR) 2013-02260 identified that a summary structural analysis (FC03901) indicated that VA-15A/B (Containment Air Cooler/Filter) plenum was overstressed by 100 percent and that VA-16A/B (Containment Air Cooler) plenum would have been overstressed during a design basis seismic event. At the time of discovery, FC03901 indicated that VA-15A/B required cross-bracing, which was added resulting in the equipment being operable. Since VA-16A/B was overstressed, they were considered inoperable. <br /><br /> The causal analysis determined that the design basis information was incomplete at the beginning of commercial operation. A weakness in licensing basis knowledge and a failure to internalize the importance of the design basis, resulted in the organization missing repeated opportunities to correct the initial deficiencies and additional errors were created over time. Also, the early culture established standards and expectations for the organization that resulted in behaviors demonstrating that the operation of the facility was more important than maintaining the license and design basis of the Station. This resulted in long-standing, reinforced, and institutionalized behaviors that resisted external and internal efforts to change. <br /><br /> The VA-16A/B plenums will be restored to an operable condition. Additional corrective actions will be tracked by the corrective action process.
2852013008 | Fort Calhoun | 04/11/2013 | 12/18/2013 | ML13353A47 | <strong>Previously Installed GE IVA Relays Failed Seismic Testing</strong><br /><i>Abstract:&nbsp;</i>On April 11, 2013, the test results of seven General Electric (GE) IVA relays, indicated that three safety-related, seismically qualified, relays did not pass seismic testing. The condition was entered in to the Station's corrective action program. A causal analysis determined that the failure was caused by the control spring in the relay contacting either the disk or the drag magnet during seismic testing resulting in a short. A wire used to support the spring was not installed in the relays that failed the testing allowing the control spring to sag and make electrical contact.<br /><br /> There are a total of 45 GE IVA relays identified in the plant, of which 32 are safety-related. Twenty-seven of the relays required replacement due to missing the support wire.
2852013009 | Fort Calhoun | 04/16/2013 | 06/14/2013 | ML13168A37 | <strong>Tornado Missile Vulnerabilities</strong><br /><i>Abstract:&nbsp;</i>While performing an extent of condition review for the condition identified in LER 2013-005-0, Control Room HVAC Modification Did Not Properly Address Safety Consequences, additional potential tornado missile vulnerabilities have been identified. These currently include the intake structure removable hatches, Room 81 roof openings, auxiliary feedwater steam driven pump exhaust stack, diesel fuel oil tanks vent stack and fill line, FO-1/FO-10, raw water pump cable pull boxes, and diesel generator exhaust stacks, DG-1/DG-2. These additional interactions appear to have existed since initial licensing. They do not appear to be a result of plant modifications as was the case with the control room air handlers. At the time of discovery, the unit was shutdown and defueled. <br><br> The station is performing extent of condition reviews associated with LER 2013-005-0. The station will determine the scope and resolutions to mitigate the currently identified interactions as well as any additional interactions prior to plant restart.
2852013010 | Fort Calhoun | 05/03/2013 | 10/23/2013 | ML13298A16 | <strong>HPSI Pump Flow Imbalance</strong><br /><i>Abstract:&nbsp;</i>On May 03, 2013, at approximately 1759 CST, station personnel identified that the high pressure safety injection (HPSI) pump injection flows to the reactor coolant system were not balanced in accordance with the Fort Calhoun Station (FCS) Updated Safety Analysis Report. When discovered, FCS was shutdown with fuel removed from the vessel.<br /><br /> The cause of the event was determined to be the emergency core cooling system pre-operational testing (1972) to balance HPSI system flow and record loop injection valve positions was not adequately translated into design documents. This resulted in the periodic flow balance requirements not being sustained. It was also identified that engineers had limited understanding of HPSI system flow balance design and unclear or incomplete HPSI design basis documents inhibited understanding of the reason for HPSI flow balance.<br /><br /> HPSI flow to the reactor coolant loops has been balanced and a testing procedure will be developed to periodically verify that HPSI injection flow into the four reactor coolant loops remains balanced.
2852013011 | Fort Calhoun | 06/13/2013 | 08/12/2013 | ML13225A36 | <strong>Inadequate Design for High Energy Line Break in Rooms 13 and 19 of the Auxiliary Building</strong><br /><i>Abstract:&nbsp;</i>During review of the analyses for high energy line breaks two deficiencies were identified. On June 13, 2013, an unevaluated break in the steam supply to the auxiliary feedwater turbine inside Room 19 was identified. Subsequently, on June 14, 2013, a deficiency was identified with verifying that the Electrical Equipment Qualification (EEQ) Program met all the criteria for establishing pipe rupture locations in Room 13. <br><br> The Root Cause Analysis resulted in two causes. Fort Calhoun Station’s responses to IE Bulletin 79-01B made inaccurate and simplifying assumptions, without supporting documentation, that compromised the validity and scope of the EEQ Program, ultimately resulting in the program being non-compliant with 10 CFR 50.49. Additionally, the EEQ Program has unique processes that are not integrated into the Engineering Change Process and impacts the sustainability of the EEQ Program. <br><br> The required analyses will be performed, required modifications completed, and supporting documentation (including program documents) updated as required. EEQ procedures will be revised such that all EEQ engineering activities are performed under the Station's configuration change control process. Additional corrective actions will be implemented using the station's corrective action program.
2852013012 | Fort Calhoun | 08/02/2013 | 09/30/2013 | ML13274A63 | <strong>Intake Structure Crane Seismic Qualification</strong><br /><i>Abstract:&nbsp;</i>On August 2, 2013, Fort Calhoun Station (FCS) Engineering identified that the intake structure crane (HE-5) seismic analysis assumes that the crane is not in operation with the hood retracted and in the parked position. The seismic analysis does not evaluate the crane's ability to withstand a seismic event when in use and an investigation identified that HE-5 was used when the raw water pumps were required to be operable. When discovered, FCS was shutdown in MODE 5. <br /><br /> The crane was not in use when the condition was identified and was verified in the parked position. Compensatory actions were identified to which would allow the use of the intake crane. The condition was entered into the station's corrective action program as Condition Report 2013-15474. A new seismic analysis to address crane use will be developed.
2852013013 | Fort Calhoun | 10/18/2012 | 12/02/2013 | ML13337A45 | <strong>Unqualified Components Used in Safety System Control Circuit</strong><br /><i>Abstract:&nbsp;</i>On October 3, 2013 station personnel identified that a condition with the control loop for HCV-1369, Turbine-Driven Auxiliary Feedwater Pump FW-10 Recirculation Valve, was incorrectly evaluated as not reportable. The original condition was identified on October 18, 2012, which identified unqualified components in the control loop whose failure could cause a spurious closure of HCV-1369 and result in pump damage. The station was shutdown in MODE 5 when discovered.<br /><br /> The condition was entered in to the station's corrective action program as Condition Report 2013-18752. Engineering is reviewing this condition and the results of this review will be used to update this report.
2852013014 | Fort Calhoun | 10/18/2012 | 01/29/2015 | ML15029A71 | <strong>Unqualified Components Used in Safety System Control Circuit</strong><br /><i>Abstract:&nbsp;</i>In October of 2012, condition report 2012-15755 identified that an inadvertent closure of the steam driven auxiliary feedwater recirculation valve, FCV-1369, could cause steam driven auxiliary feedwater pump, FW-10, damage. This scenario could result in pump damage due to dead heading FW-10. FCV-1369 is not a safety related component. The station was shutdown in MODE 5 when this condition was discovered.<br /><br /> The apparent cause was determined to be that the processes used for design and modification of systems, structures, and components do not use explicit and systematic failure mode analysis when adding, deleting, or modifying safety-related system design allowing credible failure modes to not be considered during design and modification.<br /><br /> FCV-1369 has been opened by isolating operating air to the valve, to ensure the operability of FW-10 for the current operating cycle. Appropriate components associated with FCV-1369 will be upgraded or otherwise evaluated to resolve the issue.
2852013015 | Fort Calhoun | 09/23/2013 | 02/14/2014 | ML14048A00 | <strong>Unqualified Coating Used as a Water Tight Barrier in Rooms 81 and 82</strong><br /><i>Abstract:&nbsp;</i>On September 23, 2013, it was identified that the floor structure in Rooms 81 and 82 may not maintain its integrity during a high energy line break environment allowing water to migrate into the rooms below that houses the diesel generators and safety related switchgear. This was reported on September 23, 2013, under 10 CFR 50.72(b)(3)(ii)(B), Unanalyzed Condition (Event Notification 49378). Fort Calhoun Station was shutdown in MODE 5 when the condition was identified and entered into the station's corrective action program as Condition Report 2013-18103.<br /><br /> A cause evaluation was completed and determined that corrective actions in CR 2009-0687 root cause analysis (RCA) did not resolve water intrusion into Auxiliary Building rooms containing safety related equipment due to lack of technical rigor and flawed decision making.<br /><br /> The floor in Room 82 was recoated. The seismic gap between containment and the auxiliary building was sealed. All penetrations that had openings below 2 feet above the floor were coated and the area around the impingement plate was sealed. Cracks in the ceilings of the switchgear and upper electrical penetration rooms were repaired.
2852013016 | Fort Calhoun | 11/05/2013 | 01/06/2014 | ML14015A37 | <strong>Reporting of Additional High Energy Line Break Concerns</strong><br /><i>Abstract:&nbsp;</i>On October 18, 2013, as part of an extent of condition for LERs 2012-017 and 2013-011, Fort Calhoun Station (FCS) personnel identified a potential additional high energy line break (HELB) concern with the piping associated with the letdown heat exchanger (LDHX). Subsequently on November 5, 11, 16, and 20, additional HELB impacts were also identified. These impacts involved increased loads on supports in the piping subsystem MS-4099 (main steam supply to FW-10), high energy line cracking (HELC) related to auxiliary steam in various rooms in the power block, the assumptions made regarding diesel generator operability during a HELB, and the quality of the steam to FW-10, the steam-driven auxiliary feedwater pump.<br /><br /> It was previously determined and reported that FCS did not fully implement and/or maintain the Electrical Equipment Qualification (EEQ) program to meet the requirements of 10 CFR 50.49. As a consequence, the equipment included in the EEQ program, the systems included in the High Energy Line Break (HELB) Analysis and the environmental conditions used by the EEQ program have not been maintained current or in an auditable manner. In addtion to the corrective actions (CA) to resolve the EEQ/HELB program issues previously reported, additional CAs are being pursued to address the indiviual conditions listed above.
2852013017 | Fort Calhoun | 10/31/2013 | 12/27/2013 | ML13361A20 | <strong>Containment Spray Pump Design Documents Do Not Support Operation in Runout</strong><br /><i>Abstract:&nbsp;</i>Fort Calhoun Station (FCS) has identified that design basis documents for the containment spray (CS) pumps SI-3A, SI-3B and SI-3C did not fully support pump operation during runout conditions which could occur under certain system configurations. On October 31, 2013, additional design work was completed which showed that the CS pumps would not meet their required mission time under specific accident scenarios. However, the analysis also showed that the containment peak pressure for the limiting design basis accident occurs at 202.3 seconds, which is prior to the CS delay time of 228.2 seconds. Therefore, the peak containment pressure would not be affected by this failure.<br /><br /> FCS has completed a calculation necessary to support a temporary modification which throttles the CS pump discharge valves to increase system resistance. A new CS pump curve has been issued to include operation in the extended pump operating range. A permanent modification to prevent CS pump runout is being pursued.
2852013018 | Fort Calhoun | 10/28/2013 | 12/26/2013 | ML13361A21 | <strong>Postulated Fire Event Could Result in Shorts Impacting Safe Shutdown</strong><br /><i>Abstract:&nbsp;</i>On October 9, 2013, an event notification applicable to Callaway Nuclear Power Plant was posted that documented a postulated fire event regarding the impact of unfused direct current (DC) ammeter circuits in the control room (CR). In the postulated event, a fire in the CR could cause one of the ammeter wires to short to the ground plane. Simultaneously, if the fire causes another DC wire from the opposite polarity on the same battery to also short to the ground plane, a ground loop would be established through the unprotected ammeter wiring. This event could result in excessive current flow (heating) in the ammeter wiring to the point of causing a secondary fire in the raceway system. The secondary fire could adversely affect safe shutdown equipment and potentially result in the loss of the ability to conduct a safe shutdown as required by 10 CFR50 Appendix R. Plant engineering personnel reviewed the information against station electrical schematics and at approximately 1230 CDT on October 28, 2013, an 8-hour notification was made pursuant to 10 FR 50.72(b)(3)(ii)(B). The station was in Mode 5 when the condition was identified.<br /><br /> An hourly fire watch was established in the affected locations of the station. FCS will install fuses in the DC ammeter circuitry as determined by Engineering Change 62826, Add Fuses to the DC Ammeter Circuitry for Ammeters.
2852013019 | Fort Calhoun | 12/02/2013 | 01/31/2014 | ML14031A34 | <strong>Non-Seismic Circulating Water Pipe Could Disable Raw Water Pumps</strong><br /><i>Abstract:&nbsp;</i>On December 2, 2013, NRC inspectors questioned the validity of an operability determination performed by the station on a non-safety grade pipe in the Raw Water pump vaults. The concern was determined to be valid and on December 3, 2013 at 0038 CST, an operability evaluation for Condition Report (CR) 2013-22090 confirmed operability of the RW pumps with interim actions to prevent CW flow from the affected 12" pipe into the RW vault during a seismic event. Interim compensatory actions to maintain operability of the raw water pumps are to secure the screen wash system and establish a clearance. <br /><br /> A cause analysis is in progress and an update to this LER will be provided with additional information. <br /><br /> A design change was completed to the station to eliminate the adverse interaction noted above.
2862013002 | Indian Point 3 | 03/04/2013 | 04/29/2013 | ML13141A25 | <strong>Safety System Functional Failure and Common Cause Inoperability of the Emergency Core Cooling System due to Violation of Containment Sump Debris Barrier Integrity</strong><br /><i>Abstract:&nbsp;</i>On March 4, 2013, during shutdown for a refueling outage, Radiation Protection (RP) personnel entered the reactor containment building to install plastic RP fencing for the Reactor Coolant Drain Tank (RCDT). After receiving clearance at Mode 4 to enter the Inner Crane Wall (ICW) to install fencing around the RCDT and post it as a Locked High Radiation Area (LHRA). The RP work crew assumed they could enter the ICW area through any sump barrier gate for the Emergency Core Cooling System (ECCS). The RP work crew chose to use a single gate access point due to its proximity to the RCDT. Subsequently, a RP Technician identified that personnel had not entered the area using the double access gate and had brought in plastic fencing which was inappropriate material for the sump area. The opening of the single sump barrier gate violated ECCS operability basis which requires the sump barrier system to be operable in Modes 1-4. The apparent causes were an inadequate pre-job brief and inadequate procedure for Containment Entry and Egress (OAP-007, 0-RP-RWP-405) due to poor change management. The pre-job brief failed to cover the requirement to use the dual sump barrier gate access point when in Modes 1-4, nor did it address the type of fencing allowed. The brief did not specify that only steel RP fencing could be used for the RCDT. Corrective actions included bolting closed the single gate, removal of the plastic fencing in Mode 5, and briefing RP personnel on the event, lessons learned and management expectations. Procedure OAP-007 will be revised to include the required use of the sump barrier dual access gate in applicable attachments, and RP procedure 0-RP-RWP-405 will be revised to address Mode applicability for use of the sump barrier dual gate and approved RCDT fencing material. The event had no significant effect on public health and safety.
2862013003 | Indian Point 3 | 03/03/2013 | 06/24/2013 | ML13178A22 | <strong>Technical Specification Prohibited Condition due to Turbine Driven Auxiliary Feedwater Pump Failure to Meet Test Acceptance Criteria</strong><br /><i>Abstract:&nbsp;</i>On March 3, 2013, the Turbine Driven (TD) Auxiliary Boiler Feedwater Pump (ABFP) failed to meet the Inservice Test (IST) Program full flow test acceptance criteria during performance of 3-PT-R007B (32 ABFP Full Flow Test). An investigation on March 16, 2013, identified that the ability of the steam admission valve to stroke properly to regulate the amount of steam to the turbine and the ability to change turbine/pump speed was directly affected by the thrust bearing housing being restrained in an extruded position. An assessment of past operability on April 25, 2013, concluded that although the 32 ABFP would not meet IST acceptance criteria, the 32 ABFP would remain functional for analyzed transients and accidents. Sealant was applied on the thrust bearing housing which caused additional frictional forces limiting the movement of the thrust bearing housing thus restraining it in an extruded position. Sealants are to be used on the mating surfaces when the upper and lower governor housing are being joined together but not on the thrust bearing housing. The apparent cause was maintenance practices during reassembly of the TD ABFP during previous maintenance. Corrective actions included troubleshooting the TD AFWP and steam admission valve and repairing deficient conditions. The quarterly and full flow tests will be revised or a PM created to require the steam admission valve to be stroked via the use of the governor valve. A Training Evaluation & Action Request (TEAR) will be performed to determine if additional training is required. Maintenance procedure 0-TUR-403-AFP was revised to emphasize not to apply sealant to the thrust bearing housing.
2862013004 | Indian Point 3 | 03/14/2013 | 05/13/2013 | ML13141A27 | <strong>Technical Specification Prohibited Condition due to a Leak in the Reactor Coolant Pressure Boundary Caused by Defects in a Weld on Seal Table In-core Detector Drive E-11</strong><br /><i>Abstract:&nbsp;</i>On March 14, 2013, during a scheduled refueling outage (RO) boric acid program walk down inspection, boron residue was identified on the fillet weld which attaches the E-11 incore guide tube to the seal table. Since there was no visible leak path indication that the leak had initiated at the high pressure mechanical seal connection located just above the fillet weld, the boron residue was cleaned and a surface examination [i.e., Liquid Penetrant Test (PT)] was performed on the fillet weld. Although this surface examination did not identify any rejectable indications at the leak location, it did identify rounded indications in the weld which could have been the cause of the leakage. No linear indications (i.e., cracks) were identified on the weld or on the guide tube base material above the toe of the weld. Because PT results showed rounded indications in the weld and boron residue was present, the condition was judged to represent a potential through wall defect therefore a Reactor Coolant leak path. The seal table In-core detector guide tube is part of the reactor coolant pressure boundary (RCPB). Technical Specification (TS) 3.4.13 does not allow any RCPB leakage. The apparent cause of the defect was OD initiated stress corrosion cracking of the stainless steel guide tube base material under the fillet weld. It is postulated that the rounded indications on the weld metal allowed contaminants from previous mechanical joint leaks to contact the guide tube base material under the weld resulting in SSC of the tube base material. Corrective actions included VT-2 visual examination of the remaining seal table penetrations to verify that no additional through wall leaks were present and the leaking guide tube was removed from service by cutting the tube below the leaking area and installing a welded plug to form a new RCPB. The event had no significant effect on public health and safety.
2862013005 | Indian Point 3 | 03/27/2013 | 05/23/2013 | ML13157A00 | <strong>Automatic Actuation of Safety Injection and Engineered Safety Features During Reactor Protection System Functional Testing</strong><br /><i>Abstract:&nbsp;</i>On March 27, 2013, while in Mode 3 during startup from a refueling outage, an inadvertent safety injection (SI) occurred during reactor protection logic channel functional testing. The test procedure noted that pressurizer pressure must be above 1930 psig to perform the test but signals may be installed to simulate the condition. In accordance with Appendix A of the test, helipot installation is directed for four pressurizer (PZR) pressure channels to allow PZR pressure signals to be simulated. A helipot was first installed in PT-455 and then simulated pressure raised above 2000 psi. A second helipot was installed for PT-456 and simulated pressure was raised above 2000 psi. SI is automatically enabled with 2 channels above 1900 psig but one of the two out of three pressure signals remained below the 1720 psig signal required for SI actuation. During this time the plant is susceptible to an SI actuation if one of the inputted signals is lost. Before pressure could be simulated in the remaining transmitter PT-457, the test lead connected to PT-456 failed open causing the system to register a 2/3 PZR low pressure satisfying the logic for SI actuation. The root causes were 1) The test procedure did not contain steps to preclude a single point failure, 2) Manufacturing defect of a test equipment lead, 3) Insufficient evaluation of the risk of when the test was being performed. Corrective actions include removing the defective lead from service, inspecting and testing remaining leads. A Procedure 3-PT-M13B will be revised to remove single point vulnerability. Training Evaluation & Action Request will be initiated to create a Case Study for this event which will include information associated with performing in depth risk assessments when surveillance tests are added to or removed during an outage. A TEAR will incorporate the Study into operations training, and a review will be performed on acceptability of testing in Mode 3. The event had no significant effect on public health and safety.
2862013006 | Indian Point 3 | 10/09/2013 | 12/09/2013 | ML13346A01 | <strong>Technical Specification Prohibited Condition due to an Inoperable 33 Station Battery Caused by a Cell Crack</strong><br /><i>Abstract:&nbsp;</i>On October 9, 2013, during performance of weekly surveillance test 3-PT-W013 (Station Battery Visual Inspection) on station battery 33, a crack was discovered in the battery jar of cell 14 which extended below the high level fluid line. The 33 battery is required to be operable per Technical specification 3.8.4 (DC Sources - Operating) in Modes 1-4. The 33 battery was declared inoperable after its ability to perform its design function in a seismic event was questioned due to possible crack propagation. An emergency temporary modification was installed on October 9, 2013, restoring operability. On October 17, 2013, cell 14 on the 33 battery was replaced. The direct cause of the crack in cell 14 was corrosion of the positive battery post seal area which caused the post to expand creating excessive strain on the lid of the battery jar. The most probable cause was chemically induced degradation which weakened the jar wall allowing the stress being transferred from the cover crack to physically separate the jar. An immediate corrective action was to prepare an emergency temporary modification and install the modification to restore the battery operable. Corrective actions included replacing cell 14 of the 33 battery. A failure analysis is being performed by an independent vendor. The event had no significant effect on public health and safety.
2872013001 | Oconee 3 | 10/24/2013 | 06/03/2016 | ML16161A45 | <strong>Unit 3 Manual Reactor Trip due to Main Feedwater Flow Oscillations</strong><br /><i>Abstract:&nbsp;</i>This revision provides supplemental information, including a revised cause, discovered during the cause evaluation for a similar Unit 3 manual reactor trip on January 31, 2015. <br /><br /> On October 24, 2013, Oconee Unit 3 was at 100% power when Operators observed abnormal Main Feedwater flow oscillations. Manual control was unsuccessful in stabilizing the oscillations. The Control Room supervisor directed a manual trip at 0553 hours. Four main steam relief valves (MSRV) did not fully reseat. Post-trip procedures were used to reseat the MSRVs. All other post trip conditions were normal. The 2013 cause evaluation identified a failure of a bushing seal (o-ring) in the actuator for Main Feedwater Control Valve (MFCV) 3FDW-32 as the cause of the flow oscillations. The 2015 cause evaluation revealed the cause of the 3FDW-32 control problem was a latent defect which produced an intermittent fault in the voltage to pneumatic (E/P) converter. While the o-ring failure was a plausible cause in 2013, given new information from the 2015 event, the faulted E/P converter was determined to be the cause of the 2013 event. The E/P converter was tested in 2013, but due to the intermittent nature of the fault the E/P was refuted after satisfactory testing of 3FDW-32 controls. <br /><br /> This event is reportable under 10 CFR 50.73(a)(2)(iv)(A) as a manual actuation of the Reactor Protection System (RPS).
2892013001 | Three Mile Island 1 | 11/07/2013 | 06/20/2014 | ML14175B38 | <strong>Reactor Coolant "B" Cold Leg Drain Line Flaw Supplement</strong><br /><i>Abstract:&nbsp;</i>On November 7, 2013 TMI-1 was in refueling shutdown mode during planned outage T1R20. While conducting planned ISI of the reactor coolant "B" cold leg drain line, a flaw in the pipe weld was discovered. The flaw was located in a 2 inch drain line elbow to pipe weld (designated as weld RC-289). The flaw did not meet acceptance standards and was reported as a non-emergency degraded condition. Extent of condition and ISI scope expansion was performed. The flawed section containing RC-289 was cut out and replaced. A destructive laboratory examination and finite element analysis (FEA) was performed on the removed pipe section. The root cause of the crack is unknown but believed to be the result of geometry induced focusing of lower levels of stress, not capable of inducing cracking alone, but when combined at a geometric feature such as a lack of fusion (LOF) at a natural notch, initiated the crack. The lower energy requirements of propagation then governed the crack growth. Based on the FEA results, instrumentation of the "B" cold leg drain line is recommended to determine the true source of the crack initiating stress. If the crack source can be found with this data and stopped, actions will be created to eliminate the source of cracking. Otherwise proactive replacement may be warranted.<br /><br /> The submittal of this LER constitutes reporting to the NRC in accordance with 10 CFR 50.73 (a)(2)(ii)(A).
2932013001 | Pilgrim | 01/10/2013 | 03/07/2013 | ML13070A07 | <strong>Inadvertent Trip of Both Recirculation Pumps and Subsequent Manual Scram</strong><br /><i>Abstract:&nbsp;</i>On Thursday, January 10, 2013 at 1534 hour [EST], with the reactor at 100% core thermal power, both reactor recirculation pumps unexpectedly tripped and a manual reactor scram was inserted as required by station procedures. Following the reactor scram, all rods were verified to be fully inserted and the Primary Containment Isolation System Group II (Reactor Building) and Group VI (Reactor Water Cleanup System) actuations occurred as designed due to the expected reactor water level shrink associated with the scram signal. All other plant systems responded as designed. The scram was uncomplicated and decay heat was released to the main condenser via the turbine by-pass valves. The cause of the two reactor recirculation pumps tripping was due to the inadvertent seal-in of a relay (pump trip interlock) in the Low Pressure Coolant Injection (LPCI) Loop Select Logic circuitry within the Residual Heat Removal (RHR) System during surveillance testing. When the logic was reset at completion of testing, a normally open relay contact (which was inadvertently closed) interlocked with the recirculation pumps circuit, sent a trip signal to their drive motor breakers. Corrective action has been taken to revise the subject surveillance procedure with steps to reinstall relay covers and added a verifier to observe relay status/ state prior to resetting the relay logic circuit. This event had no impact on the health and/or safety of the public.
2932013002 | Pilgrim | 01/20/2013 | 01/31/2014 | ML14042A16 | <strong>SRV-3B Safety Relief Valve Declared Inoperable Due to Leakage and Setpoint Drift</strong><br /><i>Abstract:&nbsp;</i>On Sunday January 20, 2013, at 2050 hours with the reactor at 100% core thermal power (RMSS in RUN), PNPS declared SRV-3B inoperable and entered Technical Specification (TS) 3.6.D.2 requiring an orderly reactor shutdown such that reactor coolant pressure is less than 104 psig within 24 hours. On Monday January 21, 2013, at 1300 hours (16 hrs and 10 minutes) reactor coolant pressure was lowered to less than 104 psig. SRV-3B had been declared inoperable consistent with PNPS procedures that state an SRV is inoperable if the first stage pilot thermocouple temperature is 35° F below its baseline temperature. This LER Supplement provides the determination of cause for the leakage. The cause of the SRV leakage was that the natural frequency of the pilot assembly was close to a resonant frequency of the valve assembly when installed on the PNPS main steam line, that had failed to be considered in the design of the SRV. A contributing cause was wear and looseness of parts in the main stage of RV-203-3B. <br /><br /> The reactor was depressurized and a new pilot valve assembly was installed on SRV-3B. On January 22, 2013, at 1015 hours reactor restart was commenced. On January 24, 2013 at 0312 hours 100% core thermal power was achieved. <br /><br /> This LER also reports the as-found setpoint of one SRV pilot valve tested was less than the minimum pressure required by TS 3.6.D.1. <br /><br /> This event had no impact on the health and/or safety of the public.
2932013003 | Pilgrim | 02/08/2013 | 04/08/2013 | ML13114A29 | <strong>Loss of Off-Site Power Events due to Winter Storm Nemo</strong><br /><i>Abstract:&nbsp;</i>On Friday February 8, 2013, at 2117 hours with the reactor initially at 85% core thermal power, Pilgrim Nuclear Power Station (PNPS) experienced a loss of off-site power (LOOP) resulting in a load reject and a reactor scram. All rods fully inserted and the Emergency Diesel Generators automatically started and powered safety-related buses A5 and A6. All other safety systems functioned as required. The plant stabilized in Hot Shutdown. At the time of the event a significant winter storm (Nemo) was buffeting Southern New England. At 2200 hours PNPS in conjunction with the local grid operator determined off-site power sources were not reliable and efforts to restore off-site power were temporarily suspended. At 2200 hours, PNPS declared a Notification of Unusual Event. On February 10, at 1055 hours, one of two off-site power supplies was restored, all safety buses were powered from the startup transformer and the Unusual Event was exited. Later on February 10, at 1402 hours with the plant in Cold Shutdown, ice bridging on a startup transformer insulator caused its 345 KV supply breaker to open resulting in a second LOOP. Again the EDG's started and powered safety-related buses. All other safety systems functioned as required. Shutdown cooling was restored at 1426 hours. On February 10, at 2020 hours, this occurrence was reported to the USNRC as documented in EN# 48739.<br><br> The severe winter storm which caused extensive generalized geographical damage to the electrical distribution network was root cause of the LOOP events.<br><br> These events posed no threat to public health and safety.
2932013004 | Pilgrim | 04/14/2013 | 06/18/2013 | ML13171A01 | <strong>Manual Scram Inserted During Reactor Shutdown</strong><br /><i>Abstract:&nbsp;</i>On Sunday, April 14, 2013 at 2217 hours, with the Pilgrim Nuclear Power Station (PNPS) Reactor Mode Select Switch (RMSS) in "Startup/Hot Standby", the turbine generator previously removed from service, and the reactor subcritical on Intermediate Range Monitors Range 2 and lowering, a manual reactor scram was inserted due to reactor pressure decreasing faster than normal. At the time of the manual reactor scram PNPS was conducting a planned reactor shutdown to commence refueling outage (RFO) -19. All control rods fully inserted and Primary Containment Isolation System (PCIS) Group II (Reactor Building) and Group VI (Reactor Water Cleanup System) actuations occurred as designed due to the expected reactor water level shrink associated with the scram signal. All plant systems responded as designed. Off-site power was unaffected and was supplied by the start-up transformer (normal power supply for refuel and reactor shutdown operations).<br><br> The Main Steam Isolation Valves (MSIV) were manually closed to terminate the pressure reduction and the High Pressure Coolant Injection (HPCI) system was manually started in the pressure control mode. The plant cooldown continued with the HPCI system in pressure control and reactor water level maintained within normal bands with the condensate and feedwater system. <br><br> The Root Cause of the event was that procedure PNPS 2.1.5 did not limit operation of MO-S-2, Steam Seal Bypass Valve, to below the steam line pressure design operating limit (250 psig) of the steam seal bypass. The procedure was revised to preclude recurrence.
2932013005 | Pilgrim | 05/23/2013 | 07/22/2013 | ML13211A17 | <strong>Primary Containment Declared Inoperable During HPCI Testing</strong><br /><i>Abstract:&nbsp;</i>At 0455 hours on Thursday, May 23, 2013, with Pilgrim Station in the Startup/Hot Standby Mode and reactor pressure approximately 550 psig, primary containment was declared inoperable due to a leak in the High Pressure Coolant Injection System (HPCI) turbine exhaust line observed while performing the HPCI system flow test. Power ascension was suspended pending investigation and repair. Pilgrim entered into Technical Specification 3.7.A.2 requiring the plant to be in cold shutdown within 24 hours. All other safety systems functioned as required.<br><br> The apparent cause of the leak in the HPCI turbine exhaust line was failure to adequately tighten all of the flange bolting due to unique bolting and flange configuration associated with the new check valve and butterfly valve installation during the refueling outage (RFO)-19. The flange bolting was subsequently retightened applying the target torque values for the application. A Type B Local Leak Rate Test was performed on the butterfly valve outlet flange and the measured leak rate met the Technical Specification and 10 CFR 50, Appendix J requirements, and primary containment was declared operable.<br><br> This event posed no threat to public health and safety.
2932013006 | Pilgrim | 05/23/2013 | 07/22/2013 | ML13211A17 | <strong>HPCI Flow Controller Failure to Achieve Rated Flow While in Auto Mode</strong><br /><i>Abstract:&nbsp;</i>On May 23, 2013, at 1050 hours, during plant start up from Refueling Outage (RFO-19) with the reactor at 2% core thermal power, reactor pressure at - 525 psig, and the mode switch in the Startup / Hot Standby position, Pilgrim Nuclear Power Station (PNPS) declared the High Pressure Coolant Injection (HPCI) system inoperable due to failure of the HPCI flow indicating controller (FIC-2340-1) to maintain system discharge flow rate above 4250 gpm while in the automatic mode from the Main Control Room during planned post maintenance testing. Limiting Condition for Operation (LCO) actions for Technical Specification (TS) 3.5.C.2 were entered.<br><br> The cause of the event was determined to be FIC-2340-1 out of calibration due to degradation of the automatic (null) control/output circuit. Corrective action was taken to troubleshoot, recalibrate and adjust the flow controller. Post work testing verified HPCI flow controller operability.<br><br> This event was not risk significant and had no adverse impact on the health and/ or safety of the public.
2932013007 | Pilgrim | 07/16/2013 | 09/16/2013 | ML13266A24 | <strong>Ultimate Heat Sink and Salt Service Water System Declared Inoperable</strong><br /><i>Abstract:&nbsp;</i>On Tuesday, July 16, 2013 at 1652 [EDT] and again on Wednesday, July 17, 2013 at 1054 [EDT] with the reactor at 100% core thermal power (CTP) the Pilgrim Nuclear Power Station (PNPS) declared the ultimate heat sink (UHS) and the salt service water (SSW) system inoperable due to high sea water inlet temperatures greater than 75°F. A maximum sea water inlet temperature reading of 75.5°F was observed and the maximum duration for either event was 5.5 hours. The limiting condition for operation (LCO) action for technical specification (TS) 3.5.B.4 was entered then exited based on the rise and fall of sea water inlet temperature. Plant systems and components operated as required and no equipment failures occurred. The plant was not shutdown due to the short duration of the sea water temperature excursion.<br /><br /> The cause of the high sea water inlet temperature readings was sustained increased sea water surface temperature in Cape Cod Bay due to hot summer weather conditions and the contribution from recirculation of water from the plant's outfall due to wind and tidal conditions. Corrective action was completed to establish an operational decision making issue (ODMI) action plan to reduce station power levels prior to reaching the TS UHS LCO temperature limit.<br /><br /> This event posed no threat to public health and safety.
2932013008 | Pilgrim | 08/22/2013 | 10/21/2013 | ML13302B56 | <strong>Manual Scram - Reactor Feed Pump Trip</strong><br /><i>Abstract:&nbsp;</i>On Thursday, August 22, 2013 at 0755 [EDT] with the reactor critical at 98% core thermal power (CTP), and the mode switch in RUN, the Pilgrim Nuclear Power Station (PNPS) was manually scrammed due to lowering reactor water level resulting from a trip of the reactor feed pumps. The reactor feed pumps tripped due to a loss of power to the pump seal cooling water flow switch relays and resultant automatic actuation of the feed pump trip circuit.<br /><br /> The direct cause of the reactor feed pump trip was an automatic actuation of the feed pump trip circuitry. The feed pump trip circuits actuated as designed in response to a loss of power to the pump seal cooling water flow switch relays. The seal cooling water flow switch relays lost power as a result of a 120V AC breaker trip resulting from a short-to-ground fault in the associated circuits fed by the breaker. Corrective action was taken to repair the ground fault in the associated circuits fed by the 120V AC breaker and to revise reactor feed pump trip circuit design to remove the loss of seal water trip function.
2932013009 | Pilgrim | 10/14/2013 | 12/13/2013 | ML13364A09 | <strong>Loss of Offsite Power and Reactor Scram</strong><br /><i>Abstract:&nbsp;</i>On Monday October 14, 2013 at 2121 hours [EDT], with the reactor critical at 100% core thermal power, the mode switch in RUN, and offsite power 345KV Line 342 out of service for a scheduled upgrade, a loss of offsite power (LOOP) occurred due to the loss of the second 345KV Line 355. All control rods fully inserted, main steam isolation valves closed on the loss of power to the reactor protection system, and the emergency diesel generators automatically started supplying power to both 4160V safety buses. Following the scram, reactor water level lowered to +12 inches initiating the Primary Containment Isolation System (Group II, Reactor Building Isolation System (RBIS); and Group VI - Reactor Water Cleanup System) automatically per design. A plant cool down commenced with reactor water level being maintained in the normal post-scram band of +12 inches to +45 inches utilizing the High Pressure Coolant Injection (HPCI) and Reactor Core Isolation Cooling (RCIC) systems.<br /><br /> The cause of Line 355 loss was due to a failure of an offsite substation tower support. The offsite tower was repaired and Line 355 was energized at 2023 hours on October 15, 2013.<br /><br /> These events posed no threat to public health and safety.
2932013010 | Pilgrim | 10/19/2013 | 12/18/2013 | ML13361A08 | <strong>Automatic Group I Primary Containment Isolation Actuation During Plant Startup due to Reactor High Water Level</strong><br /><i>Abstract:&nbsp;</i>On Saturday, October 19, 2013 at 0330 [EDT] with the reactor critical at 1% core thermal power (CTP), and the mode switch in START UP, a high reactor water level condition (+55") resulted in a valid Group I primary containment isolation signal and resultant closure of the main steam isolation valves (MSIV), MSIV drain line valves, and reactor recirculation system sample line valves. The plant was in the process of starting up with reactor pressure at approximately 290 psig with a corresponding reactor coolant temperature for that pressure. Reactor startup was suspended and control rods were manually reinserted. Reactor water level was recovered and maintained within normal bands. Plant systems responded as designed to the Group I containment isolation signal.<br /><br /> The direct cause of MSIV isolation was automatic actuation of the Group I containment isolation signal due to high reactor high water level with the mode switch in START UP. The cause of the high reactor water level was due to unexpected rapid opening of three turbine steam bypass valves. The reason the bypass valves rapidly opened was due to a malfunction of the mechanical pressure regulator (MPR). The MPR malfunctioned because an increased error signal between turbine steam pressure and the MPR setpoint due to friction between the MPR pilot valve and the pilot valve bushing resulting from lack of rotation of the pilot valve bushing. Corrective action was taken to flush the needle valve that controls oil flow to the pilot valve bushing and exercise of the pilot valve bushing to restore proper rotation.<br /><br /> This event posed no threat to public health and safety.
2962013001 | Browns Ferry 3 | 01/09/2013 | 05/10/2013 | ML13134A01 | <strong>Inoperable Emergency Diesel Generator due to Failed Electric Generator Casing Fan Bearing</strong><br /><i>Abstract:&nbsp;</i>On January 9, 2013, at 0400 Central Standard Time, an Auxiliary Unit Operator (AU()) performing rounds near the 3D Emergency Diesel Generator (EDG) discovered metal residue around the blower shaft. Inspection by Maintenance determined the blower bearing had failed. Operations declared the 3D EDG inoperable.<br><br> The root causes of this condition are the shielded bearings in the EDG blowers were not adequately assessed on a component level to identify potential failure modes and impacts to EDG operability, and standard vibration data was ineffective in identifying the degradation of the lubrication in the shielded bearings of the BFN, Unit 3, EDG blowers due to the masking effect of generator vibrations.<br><br> Immediate corrective actions included the inspection and replacement of all diesel blower bearings that had not been replaced since 2012. The corrective actions to prevent recurrence are to determine appropriate Preventive Maintenance strategies for the population of sealed or shielded bearings associated with EDGS and safety or quality related rotating equipment, and to add an additional vibration monitoring point to the EDG blower fan bearings and relocate two existing monitoring points to the drive end bearing housing.
2962013002 | Browns Ferry 3 | 02/11/2013 | 06/07/2013 | ML13162A40 | <strong>Manual Actuation of Reactor Core Isolation Cooling System During Reactor Shutdown</strong><br /><i>Abstract:&nbsp;</i>On February 11, 2013, the Reactor Core Isolation Cooling (RCIC) system was manually started during a planned Browns Ferry Nuclear Plant (BFN), Unit 3, reactor shutdown. A Reactor Feedwater recirculation piping through wall leak resulted in the loss of condenser vacuum and subsequent unavailability of the Main Turbine Bypass Valves. The RCIC system was manually started to control reactor water level in anticipation of loss of Reactor Feedwater Pumps tripping on low vacuum. Safety Relief Valves were manually operated to maintain reactor pressure. No Emergency Core Cooling System or RCIC system reactor water level initiation set points were reached.<br><br> The root causes of this condition are the design used for valves 3-FCV-03-0071, -0072, and -0073 in the Feedwater Long Cycle Return Line is incorrect for the specified application, and BFN personnel did not consistently consider risk when making decisions to replace the BFN, Unit 3, Feedwater Long Cycle valves.<br><br> Corrective actions to prevent recurrence are to replace valves 1, 2, 3-FCV-03-0071, -0072, and -0073 with valves appropriately designed for the required operating conditions and to establish initial and continuing training for leaders and craft that support their roles and responsibilities. Also, BFN has implemented a Strategic Performance Management process to reinforce and institutionalize conservative decision making principles.
2962013003 | Browns Ferry 3 | 02/25/2013 | 12/18/2013 | ML13354B85 | <strong>Automatic Reactor Shutdown due to an Actuation of the Reactor Protection System from a Turbine Trip</strong><br /><i>Abstract:&nbsp;</i>On February 25, 2013, at approximately 1313 hours Central Standard Time, the Browns Ferry Nuclear Plant (BFN), Unit 3, reactor automatically scrammed due to an actuation of the Reactor Protection System from a turbine trip. The turbine tripped on low condenser vacuum due to a reactor feedwater piping separation. The Main Steam Isolation Valves were manually closed. There was one Safety Relief Valve that was manually operated to maintain reactor pressure due to the unavailability of the Main Turbine Bypass Valves upon loss of condenser vacuum. All systems responded as expected to the turbine trip. No Emergency Core Cooling System or Reactor Core Isolation Cooling (RCIC) system reactor water level initiation set points were reached. Reactor water level was controlled with the RCIC system and reactor pressure was controlled with the High Pressure Coolant Injection system.<br /><br /> The root cause for this event is that the system design for BFN, Unit 3, Feedwater Long Cycle line does not account for flashing of water to steam due to isolation valve leakage.<br /><br /> The corrective action to prevent recurrence is to redesign Feed Water Long Cycle lines downstream of each Feed Water Long Cycle isolation valve and upstream of the Miscellaneous Drain Header with a valve and piping configuration appropriately designed for the specified application.
2982013001 | Cooper Station | 10/30/2013 | 12/20/2013 | ML13361A08 | <strong>Unfused Direct Current Ammeter Circuits Result in Unanalyzed Condition</strong><br /><i>Abstract:&nbsp;</i>During a review of Operating Experience for unfused remote Direct Current (DC) Ammeter Circuits that could result in a secondary fire due to multiple fire induced faults, Cooper Nuclear Station determined susceptibility to the same condition. In a postulated event, a fire in the area of the shunt conductor's route could cause one of the ammeter wires to short to the ground plane. Simultaneously, the event could cause another DC wire from the opposite polarity on the same battery to short to the ground plane. This would cause a ground loop through the unprotected ammeter wire. Since this circuit is not protected, this event could result in excessive current flow in the ammeter wiring causing a secondary fire in a separate fire area.<br /><br /> The cause of the unfused ammeter circuits is that the original design criteria had not factored in the potential of the multiple shorts to ground failure mode and therefore, did not require overcurrent protection for remote shunt fed ammeter circuits.<br /><br /> Compensatory fire watch measures have been implemented until an analysis is performed demonstrating that remote circuits can meet fire protection requirements without fuses. If an analysis cannot demonstrate meeting fire protection requirements with the existing circuit design, then a modification to correct the remote ammeter circuits will be implemented.
3022013001 | Crystal River 3 | 06/01/2013 | 07/25/2013 | ML13221A57 | <strong>Valid Actuation of an Emergency Diesel Generator Due to a Spurious Fault on a Breaker Non-Segregated Bus Duct</strong><br /><i>Abstract:&nbsp;</i>At 21:29, on June 1, 2013, Crystal River Unit 3 (CR-3) was in NO MODE (core permanently off loaded for decommissioning) at 0 percent RATED THERMAL POWER when a spurious fault above Breaker 3104 (Startup Transformer (SUT) feed to the "B" Unit 6.9 kilovolt (kV) nonsegregated bus) occurred. Protective relaying de-energized the SUT and the Backup Engineered Safeguards Transformer, which de-energized the "B" Engineered Safeguards (ES) 4160 volt (V) bus. All relays operated as designed. The "B" Emergency Diesel Generator automatically started and re-energized the "B" ES 4160V bus, as designed. The only credible accidents for CR-3 are a Fuel Handling Accident and a Waste Gas Decay Tank (WGDT) Rupture Accident. At the time of the spurious fault, the Spent Fuel Pools (SFPs) were being cooled by the "A' SFP pump. The SFPs and WGDTs were unaffected. This condition does not represent a reduction in the public health and safety. Valid actuation of an Emergency Diesel Generator is reportable under 10 CFR 50.73(a)(2)(iv)(A). The cause for the fault was lack of a bus duct internal seal inspection Preventive Maintenance (PM) task which led to undetected condensate accumulation and formation of a conductive bridge to ground causing the bus fault. An internal seal inspection criterion is being developed. Similar occurrences have not been previously reported to the NRC.
3132013001 | Arkansas 1, Arkansas 2 | 03/31/2013 | 08/22/2013 | ML13234A24 | <strong>Collapse of a Main Generator Stator Temporary Lift Assembly Results in a Fatality, Multiple Injuries, a Plant Scram, a Notification of Unusual Event, and Dual Unit Structural Damage</strong><br /><i>Abstract:&nbsp;</i>On March 31, 2013, at approximately 0750 CDT, during lifting and removal of the Arkansas Nuclear One Unit 1 (ANO-1) original Main Generator Stator (Stator), the temporary lift assembly collapsed due to failure of one of the structural columns, resulting in the Stator falling onto the turbine deck (386' elevation) and rolling down into the ANO-1 train bay (354' elevation) adjacent to Arkansas Nuclear One Unit 2 (ANO-2). The event resulted in one fatality, multiple injuries, structural damage to the ANO-1 and ANO-2 turbine buildings, and damage to non-vital systems and electrical equipment. At the time of the event, ANO-1 was in MODE 6 and ANO-2 was in MODE 1 at approximately 100 percent power. The event resulted in a loss of offsite power for ANO-1, with both Emergency Diesel Generators (EDGs) starting to supply safety loads. ANO-1 decay heat removal was lost for approximately four minutes. ANO-2 automatically tripped off-line after the vibration from the dropped Stator resulted in the actuation of relays in the ANO-2 switchgear located adjacent to the train bay, subsequently tripping a reactor coolant pump motor breaker. After the reactor trip, emergency feedwater was manually initiated by ANO-2 Control Room Operators. As debris fell into the train bay, an 8-inch firewater pipe was ruptured and the Alternate AC Diesel Generator electrical tie to ANO-1 was severed. At 0923 CDT that same day, water intrusion from the ruptured firewater piping into a 4160 volt breaker resulted in an ANO-2 Startup Transformer lockout, de-energizing a safety bus. An EDG automatically started as designed and supplied the affected safety bus. An ANO-2 Notification of Unusual Event was declared at 1033 CDT due to fire or explosion from an electrical fault in the 4160 volt switchgear with indications of bus damage. After damage assessment and repairs, ANO-2 returned to power operation on April 28, 2013. ANO-1 returned to power operation on August 7, 2013.
3152013001 | Cook 1 | 03/31/2013 | 05/28/2013 | ML13151A02 | <strong>Unit 1 Reactor Coolant System Weld Defect and Pressure Boundary Leakage</strong><br /><i>Abstract:&nbsp;</i>On March 30, 2013, at 0124 EDST, Donald C. Cook Nuclear Plant (CNP) Unit 1 reactor was in Mode 5, Cold Shutdown, after shutdown for a refueling outage. During planned maintenance activities, a small amount of dry boric acid was identified on the weld face of a 3/4 inch socket welded elbow-pipe connection upstream of a flow instrument isolation valve of the Reactor Coolant System (RCS). The weld is located in a non-isolable section of the RCS piping. Liquid dye penetrant testing was performed on March 31, 2013, at 0414 EDST and identified a 10mm long linear indication on the face of the weld. The indication is considered a through wall leak of the RCS that was active during the past operating cycle during modes of applicability. Technical Specification Limiting Condition for Operation (LCO) 3.4.13 limits the RCS to no pressure boundary leakage and is applicable in Modes 1, 2, 3, and 4.<br><br> Based on engineering judgment, the apparent cause is vibration fatigue of a cantilever tap connection which resulted in a through wall weld defect. Repairs completed include modification of the piping, revised fillet welds, and replacement of the elbow. Material failure analysis and a full causal evaluation of the socket weld and associated piping is pending at the time of this report. The weld defect was reported in accordance with 10 CFR 50.72(b)(3)(ii)(A).<br><br> The weld defect and the subsequent through wall leak of the RCS pressure boundary are reportable as a Licensee Event Report (LER) in accordance with 10 CFR 50.73(a)(2)(ii)(A) and 10 CFR 50.73(a)(2)(i)(B).
3152013002 | Cook 1 | 04/24/2013 | 06/24/2013 | ML13177A03 | <strong>System Actuation of the Unit 1 CD Emergency Diesel Generator</strong><br /><i>Abstract:&nbsp;</i>On April 24, 2013, the Donald C. Cook Nuclear Plant (CNP) Unit 1 reactor was in a refueling outage and defueled.<br><br> At 1411, a ground fault occurred on a power cable routed between 1-TR101CD, 4kV Buses 1C and 1D Reserve Feed Auxiliary Transformer (RAT) and 4kV circuit breaker 1-1C4, Reserve Incoming Feed from RAT 1-TR101CD. Fault protection circuitry caused breaker 12-12CD, Reserve Feed Auxiliary Transformers TR101CD and TR201CD Supply Breaker to open which de-energized both the Unit 1 and Unit 2 Reserve Feed Transformers, respectively. The unexpected loss of Train A Reserve Feed on Unit 1 caused a valid actuation of the Unit 1 CD Emergency Diesel Generator (EDG), which automatically started and loaded, as designed. Unit 2 remained stable at 100% power after the loss of Train A Reserve Feed power to the 2-TR201CD RAT.<br><br> The apparent cause of the power cable failure was a reduction of the insulation dielectric strength of the 4kV cabling running from the 1-TR101CD transformer to the plant buses. The insulation properties were affected from cable age combined with a stressor of a prolonged pressure point from the cable lay path in the cable tray.<br><br> The valid actuation and start of the U1 CD EDG was reported in accordance with 10 CFR 50.72(b)(3)(iv)(A), as an eight hour report. The valid actuation is reportable as a Licensee Event Report (LER) in accordance with 10CFR 50.73(a)(2)(iv)(A), System Actuation of an Emergency Diesel Generator.
3162013001 | Cook 2 | 07/28/2013 | 09/24/2013 | ML13269A36 | <strong>Unit 2 Manual Reactor Trip due to Lowering Steam Generator Level</strong><br /><i>Abstract:&nbsp;</i>On July 28, 2013, the Donald C. Cook Nuclear Plant Unit 2 reactor was operating at 100 percent power. At 1018, reactor operators manually tripped the reactor when reaching a low steam generator level threshold during a secondary plant transient event.<br /><br /> The secondary plant transient occurred when a steam supply valve closed to the Right Moisture Separator Reheater which resulted in feedwater heater level oscillations followed by Heater Drain Pumps tripping on heater low levels. This caused feedwater pump suction pressure to lower and automatically tripped the West Main Feedwater Pump. As a result, steam generator level lowered to 23 percent on the #4 Steam Generator. The reactor operators manually tripped the reactor based on a manual trip threshold for Steam Generator levels that was established by the Unit Supervisor.<br /><br /> The initiating cause of the steam supply valve closure and subsequent secondary plant transient was a loss of control air to the air operated valve resulting from fretting of the control air line.<br /><br /> The Reactor Protection System and the specified Auxiliary Feedwater System actuation was reported in accordance with 10 CFR 50.72(b)(2)(iv)(B) and 10 CFR 50.72(b)(3)(iv)(A). The valid actuation is reportable as a Licensee Event Report (LER) in accordance with 10 CFR 50.73(a)(2)(iv)(A).
3172013002 | Calvert Cliffs 1, Calvert Cliffs 2 | 10/18/2013 | 12/17/2013 | ML13353A17 | <strong>Unfused Ammeter Circuits Result in Appendix R Unanalyzed Condition</strong><br /><i>Abstract:&nbsp;</i>On October 18, 2013, a review of industry operating experience determined an unanalyzed condition existed with respect to 10 CFR Part 50 Appendix R analysis requirements. The unanalyzed condition involved a postulated fire in Unit 1 Cable Spreading Room (CSR) that could cause an unfused direct current (DC) ammeter circuit to become grounded. If the fire also caused another DC wire of the opposite polarity on the same component to become grounded, a ground loop through the unfused DC ammeter wiring could exist. This ground loop could draw excessive current and could overheat. Because the affected DC ammeter circuits run through both unit CSRs on the way to the Control Room, a secondary fire could occur in Unit 2 CSR. Fire in both CSRs is not an analyzed condition under the 10 CFR Part 50 Appendix R program. Review determined that only three unfused DC ammeter circuits were susceptible to this condition. The apparent cause was determined to be that the original design of the DC ammeter circuits did not adequately address fire protection program requirements. On November 11, 2013 technicians lifted the leads to the affected ammeter circuits which eliminated this unanalyzed condition. A modification to install fuses on the affected DC ammeter circuits is planned.
3182013001 | Calvert Cliffs 2 | 02/17/2013 | 04/18/2013 | ML13109A49 | <strong>Reactor Coolant System Pressure Boundary Leakage in Valve Leakoff Line Weld</strong><br /><i>Abstract:&nbsp;</i>On February 17, 2013, while Unit 2 was in Mode 3 during a refueling outage, a pinhole leak was identified at the upper packing leakoff line cap seal weld of pressurizer spray valve 2CV-100F, which constituted a Reactor Coolant System pressure boundary leak. The Technical Specifications limit Reactor Coolant System pressure boundary leakage to zero. Based on visual inspection performed during the boric acid walkdown the leak most likely existed during plant operation. The most likely cause of the pinhole was a latent weld defect created during the installation of the cap seal weld. A similar event is documented in Licensee Event Report 318/2010-002. The most likely cause for that event was a latent weld defect created during manufacture. The valve bonnet assembly, which includes the packing leakoff line, was replaced and inspected satisfactorily prior to startup from the Unit 2 refueling outage.
3182013002 | Calvert Cliffs 2 | 03/12/2013 | 05/02/2013 | ML13126A07 | <strong>Pressurizer Safety Valve Setpoint High due to Insufficient Margin</strong><br /><i>Abstract:&nbsp;</i>On March 12, 2013, during scheduled testing at an offsite testing facility, the as-found lift setting for pressurizer safety valve, serial number BN04375, was measured higher than the Technical Specification allowable value. The valve had been installed in Unit 2 at the 2RV200 location (Unit 2 pressurizer safety valve) and was removed during the 2013 Unit 2 refueling outage for scheduled testing and maintenance. No material conditions were found that contributed to the high setpoint discovered during the test. The apparent cause is insufficient margin to address time-related drift. Corrective actions are to increase the Technical Specification setpoint tolerance and revise the procurement engineering standard as-left margin. A similar event is documented in Licensee Event Report 318/2011-002. The cause for that event was setpoint variation.
3182013003 | Calvert Cliffs 2 | 05/08/2013 | 07/03/2013 | ML13191A17 | <strong>Reactor Trip Due to Intermittent Failure in the Turbine Control System</strong><br /><i>Abstract:&nbsp;</i>On May 8, 2013, at 2147 eastern daylight time, Unit 2 experienced an automatic reactor trip from 99.5 percent power. The Reactor Protective System actuated on high pressurizer pressure. The high pressurizer pressure condition occurred due to a loss of load event caused when main turbine steam admission valves closed. The most probable cause of the event was an intermittent failure of a component or signal path in main turbine control cabinet 2T11 that resulted in a control signal to the steam admission valves to close. At Calvert Cliffs, there have been no recent similar events involving a reactor trip caused by the failure of the turbine control system. This event is being reported pursuant to 10 CFR 50.73(a)(2)(iv)(A) due to Reactor Protective System actuation. Corrective actions include replacement of circuit cards in the main turbine overspeed protection circuitry, monitoring selected control system signals which could indicate the source of the signal should the event recur, and implementation of a project plan for selected turbine control circuit card replacement during a future refueling outage.
3182013004 | Calvert Cliffs 2 | 05/21/2013 | 07/17/2013 | ML13199A43 | <strong>Manual Reactor Trip Due to 22 Steam Generator Feed PUMD Trip</strong><br /><i>Abstract:&nbsp;</i>On May 21, 2013 at 0533, Calvert Cliffs Nuclear Power Plant Unit 2 initiated a manual reactor trip from 99.5 percent power in response to a trip of 22 Steam Generator Feed Pump (SGFP). All post-trip actions were completed and the event terminated without complications. The cause of the initiating event was the failure of the 22 SGFP coupling that connects the pump to its steam turbine driver, such that the pump and steam turbine were effectively disconnected. Inspection of the pump end of the coupling assembly revealed mechanical damage and separation along a weld seam. Forensic analysis identified areas of incomplete weld fusion on the turbine end of the failed coupling dating to the original component manufacture, combined with stresses induced by high cycle stress as being the root cause of 22 SGFP coupling failure. Immediate corrective actions taken included the examination, inspection, and replacement of the 22 SGFP coupling.
3182013005 | Calvert Cliffs 2 | 09/05/2013 | 10/25/2013 | ML13302C06 | <strong>Manufacturing Defect Results in Shutdown due to Dropped Control Element Assembly</strong><br /><i>Abstract:&nbsp;</i>On September 5, 2013, Unit 2's Control Element Assembly (CEA) #27 dropped to the fully inserted position while the CEA was being operated as part of a surveillance test. Operators entered applicable Technical Specifications for the dropped CEA. When operators were unable to restore the CEA to its proper alignment within the required Completion Time, operators commenced a reactor shutdown in accordance with Technical Specification Required Action 3.1.4.F.1. The unit was shutdown at 1735 on September 5, 2013. Troubleshooting identified Control Element Drive Mechanism (CEDM) #27 lift coil lead wire was grounded internally to the coil housing due to a chafed wire. The root cause for the dropped CEA was determined to be a manufacturing defect that resulted in circumferential displacement of the coil within the coil housing and the misalignment of the lift coil lead wire within the coil housing nipple. Corrective actions included replacement of the CEDM coil stack with one that includes a change in design featuring a protective heat shrink wrap at the point where the lead wire penetrates the coil housing nipple. All other Unit 2 CEDMs were meggered with satisfactory results. A detailed plan to replace the remaining Unit 2 CEDM coil stacks is being developed. Replacement of the Unit 2 coil stacks is expected to begin during the 2015 refueling outage.
3212013001 | Hatch 1 | 02/10/2013 | 05/29/2013 | ML13149A29 | <strong>Unplanned RPS Actuation in Response to Reactor Coolant Chemistry Event Caused by a Condenser Tube Leak</strong><br /><i>Abstract:&nbsp;</i>On February 10, 2013 at 0536 Eastern Standard Time (EST), while operating at 99.8 percent rated thermal power (RTP), a system operator reported that the "System Inlet High Conductivity" alarm had been received at the local Condensate Polishing System panel. This annunciator is set to alarm when conductivity reaches 0.239 micro mhos per cm. Control room instruments immediately began to indicate that conductivity levels were slowly increasing for the condenser and the reactor vessel coolant. The crew entered the abnormal operating procedure for Condenser Tube Leaks/Chemical Intrusion and began decreasing power to 88 percent at 0555 EST. The crew continued to reduce power to 47 percent RTP. Inlet conductivity reached 5 micro mhos per cm and the shift supervisor directed the crew to enter the abnormal operating procedure for a manual SCRAM at 0700 EST. The unplanned manual RPS actuation was initiated as a protective action for the reactor vessel, as the increasing water chemistry conductivity indicated a possibly serious condition in which circulating water tube(s) were damaged within the condenser and were leaking into the hot well. After shutdown, significant damage to condenser internals was discovered, including fractures in the false bottom and divider wall. A section of a tube bundle was damaged by impact from fractured steel sections. The direct cause of this damage was operating the condenser with high hotwell water levels while thermodynamically driven pressure surges were taking place under the false bottom. Repairs were made and better methods of monitoring and controlling hotwell levels were instituted. Measures were put in place to better control theromdynamic inputs into the hotwell.
3232013001 | Diablo Canyon 2 | 02/28/2013 | 04/29/2013 | ML13120A26 | <strong>Valid EDG 2-1 Start Signal Caused by a Loss of 4kV Class 1E Bus G</strong><br /><i>Abstract:&nbsp;</i>On February 28, 2013, at 21:54 PST, with Diablo Canyon Power Plant (DCPP) Unit 1 in Mode 1 at 100 percent power and Unit 2 shut down and defueled for the Unit 2 Refueling Outage Cycle 17, 4 kilovolt vital Bus G on Unit 2 deenergized, which generated a valid actuation signal to start emergency diesel generator (EDG) 2-1. The EDG did not start, as it was in manual control in preparation for planned maintenance. The planned activity did not anticipate an actual loss of power to Bus G. Therefore, the EDG start signal was valid, and was not part of a pre-planned sequence during testing. DCPP determined this condition was reportable in accordance with 10 CFR 50.73(a)(2)(iv)(A).<br><br> This condition was caused when technicians did not ensure all maintenance prerequisites were met prior to beginning work. DCPP determined the root cause was a lack of a formal process for evaluating the risk of outage emergent work. Additionally, maintenance leadership has not been proactive in their approach to prevent shortfalls in human performance standards and use. DCPP will revise select site procedures to include risk management when shutdown. DCPP will also perform corrective actions to address human performance shortfalls to internalize the use of error prevention tools. This condition did not adversely affect the health and safety of the public.
3232013002 | Diablo Canyon 2 | 03/12/2013 | 08/22/2013 | ML13235A10 | <strong>Two Source Range Nuclear Instruments Inoperable While in Mode 6</strong><br /><i>Abstract:&nbsp;</i>On March 12, 2013, at 17:06 PDT, with Diablo Canyon Power Plant (DCPP) Unit 2 shut down for the Unit 2 Refueling Outage Cycle 17, Unit 2 source range (SR) instrument N-32 experienced an unexpected increase in indicated counts per second (cps). Other available SR indications showed no rise in cps. At the time, SR instrument N-31 was inoperable. Since operators considered N-32 inoperable while N-31 was already inoperable, the audible count rate in the control room was no longer reliable. DCPP determined this condition constituted a loss of a safety function required to maintain the reactor in a safe shutdown condition and was reportable in accordance with 10 CFR 50.73(a)(2)(v)(A). <br /><br /> Following a vendor failure analysis, DCPP determined that a discontinuity in the cable insulation shield caused the N-32 high count rate readings. DCPP replaced the faulted cable. This condition did not adversely affect the health and safety of the public.
3232013003 | Diablo Canyon 2 | 03/18/2013 | 05/16/2013 | ML13136A04 | <strong>Technical Specification 3.6.3 and 3.0.4.a Not Met due to Human Error</strong><br /><i>Abstract:&nbsp;</i>On March 18, 2013, at 09:30 PDT, following a transition from Mode 5 to Mode 4, an operator discovered that Unit 2 service air containment isolation valve (CIV) AIR-S-2-200 was open. Technical Specification (TS) 3.6.3 requires that each manual CIV be verified closed prior to entry into Mode 4, unless open under administrative controls. TS 3.0.4.a specifies that entry into a Mode shall only be made when associated TS-required actions permit continued operation in that Mode for an unlimited period of time. TS 3.6.3, Required Action A.2, requires Diablo Canyon Power Plant (DCPP) to verify containment Penetration 56 flow path is isolated prior to entering Mode 4 from Mode 5 for isolation devices inside containment. DCPP failed to verify the flow path was isolated prior to the Mode transition, and concluded that the transition from Mode 5 to Mode 4 with AIR S-2-200 open was a condition prohibited by TS 3.0.4.a and TS 3.6.3, and was reportable in accordance with 10 CFR 50.73(a)(2)(i)(B).<br><br> DCPP determined that a failure to properly use human performance error prevention tools and an inadequate supervisor review process for sealed component checklist completion caused the event. DCPP will revise the checklist to require independent supervisor verification that it is complete. This condition did not adversely affect the health and safety of the public.
3232013004 | Diablo Canyon 2 | 06/08/2013 | 03/30/2015 | ML15089A59 | <strong>Technical Specification 3.8.1 Not Met due to Failed Wire Lug on Emergency Diesel Generator 2-3</strong><br /><i>Abstract:&nbsp;</i>On June 8, 2013, at 08:40 PDT, with Diablo Canyon Power Plant (DCPP) Unit 2 in Mode 1 at 100 percent power, Emergency Diesel Generator (EDG) 2-3 failed to complete a scheduled surveillance run. Cyclic fatigue failure of a wire lug in the EDG 2-3 current differential protection circuit caused an automatic EDG shut down 21 hours and 42 minutes into the 24-hour load run. DCPP determined the last time EDG 2-3 would have been able to complete its 24-hour surveillance run was greater than the technical specification allowed outage time. Additionally, during the time that EDG 2-3 was unable to complete its load run, EDGs 2-1 and 2-2 also had been declared inoperable on several occasions.<br /><br /> DCPP determined that a vibrating terminal block cover induced cyclical fatigue in the wire lug, causing it to fail. DCPP replaced the broken wire lug and permanently removed the cover. Additionally, DCPP will revise a procedure to periodically inspect for wear on the wires and lugs.<br /><br /> This condition did not adversely affect the health and safety of the public.
3232013005 | Diablo Canyon 2 | 07/10/2013 | 11/21/2013 | ML13326A93 | <strong>Unit 2 Reactor Trip due to Lightning Arrester Flashover</strong><br /><i>Abstract:&nbsp;</i>On July 10, 2013, at 09:50 PDT, while performing the periodic hot-washing of the 500 kV insulators, a flashover of the Phase A 500 kV to ground across the Phase A lightning arrestor occurred and actuated the 500 kV differential relay. The actuation of the 500 kV differential relay opened the Unit 2 generator output breakers to isolate the generator, which then actuated a turbine trip. Since Unit 2 was operating above the 50 percent power permissive, the reactor protection system initiated a Unit 2 reactor trip. All plant equipment responded as designed.<br /><br /> Diablo Canyon Power Plant (DCPP) staff determined the root cause of this event to be the hot-washing of the Phase A transmission line string insulators (500 kV dead-end insulators) with inadequate controls for oversight of supplemental PG&E transmission line personnel and on-line maintenance risk analysis that resulted in a conductive overspray, which induced an external arc around the lightning arrester insulation resulting in flashover. The corrective action to prevent reoccurrence involves the development and implementation of a maintenance strategy for 500 kV dead-end insulators to ensure they remain adequately contamination free, structurally sound, and minimize risk to DCPP.<br /><br /> There were no personnel injuries, no offsite radiological releases, and no damage to safety-related equipment associated with this condition. This condition did not have an adverse effect on the health and safety of the public.
3242013001 | Brunswick 2 | 03/07/2013 | 05/06/2013 | ML13141A28 | <strong>Implementation of Enforcement Guidance Memorandum (EGM) 11-003, Revision 1</strong><br /><i>Abstract:&nbsp;</i>On March 7, 2013, Unit 2 implemented the guidance of EGM 11-003, Revision 1, "Enforcement Guidance Memorandum on Dispositioning Boiling Water Reactor Licensee Noncompliance with Technical Specification Containment Requirements During Operations With a Potential for Draining the Reactor Vessel," dated December 20, 2012. Consistent with EGM 11-003, Revision 1, secondary containment operability was not maintained during Operations With a Potential for Draining the Reactor Vessel (OPDRV) activities, and Required Action C.1 of Technical Specification (TS) 3.6.4.1, "Secondary Containment," was not completed. EGM 11-003, Revision 1, was implemented four additional times during the 2013, Unit 2 refueling outage. These conditions are being reported in accordance with 10 CFR 50.73(a)(2)(i)(B) as operations prohibited by the plant's TSs.<br><br> Implementation of EGM 11-003, Revision 1, during the Unit 2 refueling outage was a planned activity. As such, there was no root cause evaluation of the event. Consistent with the guidance provided in EGM 11-003, Revision 1, BSEP will submit a license amendment request to adopt a Technical Specifications Task Force (TSTF) traveler associated with generic resolution of this issue within four months after the issuance of the Notice of Availability of the TSTF traveler.
3242013002 | Brunswick 2 | 03/29/2013 | 05/28/2013 | ML13156A37 | <strong>Vibration-Induced Failure of Residual Heat Removal System Heat Exchanger Bypass Valve</strong><br /><i>Abstract:&nbsp;</i>On March 29, 2013, Unit 2 was in a refueling outage with all fuel removed from the reactor vessel when it was discovered that a stud holding the valve yoke to the bonnet on the "A" residual heat removal (RHR) system heat exchanger bypass valve had failed. A second stud failed during removal. In this condition, the valve may not have been capable of closing for the purpose of throttling flow past the heat exchanger for the suppression pool cooling mode and shutdown cooling mode of RHR operation.<br><br> The studs failed due to low stress, high cycle fatigue resulting from vibration that occurs when the valve is throttled while operating in the shutdown cooling mode of RHR. The root causes of this event were failure to fully understand the source of vibration in the RHR system and a failure to prevent vibration related failure mechanisms with an adequate system design.<br><br> Completed corrective actions for this event included replacing all four studs on the valve with capscrews. The system or valve design will be changed to reduce vibration. As an interim action, periodic maintenance will be performed on the valve to ensure reliability until the design change is completed.
3242013003 | Brunswick 2 | 05/21/2013 | 07/22/2013 | ML13212A17 | <strong>Machining Surface Leads to Setpoint Drift in Main Steamline Safety/Relief Valves</strong><br /><i>Abstract:&nbsp;</i>On May 21, 2013, the Brunswick Steam Electric Plant as-found testing of 11 safety/relief valves (SRVs) which had been removed from Unit 2 during the spring 2013 refueling outage was completed. The testing indicated that four of the 11 valves were found to lift at more than 3 percent above their Technical Specifications required setpoints. Therefore, these four valves were determined to have been inoperable while the unit was in operation. Since Technical Specification 3.4.3, "Safety/Relief Valves," requires at least 10 of the 11 valves to be operable, this condition is being reported in accordance with 10 CFR 50.73(a)(2)(i)(B) as operation prohibited by the plant's Technical Specifications.<br><br> The setpoint drift occurred because of less than optimum surface finish on SRV pilot discs which caused a loss of the platinum coating followed by corrosion bonding of the discs and seats. Surface finish requirements were known to the personnel who developed the platinum coating process, but these requirements were not included in the procedure used to refurbish the SRVs.<br><br> Corrective actions for this event include defining pilot disc conical seating surface finish requirements for platinum coating and revising the procedure used to control the SRV pilot valve machining process. The entire population of Unit 2 SRVs was replaced during the spring refueling outage with valves that had the correct surface finish on the pilots.
3242013004 | Brunswick 2 | 06/20/2013 | 08/19/2013 | ML13248A45 | <strong>Operation Prohibited by Technical Specifications - Recirculation Loop Flow Mismatch</strong><br /><i>Abstract:&nbsp;</i>On June 20, 2013, Engineering personnel determined that Unit 2 had operated with recirculation loop jet pump flow mismatch in excess of the limits established in Surveillance Requirement (SR) 3.4.1.1 of Technical Specification 3.4.1, "Recirculation Loops Operating." Review of plant data determined that, on two occasions, Unit 2 operated with excessive flow mismatch for greater than the Completion Times associated with Technical Specification (TS) 3.4.1. These conditions are being reported in accordance with 10 CFR 50.73(a)(2)(i)(B) as operations prohibited by the plant's TSs. <br /><br /> The root cause of this event is inadequate rigor in selecting the equipment used to perform SR 3.4.1.1 when the SR was revised to verify recirculation loop flows versus recirculation pump speeds. The SR was revised by Amendments 244 and 272 for Units 1 and 2, respectively, issued December 17, 2007. Corrective actions include completion of procedure revisions to require use of plant process computer recirculation loop flow points as well as control room recirculation loop flow indicators when performing SR 3.4.1.1.
3252013002 | Brunswick 1, Brunswick 2 | 07/29/2013 | 09/27/2013 | ML13283A01 | <strong>Fire Related Unanalyzed Condition that Could Impact Equipment Credited in Safe Shutdown Analysis</strong><br /><i>Abstract:&nbsp;</i>On July 29, 2013, as a result of the transition process from 10 CFR 50, Appendix R, to NFPA 805, a review of the Brunswick Steam Electric Plant (BSEP) Safe Shutdown Analysis identified conditions wherein the appropriate recovery actions were not specified in station procedures to ensure that a protected train of equipment remains available under certain hypothetical fire scenarios. The analysis determined that a postulated fire in specific fire areas could disable critical components, potentially resulting in equipment required for safe shutdown being inoperable. Potentially affected equipment included a Residual Heat Removal pump on each unit, a Nuclear Service Water pump on each unit, a Core Spray pump on Unit 1, and certain 480-volt AC electrical busses on each unit. <br /><br /> The safety significance of this event is minimal. Although deterministic analysis methods used to comply with Appendix R require every possible fire scenario to be addressed, the risk posed by these hypothetical events has been determined by analysis to be minimal. <br /><br /> Corrective actions for this event include establishing fire watches in affected areas and revising fire response procedures to mitigate the consequences of a hypothetical fire in these areas in order to establish compliance with Appendix R and the current licensing basis.
3252013003 | Brunswick 1, Brunswick 2 | 09/17/2013 | 11/14/2013 | ML13338A58 | <strong>Operation Prohibited by Technical Specifications - Service Water System Inoperability</strong><br /><i>Abstract:&nbsp;</i>Brunswick has conducted walkdowns in response to Near Term Task force (NTTF) Recommendation 2.3, Flooding Walkdown of the Near-Term Task Force Review of Insights from the Fukushima Dai-ichi Accident. Two of the conditions identified and corrected as a result of the walkdowns were: (1) an improperly sealed 5-inch conduit that entered the Service Water (SW) building below plant grade elevation, and (2) ten drain hubs in the 20-foot elevation of the SW building that communicated directly with the SW bays. Individually, neither of these conditions could have impacted operability of safety-related equipment under design basis probable maximum hurricane (PMH) conditions. However, on September 17, 2013, Engineering personnel determined that the aggregate effect of the conditions could have resulted in submergence of the motor operated discharge valves for the ten Unit 1 and Unit 2 service water pumps during PMH conditions, potentially causing inoperability of the systems.<br /><br /> The root cause of this event is the historical lack of an external flooding program at Brunswick. As a result, flood protection deficiencies were not appropriately identified and corrected. The corrective actions to prevent recurrence are to develop and implement an engineering program to mitigate consequences of external flooding at Brunswick and to develop topical design basis for internal and external flooding.
3272013001 | Sequoyah 1, Sequoyah 2 | 02/06/2013 | 04/08/2013 | ML13101A31 | <strong>Latent Design Input Inconsistencies Adversely Affect Probable Maximum Flood Analysis</strong><br /><i>Abstract:&nbsp;</i>On July 28, 2009, the Tennessee Valley Authority (TVA) identified latent design input inconsistencies in hydrological computer modeling used for probable maximum flood (PMF) calculations. <br /><br /> The root causes of the condition were an organizational behavior which allowed the latent input inconsistencies to go undetected and management failure to provide oversight of the impact of river system changes on the calculated value of the PMF. The corrective actions to prevent recurrence are to procedurally require a Flood Protection Program, develop formal Flood Protection Program Management Implementing Procedure(s) and Design Standards/Guides, create a formal documented risk management process for all engineering products, formalize the elements of engineering technical rigor, and implement an upper tier integrated risk management process. <br /><br /> Upon discovery, TVA implemented both immediate and interim corrective actions to ensure the Fort Loudoun, Cherokee, Tellico and Watts Bar dams would not overtop during an assumed PMF event.
3272013002 | Sequoyah 1 | 02/28/2013 | 04/29/2013 | ML13120A26 | <strong>Loss of Auxiliary Control Room Instrumentation</strong><br /><i>Abstract:&nbsp;</i>On February 26, 2013, it was determined the Sequoyah Unit 1 auxiliary feedwater (AFW) flow indicators in the auxiliary control room (ACR) had been inoperable from February 8, 2013, until February 16, 2013. The AFW flow indicators in the ACR normally indicate zero. TVA was unable to identify evidence of when exactly they failed. Operators noticed that an Essential Raw Cooling Water indicator failed on February 8, 2013. During troubleshooting on February 15, 2013, it was discovered that two fuses in the circuit cleared. These fuses supply power to instrument loops including power to the AFW flow indicators. When these fuses are blown, power is lost to the flow modifiers that provide indication. The AFW flow indicators are fed from the same power supply that feeds two other instrument loops. A flow modifier that drives a plant computer data point failed resulting in the blown fuses. The fuses and flow modifier were replaced and the indicators were returned to operable status. Based on the review of the data, it was determined the AFW flow indicators had been out of service longer than allowed by Technical Specification 3.3.3.5.
3272013003 | Sequoyah 1 | 08/23/2013 | 10/21/2013 | ML13301A00 | <strong>Limiting Conditions for Operation Exceeded for Emergency Core Cooling System</strong><br /><i>Abstract:&nbsp;</i>On August 8, 2013, position indication for emergency core cooling system (ECCS) A-Train residual heat removal (RHR) Containment Sump Isolation Valve was found showing the valve to be in mid-position. The valve was verified to be in a closed position. On August 14, ECCS valve testing was conducted. Testing identified the 1A RHR Pump Suction Valve failed to close when requested. Operations personnel declared the valve inoperable and remained in the applicable LCO's. Maintenance troubleshooting determined that multiple grounds existed in the control circuits of each of the valves. Water was found in the motor limit-switch housing control circuit of the RHR Containment Sump Isolation Valve. The cause of the condition was that the conduit penetrations for RHR Containment Sump Isolation Valve were not designed to account for groundwater infiltration through the plant concrete structures resulting in leakage into the conduit. Actions are being taken to redesign the conduit penetrations for each Unit's RHR Containment Sump Isolation Valves, to ensure the penetrations are sealed and/or water tight to prevent water from entering the motor operator valve operator associated with each valve.
3272013004 | Sequoyah 1 | 10/21/2013 | 03/27/2014 | ML14092A08 | <strong>Failure to Comply with Technical Specifications for Containment Penetrations During Fuel Movement Resulting from Ineffective Procedures</strong><br /><i>Abstract:&nbsp;</i>Between October 21-28, 2013, workers breached SQN Unit 1 containment penetration X-108 several times during fuel movement while performing plant maintenance. Technical Specification 3.9.4, Containment Building Penetrations, requires that containment building penetrations providing direct access from the containment atmosphere to the outside atmosphere shall be closed during fuel movement. Workers were not aware that use of X-108 penetration was not allowed during movement of irradiated fuel. On October 27, 2013, a Senior Reactor Operator identified penetration X-108, affecting the auxiliary building secondary containment enclosure (ABSCE), was breached without required compensatory measures. The penetration manual valves were subsequently closed and secured. The root cause is ineffective procedures for controlling containment penetration breaches during Modes 5 and 6. A governing procedure will be developed and implemented for controlling breaches of the shield building, ABSCE, control room boundaries, and design basis flood barriers.
3282013001 | Sequoyah 2 | 02/24/2013 | 04/25/2013 | ML13116A21 | <strong>Manual Reactor Trip due to Loss of Hotwell Level</strong><br /><i>Abstract:&nbsp;</i>On February 24, 2013, at 1205 Eastern Standard Time, Operations personnel manually tripped the Sequoyah Unit 2 reactor from approximately 19 percent rated thermal power on imminent loss of condenser hotwell level. Specifically, Operations personnel entered an abnormal operating procedure based on indications of rising condenser pressure. When Operations personnel determined the hotwell level in "B" Condenser could not be maintained, a manual reactor trip was initiated. Prior to the manual reactor trip, the Unit 2 reactor had been at approximately 24 percent power with the main turbine offline for maintenance activities. All control rods fully inserted as required. The auxiliary feedwater system automatically initiated and provided feed water to the steam generators. No complications were experienced during or after the reactor trip. The loss of condenser vacuum indication was caused by the pressure indicator's drain line breaking under cyclic fatigue. It is suspected that initial damage to the drain line was caused during the previous refueling outage. The drain line was replaced prior to restart of the unit. Corrective actions will be performed to provide shielding of the condenser pressure transmitters' drain line, and the surrounding area will be marked as a unit trip hazard. Employees are to receive a briefing regarding the requirement for providing adequate spacing between stored items and sensitive equipment.
3312013001 | Duane Arnold | 03/08/2013 | 05/07/2013 | ML13127A38 | <strong>Emergency Diesel Generator Inoperability Results in Safety System Functional Failure</strong><br /><i>Abstract:&nbsp;</i>On March 8, 2013, while operating at 100% power, the ‘A’ Emergency Diesel Generator (EDG) was in day 2 of 7 of Technical Specification (TS) Limiting Condition for Operation (LCO) in support of embedded conduit inspections. As part of post maintenance testing, the ‘A’ EDG was operated and a small lube oil leak was discovered on the lube oil cooler heat exchanger. After maintenance activities to verify the heat exchanger channel head bolts were properly tight, a second run of the ‘A’ EDG occurred. During this run, the lube oil leak increased to an excessive amount and the ‘A’ EDG was manually tripped. The direct cause of the lube oil leak was inadequate gasket crush from maintenance activities that occurred during October 2012. The root cause of the failure was determined to be misalignment or flaws between the heat exchanger flange mating surfaces. The ‘A’ EDG lube oil heat exchanger was repaired on March 9, 2013 and the EDG was declared operable. A past operability evaluation concluded that the ‘A’ EDG was inoperable from February 16, 2013 to March 8, 2013. Since the ‘A’ EDG was inoperable longer than it’s allowed TS seven day LCO, the event is reportable as a Condition Prohibited by TS. In addition, since the ‘B’ EDG was inoperable on three occasions while the ‘A’ EDG was inoperable, this event is reportable as an Event or Condition Alone That Could Prevent Fulfillment of a Safety Function.
3312013002 | Duane Arnold | 08/22/2013 | 12/20/2013 | ML14002A25 | <strong>Condition Prohibited by Technical Specifications - Reactor Core Isolation Cooling System</strong><br /><i>Abstract:&nbsp;</i>On August 22, 2013 at 1340, while operating at 100% power, during the performance of Surveillance Test Procedure (STP) 3.5.3-02, RCIC System Operability Test, the Reactor Core Isolation Cooling (RCIC) turbine tripped on electronic over-speed immediately upon startup. Subsequent troubleshooting found the RCIC governor controls dropping resistor in the power supply circuit to be partially open. This resulted in less than adequate power supply to the RCIC electronic governor which allowed the RCIC turbine to overspeed and trip on electronic over-speed. The RCIC governor controls dropping resistor was replaced and RCIC was returned to service on August 24, 2013 at 0515. A past operability evaluation determined that the RCIC system was inoperable from June 21, 2013 to August 23, 2013, which is in excess of Technical Specification (TS) 3.5.3 Limiting Condition for Operation Completion Time. Therefore, this event resulted in a Condition Prohibited by TS and is reportable pursuant of 10 CFR 50.73(a)(2)(i)(B). The Root Causes of this event were a failed dropping resistor and an inadequate Operability screening of a Condition Report. The safety significance for this event was very low based on fact that RCIC could have been operated in manual as directed by existing procedures.
3312013003 | Duane Arnold | 09/11/2013 | 11/11/2013 | ML13317B92 | <strong>Condition Prohibited by Technical Specifications - Spent Fuel Storage</strong><br /><i>Abstract:&nbsp;</i>On September 11, 2013, while operating at 100% power, Boron-10 Areal Density Gage for Evaluating Racks (BADGER) test results from June 2013 testing were received by NextEra Energy Duane Arnold, LLC. The results indicated that the areal density used in the criticality analysis of record may not be supported. Specifically, the report indicated that the areal density assumed in the criticality analysis of record as discussed in UFSAR Section 9.1.2.2.1 may not be supported. This conclusion was based on eleven of the tested panels having an average areal density (mass per unit area) below the minimum of 0.0232 gm-B10/cm2 (grams of Boron-10 per squared-centimeter) and nineteen of the tested panels having a minimum (2-inch) areal density below the minimum of 0.0232 gm-B10/cm2. Since the previously noted assumed minimum areal density in the criticality analysis cannot be supported based on testing results, the PaR spent fuel pool racks do not conform to K-infinity and enrichment limits of DAEC. Technical Specification (TS) Design Specifications 4.3.1.1(i) and 4.3.1.1(iii). Therefore, the racks were determined to be Operable but Non-Conforming. This event resulted in a Condition Prohibited by TS and is reportable pursuant of 10 CFR 50.73(a)(2)(i)(B). A Root Cause Evaluation determined the root cause to be insufficient margin to allow for the uncertainty added by BADGER testing.
3312013004 | Duane Arnold | 12/23/2012 | 12/20/2013 | ML14002A25 | <strong>Condition Prohibited by Technical Specifications - Main Steam Line Steam Leak Detection</strong><br /><i>Abstract:&nbsp;</i>On December 23, 2012, while operating at 100% power, Temperature Indicating Switch (TIS) 4479 Channel 1, Turbine Building Main Steam Line 'C', was found indicating 183F. This indication did not meet the acceptance criteria of >= 70F and <= 175F of Surveillance Test Procedure (STP) 3.0.0-01, Instrument Checks. Subsequently, the indicated temperature returned to within its acceptance criteria and no actions were taken to declare TIS-4479 inoperable. On December 28, 2012, TIS-4479, Channel 1 was again found to be outside of its surveillance requirements and was declared inoperable. A Past Operability Review (POR), completed on March 12, 2013, concluded that TIS-4479 was operable from December 23, 2012 to December 28, 2012. The POR conclusion was based on a lack of firm evidence indicating when the TIS was no longer performing its required safety function. A subsequent revision to the POR, completed on October 18, 2013, determined that TIS-4479 was inoperable from December 23, 2013 to December 28, 2012. Technical Specification (TS) 3.3.6.1, Primary Containment Isolation Instrumentation, Required Action D.1, requires the associated Main Steam Line be isolated within 12 hours or be in Mode 3 condition prohibited by TS. The causes of this event were an undetermined failure internal to the TIS and inadequate procedure guidance on how to perform a qualitative channel check as required by TS. TIS-4479 was replaced and returned to service on December 29, 2012.
3312013005 | Duane Arnold | 06/21/2013 | 12/20/2013 | ML14002A25 | <strong>Condition Prohibited by Technical Specifications - Main Steam Line Steam Leak Detection</strong><br /><i>Abstract:&nbsp;</i>On June 21, 2013, while operating at 100% power, Temperature Indicating Switch (TIS) 4480 Channel 1, Turbine Building Main Steam Line `D', was found to have spiked from 133F to 150F. Since the indication was within the acceptance criteria of >= 70F and <= 175F of Surveillance Test Procedure (STP) 3.0.0-01, Instrument Checks, the instrument was not declared inoperable. On June 22, 2013, TIS-4480, Channel 1 was again found to be indicating erratically. A review of TIS-4480 indications from May 5, 2013, indicated a trend was present. Therefore, TIS-4480 was declared inoperable on June 22, 2013. A Past Operability Review (POR) was not completed based on the conclusions of a previous similar event that occurred in December 2012, reference License Event Report (LER) 2013-004. On October 22, 2013, a POR was completed and concluded that TIS-4480 was inoperable from May 5, 2013 to June 22, 2013. Technical Specification (TS) 3.3.6.1, Primaly Containment Isolation Instrumentation, Required Action D.1, requires the associated Main Steam Line to be isolated within 12 hours or be in Mode 3 within 12 hours. Neither of these Required Actions were completed. Therefore, this condition constituted a condition prohibited by TS. The causes of this event were an undetermined failure internal to the TIS and inadequate procedure guidance on how to perform a qualitative channel check as required by TS. TIS-4480 was replaced and returned to service on June 23 , 2013.
3312013006 | Duane Arnold | 12/18/2013 | 02/14/2014 | ML14051A35 | <strong>Both Doors in Secondary Containment Airlock Opened Concurrently</strong><br /><i>Abstract:&nbsp;</i>On December 18, 2013, while operating at 100% power, two workers opened doors concurrently when entering a secondary containment access airlock. Both individuals realized that this was not allowed and closed their respective door; however, the result was a brief inoperability of secondary containment integrity. This resulted in an 8 hour reportable event. The Resident Inspector was notified, and Event Notification Number 49657 was made pursuant to 10 CFR 50.72(b)(3)(v)(C) due to a condition at the time of discovery that prevented the fulfillment of the Secondary Containment safety function.<br /><br /> The apparent cause of the event was determined to be excess strength of a permanent magnet on one of the doors. The monthly surveillance test will be revised to check the permanent magnet for proper adjustment and to adjust it as needed.<br /><br /> This event did not result in a safety system functional failure. There were no radiological releases associated with this event.
3332013001 | FitzPatrick | 01/15/2013 | 03/18/2013 | ML13078A05 | <strong>Failed Under Voltage Relay Results in Auto Start of the Emergency Diesel Generators</strong><br /><i>Abstract:&nbsp;</i>On January 15, 2013, during the performance of surveillance test, ST-43D, “Remote Shutdown Panel 25ASP-3 Component Operation and Isolation Verification,” the James A. FitzPatrick Nuclear Power Plant experienced an automatic start of the B and D emergency diesel generators (EDG). The automatic start of the EDGs was caused by the failure of contact set 3/4 of the 10600 Emergency Bus Under Voltage Relay (71-271AB-1HOEB04) in the closed position. The relay is designed such that these contacts will close when a loss of voltage is detected on the AB phase of the bus. This closure inserts one channel of the two required to start the EDGs on loss of bus voltage. The circuitry detected a loss of voltage condition during the test when the BC phase Bus under voltage relay was actuated per the ST. When the EDG output voltage reached 75% of normal output voltage, the voltage monitoring circuit initiated a trip of the 10614 and10404 breakers which feed the 4kV emergency bus (10600). This resulted in a loss of the 10600 bus voltage, a B side half scram, and group II primary containment isolation. These events are reportable in accordance with 10 CFR 50.73(a)(2)(iv)(A), Any event or condition that resulted in the automatic actuation of general containment isolation signals affecting containment isolation valves in more than one system and the automatic start of the emergency diesel generators.
3332013002 | FitzPatrick | 08/19/2013 | 09/16/2013 | ML13260A08 | <strong>RCIC Condensate Storage Tank Level Switch Inoperable due to Corrosion</strong><br /><i>Abstract:&nbsp;</i>The Reactor Core Isolation Cooling (RCIC) “B” condensate storage tank (CST) level switches failed to trip due to corrosion build-up caused by water intrusion. The first instance in which corrosion interfered with the trip mechanism was when 13LS-76B failed to trip due to corrosion while testing on July 16, 2013. The second instance was both 13LS-76B and 13LS-77B failed to trip due to corrosion on August 19, 2013. These two instruments are 2 of 4 channels for the CST low level function of the RCIC system. The “A” side channels are Operable and show no signs of being affected by corrosion or water intrusion. The “B” side channels share a junction box which is evidently the source of water intrusion from environmental conditions of the CST pit. This deficiency is being corrected by replacing the affected level switches and update testing procedures to identify signs of corrosion.<br /><br /> The Technical Specifications (TS) requires all 4 RCIC CST level switches be Operable. Since two of the level switches were Inoperable due to corrosion the RCIC system also became Inoperable. Since the actions prescribed by the TS were not performed, the RCIC had been in a condition prohibited by TS, 10 CFR 50.73(a)(2)(i)(B).
3332013003 | FitzPatrick | 10/31/2013 | 12/26/2013 | ML13360A26 | <strong>Unfused DC Ammeter Circuits Result in Unanalyzed Condition</strong><br /><i>Abstract:&nbsp;</i>During James A. Fitzpatrick’s (JAF) review of Operating Experience INPO ICES-305419, JAF identified a similar condition. The station’s review determined that the plant wiring design for the station battery ammeter circuits contains a shunt in the current flow from each direct current (DC) battery, with leads to an ammeter in the main control room (MCR). The ammeter wiring attached to the shunt does not have fuses, and if one of the ammeter wires shorts to ground during a fire at the same time another DC wire from the opposite polarity on the same battery also shorts to ground (as a result of the fire), a ground loop through the unfused ammeter cable could occur. With enough current going through the cable, the potential exists that the overloaded ammeter wiring could damage safe shutdown wiring in direct physical contact with the cable resulting in a loss of the associated safe shutdown function/capability or a secondary fire in another fire area.<br /><br /> The cause of this condition is the original design criteria not specifying protection for shunt fed ammeter circuits. The condition is being tracked by the corrective action process; an analysis is underway to determine the appropriate resolution.
3332013004 | FitzPatrick | 11/04/2013 | 01/03/2014 | ML14003A21 | <strong>RCIC Condensate Storage Tank Level Switch Inoperable due to Misalignment</strong><br /><i>Abstract:&nbsp;</i>The Reactor Core Isolation Cooling (RCIC) “B” condensate storage tank (CST) level switch (13LS-76B) failed to trip on November 4, 2013 while performing the switch’s low water level functional test. The cause of the failure was a misalignment of the microswitch assembly. The microswitch assembly was replaced on September 17, 2013; it passed its functional test but microswitch alignment was not performed per vendor instructions which resulted intermittent performance.<br /><br /> 13LS-76B is 1 of 4 channels for the CST low level function of the RCIC system. All other channels are Operable and are unaffected by this microswitch assembly misalignment. Upon discovery, 13LS-76B channel was placed in trip per plant Technical Specifications (TS) and RCIC is Operable. Since, TS require all 4 RCIC CST level switches to be Operable, RCIC was in a condition prohibited by TS. This report is being submitted in accordance with 10 CFR 50.73(a)(2)(i)(B).
3332013005 | FitzPatrick | 11/07/2013 | 01/06/2014 | ML14007A01 | <strong>Failure to Isolate the Reactor Building Results in a Condition Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On November 07, 2013, with the “A” Reactor Building Ventilation Radiation Monitor inoperable, the required action for Technical Specification (TS) 3.3.6.2 Condition A was not met within the required completion time of 24 hours. In addition, the required actions for TS 3.3.6.2 Condition C were also not met within the completion time of 1 hour after the action for Condition A was not completed. The failure to perform the TS required actions within the required completion times resulted in a condition prohibited by the TS which is reportable in accordance with 10 CFR 50.73(a)(2)(i)(B).<br /><br /> The apparent cause of this event was operating procedures instructions were not adequately followed and understood. Additionally control room personnel failed to verify that the actual plant configuration matched the configuration needed to remain compliant with the TS. Immediate corrective actions included isolating the reactor building ventilation system to restore compliance with the TS. All involved control room personnel were removed from watch standing duties. Following remediation, some personnel were reinstated. Operations Management briefed on-coming watch crews on this event and the need to resolve discrepant items identified during turnover. Additionally, Shift Managers were briefed on the need to be more intrusive on TS related work preparation activities and execution.
3332013006 | FitzPatrick | 12/17/2013 | 02/18/2014 | ML14045A28 | <strong>Loss of HPCI Safety Function due to Failure of “B” CST Level Switches</strong><br /><i>Abstract:&nbsp;</i>On the morning of December 17, 2013, at James A. FitzPatrick (JAF) Nuclear Power Plant, with the reactor at 100 percent power, performance of ISP-75 commenced at 0810 EST. ISP-75 functionally tests and calibrates the Condensate Storage Tank (CST) Low Water Level instrument channels of the High Pressure Coolant Injection (HPCI) System. During performance of this planned surveillance, the first level switch associated with the “B” CST that was tested (23LS-74B) failed to actuate. At 0938 EST, the Chief Instrumentation and Controls technician performing the test reported the failure of 23LS-74B to the Control Room Supervisor, and was directed to continue testing per ISP-75. Subsequent testing of the redundant “B” CST level switch (23LS-75B) revealed that the level switch actuated at a simulated CST level of 58.5 inches.<br /><br /> The combination of these two deficiencies would have prevented the HPCI automatic suction swap-over function until the “B” CST level dropped to 58.5 inches. This is less than the analyzed Technical Specification (TS) required value for low CST water level of 59.5 inches; per TS 3.3.5.1 Condition D, this would have resulted in the HPCI system being declared inoperable. Therefore, this event is reportable pursuant to 10 CFR 50.73(a)(2)(v)(D) as an event or condition that could have prevented fulfillment of a safety function.
3342013001 | Beaver Valley 1 | 09/30/2013 | 11/27/2013 | ML13337A17 | <strong>Manual Start of a Motor Driven Auxiliary Feedwater Pump</strong><br /><i>Abstract:&nbsp;</i>At approximately 0228 hours on September 30, 2013, during a planned shutdown of Beaver Valley Power Station (BVPS) Unit 1 for a refueling outage, the "B" motor driven Auxiliary Feedwater (AFW) pump was manually started, while in Mode 3, due to lowering levels in the steam generators.<br /><br /> The condensate pump recirculation flow Control valve opened to approximately 40 percent, which resulted in a reduction of the condensate flow to the steam generators and a decrease in the steam generator levels. The operators recognized that adequate feedwater flow was not available using the normal flow path of the condensate pump through the bypass feedwater regulating valves to the steam generators. In response to the lowering steam generator levels, the operators manually started the "B" motor driven AFW pump to restore the steam generator water levels. Following the start of the AFW pump, the steam generator levels were returned to their normal operating control band. The apparent cause of this event was that the condensate flow control valve opened when it was not intended due to the associated flow controller being out of calibration. The controller was repaired and functionally checked during the refueling outage.<br /><br /> This event is being reported under 10 CFR 50.73(a)(2)(iv) as a condition that resulted in the valid manual start of a system listed in (a)(2)(iv)(B)(6) - Auxiliary Feedwater. The safety significance associated with the manual start of the AFW pump is considered to be very low.
3342013002 | Beaver Valley 1 | 10/04/2013 | 02/14/2014 | ML14051A44 | <strong>Containment Liner Through Wall Defect Discovered During Planned Visual Inspection</strong><br /><i>Abstract:&nbsp;</i>During the Beaver Valley Power Station (BVPS) Unit 1 1R22 Refueling Outage, a through wall defect was discovered during a planned visual examination of the Reactor Containment Building (RCB) steel liner. The BVPS Unit 1 containment design consists of an internal steel liner that is surrounded by reinforced concrete. Investigation and laboratory analysis determined that there were indications of two through wall penetrations with a possible third penetration slightly off-set from the second. The total combined area of the three penetrations was calculated to be 0.395 square inches. A visual inspection of 100 percent of the accessible liner area was completed. No additional significant indications of corrosion were identified. Prior to startup from 1R22, the RCB steel liner was repaired and tested satisfactory.<br /><br /> The direct cause of this event was determined to be pitting type corrosion, originating from foreign material introduced during the original construction of the containment wall.<br /><br /> An evaluation determined that there is reasonable assurance that the containment was operable during the period of time that the plant was operated with the small areas of through wall corrosion on the steel liner. Therefore, there was no loss of safety function and the safety significance is considered to be very low. This event is being reported under 10 CFR 50.73(a)(3)(ii)(A) as a condition resulting in a principal safety barrier being degraded.
3342013003 | Beaver Valley 1 | 11/05/2013 | 01/06/2014 | ML14008A11 | <strong>Beaver Valley Unit 1 Turbine Trip and Subsequent Manual Reactor Trip due to 4KV Cable Fault</strong><br /><i>Abstract:&nbsp;</i>On November 5, 2013 at 1747 hours, Beaver Valley Power Station (BVPS) Unit 1 was operating at 47 percent power after the 1R22 Refueling Outage. The Unit 1 Control Room received multiple unexpected alarms. The Turbine/Generator tripped due to Unit Station Service Transformer (USST) "BV-TR-1C" differential protection relay actuation. This transformer was energized but not in service at the time. The reactor operator manually tripped the reactor due to multiple unexpected alarms. An automatic reactor trip signal was not generated due to the fact that the reactor was operating at a power level less than the turbine trip - reactor trip setpoint of 49 percent power. The Steam Driven Auxiliary Feedwater (AFW) pump automatically started due to low level in the "C" Steam Generator. The "B" Motor Driven AFW pump was manually started to assist in maintaining steam generator levels. An Unusual Event was declared at 1828 hours due to reports from the fire brigade that an explosion had occurred in a cable tray in the Unit 1 turbine building mezzanine. The cause of this event was determined to be a fault in the "B" 4KV bus supply cables from BV-TR-1C that resulted in an arc flash and subsequent fire. Corrective actions include planned replacement of the faulted supply cables and inspections of the remaining Unit 1 and Unit 2 4KV bus supply cables for signs of degradation and aging. <br /><br /> This event is being reported under 10 CFR 50.73(a)(2)(iv)(A) as a condition that resulted in the valid manual and automatic actuation of systems listed in (a)(2)(iv)(B) - (1) manual Reactor trip, (6) manual and automatic Auxiliary Feedwater pump start. A 10 CFR 50.72 notification was made at 1927 hours on November 5, 2013 to report entry into an Unusual Event, RPS Actuation and a Specified System, Auxiliary Feedwater actuation (EN 49505).
3352013001 | St. Lucie 1 | 03/12/2013 | 05/10/2013 | ML13142A20 | <strong>Automatic Reactor Trip due to Failure of the 1B Main Steam Isolation Valve</strong><br /><i>Abstract:&nbsp;</i>On March 12, 2013 at 1451 EDT, St. Lucie Unit 1 was in Mode 1 at 100% reactor power when the spurious closure of HCV-08-1B, 1B Main Steam Isolation Valve (MSIV), resulted in an automatic reactor trip. Upon troubleshooting and valve disassembly, it was discovered that interference between the internal tail link and the valve body prevented the valve disc from fully opening. This allowed unintentional loading of internal parts resulting in the failure of the valve's lower shear pin. The pin failure led to spindle/disc separation and inadvertent closure of the valve.<br><br> This reactor trip event is reportable pursuant to 10 CFR 50.73(a) (2) (iv) (A) as an automatic actuation of the reactor protection system (RPS). This event had no significant safety consequence since the RPS successfully performed its intended safety function upon the failure of the 1B MSIV.<br><br> The internal interference was caused by an oversized tail link supplied by the valve manufacturer. To correct the problem, the tail link was reworked to eliminate the body interference, and the MSIV was reassembled.<br><br> This event had no effect on the health and safety of the public.
3352013002 | St. Lucie 1 | 11/12/2013 | 01/13/2014 | ML14024A60 | <strong>Unplanned Manual Reactor Trip Due to Digital-Electro-Hydraulic (DEH) System Leak</strong><br /><i>Abstract:&nbsp;</i>On November 12, 2013 St. Lucie (PSL) Unit 1 was manually tripped due to a digital-electro-hydraulic (DEH) fluid leak from a tubing fitting in the turbine control system. Prior to the reactor trip, PSL Unit 1 was at 90% power ascending to 98% power following the SL1-25 refueling outage. Following the reactor trip, emergency operating procedures were successfully completed and the unit was stabilized in Mode 3. The reactor trip was uncomplicated. All systems functioned as designed. There were no automatic safety system actuations as a result of the trip. <br /><br /> A root cause evaluation was performed which identified the cause as failure of a DEH tubing fitting as the result of high cycle fatigue fracture and inadequate tubing support following a DEH pump replacement. <br /><br /> Corrective actions include: 1) update of the engineering procedure for post-modification testing and 2) update of the maintenance procedure for post-maintenance testing, to inspect for vibration and inadequate support of adjacent tubing/piping after a change to a vibration inducing component (pump, fan, etc.) <br /><br /> This reactor trip event is reportable pursuant to 10 CFR 50.73(a)(2)(iv)(A) as a manual actuation of reactor protection system (RPS). This event had no significant safety consequence. Given the response of the plant and the actions taken, the health and safety of the public was not affected by this event.
3362013001 | Millstone 2 | 01/17/2013 | 03/12/2013 | ML13080A25 | <strong>Historical Acoustic Monitor Channel Check Discovered to Have Not Met Acceptance Criteria</strong><br /><i>Abstract:&nbsp;</i>At 0938 on January 15, 2013, with Millstone Power Station Unit 2 (MPS2) in Mode 1, operating at 100 percent power, while performing a monthly required channel check on the safety valve's position indication, technicians discovered that the channel B primary safety valve acoustic valve monitor system (AVMS) position indicator failed to meet acceptance criteria contained in Surveillance Procedure SP2410A. In this instance, the technicians had expected to observe a frequency peak at or near 74.25 Hz on the AVMS' output, which is induced by an operating reactor coolant pump. After reviewing a printout obtained from the instrumentation loop, it was determined that the frequency peak expected at or near 74.25 Hz was not detected. Therefore, the AVMS channel was declared inoperable and Operators entered Technical Specification (TS) 3.3.3.8, Accident Monitoring Instrumentation, Action 3, for Item 6, Safety Valve Position Indicator, which specifies that alternate indications shall be checked once each shift. On January 17, 2013, upon reviewing the results from the previous month's completed channel check surveillance performed in December 2012, it was discovered that the instrument had also failed to meet the acceptance criteria for a channel check in SP2410A at the time. However, it was not recognized that the surveillance results did not meet acceptance criteria, so the instrument was not declared inoperable at the time. This condition is being reported pursuant to 10 CFR 73(a)(2)(i)(B) as any operation or condition which was prohibited by the plant's Technical Specifications. The cause was determined to be inadequate procedure guidance in SP2410A which led to confusion when interpreting surveillance results. The surveillance procedure has been revised to include clear acceptance criteria for a channel check.
3362013002 | Millstone 2 | 03/07/2013 | 05/06/2013 | ML13141A28 | <strong>Turbine Driven Auxiliary Feedwater Pump HELB Door Left Open During Surveillance Test</strong><br /><i>Abstract:&nbsp;</i>On March 7, 2013, with Millstone Power Station Unit 2 in MODE 1 at 100% power, during a turbine driven auxiliary feedwater (TDAFW) pump surveillance test, the operators left the door to the TDAFW pump room open. This condition existed for approximately 30 minutes. The door is a high energy line break (HELB) barrier. With the door open there is no HELB protection for the motor driven auxiliary feedwater (AFW) pumps thus potentially rendering both trains of AFW inoperable. Additionally, during the surveillance run the TDAFW pump was declared inoperable.<br><br> The HELB requirements during operation of the TDAFW pump were not fully considered during the pre-job brief.<br><br> Management has reinforced expectations to Operations Department personnel and station personnel on the need to ensure the requirements for any barrier are met prior to opening any door or duct. Training for Operations, Maintenance and Engineering is planned to reinforce understanding of expectations concerning passive design features, like flood barriers, fire doors and HELB barriers. Additional corrective actions are being taken in accordance with the station's corrective action program.<br><br> This event is being reported pursuant to 10 CFR 50.73(a)(2)(v) as any event or condition that alone could have prevented the fulfillment of the safety function of structures or systems that are needed to: (B) Remove residual heat; and (D) Mitigate the consequences of an accident.
3362013003 | Millstone 2 | 10/30/2013 | 12/18/2013 | ML14023A59 | <strong>Postulated DC Ammeter Circuit Hot Shorts</strong><br /><i>Abstract:&nbsp;</i>While Millstone Power Station Unit 2 (MPS2) was operating at 100 percent power in Mode 1 on October 30, 2013, operations determined that a concern identified by Engineering as a result of recent industry operating experience could result in an unanalyzed condition. Engineering's review of the impact of unfused direct current (DC) ammeter circuits in the Control Room determined the described condition to be applicable to MPS2. It is postulated that a fire could cause one of the DC ammeter wires to hot short to ground. Concurrently, the fire causes another DC wire from the opposite polarity on the same battery to also short to ground. This would cause a current path through the unfused ammeter cable. The original plant wiring design and associated circuitry analysis for the DC ampere indications do not include overcurrent protection features to limit the fault current in this scenario.<br /><br /> This condition is reportable pursuant to 10 CFR 50.73(a)(2)(ii)(B) as an unanalyzed condition that significantly degraded plant safety. A prompt notification per EN49487 was submitted to the NRC on October 30, 2013.<br /><br /> The cause of the condition was a latent design error that was made during plant construction. Compensatory measures, i.e., fire watches, have been implemented for affected areas of the plant. Plant modifications are planned that will protect or isolate the affected circuits leaving the initial fire area.
3362013004 | Millstone 2 | 11/09/2013 | 12/19/2013 | ML14002A31 | <strong>Reactor Trip While Backwashing D Waterbox</strong><br /><i>Abstract:&nbsp;</i>On November 9, 2013, at 1514, Millstone Power Station Unit 2 (MPS2) experienced a turbine trip and an automatic reactor trip from 95% power MODE 1 due to loss of condenser vacuum. The Unit was in the process of condenser backwashing operations when condenser vacuum was lost due to unexpected pump ramp-down of the 'C' circulating water pump (CWP) when the 'D' CWP was secured as required by procedure.<br /><br /> All control rods inserted on the reactor trip. An auxiliary feedwater (AFW) automatic start occurred post trip, as expected per design, and all other safety systems functioned as required.<br /><br /> The direct cause of the event was the MPS2 'C' CWP ramped off due to failure of contacts on a time-delay relay to deenergize as designed.<br /><br /> The defective relay was replaced. Additional corrective actions are being taken in accordance with the station's corrective action program.<br /><br /> This event is being reported per 10 CFR 50.73(a)(2)(iv)(A) as an event that resulted in a manual or automatic actuation of systems listed in 10 CFR 50.73(a)(2)(iv)(B). Actuations of the reactor protection system and the AFW system are reportable under this paragraph.
3382013001 | North Anna 1 | 09/26/2013 | 12/20/2013 | ML14002A12 | <strong>Unit 1 Emergency Diesel Generators Inoperable During Core Alterations</strong><br /><i>Abstract:&nbsp;</i>On September 26, 2013, at 1717 hours with Unit 1 in Mode 6, zero percent power, core alterations began with two inoperable emergency diesel generators. One emergency diesel generator (1J EDG), in a two train system, was out of service for maintenance with the second emergency diesel generator (1H EDG) inoperable, but unknown at the time. A subsequent failure of the 1H EDG during a 24 hour run, parallel to the grid, determined prior inoperability. Technical Specifications 3.8.2 requires one operable qualified circuit between the offsite transmission network and the onsite Class 1E AC electrical power distribution subsystem(s) required by TS 3.8.10 and one OPERABLE EDG. Momentary loss of control power to the Digital Reference Unit (DRU) caused it to reset to the 60 HZ setting which unloaded the EDG. A loose fuse holder caused the momentary loss of control power. This event is reportable per 10 CFR 50.73(a)(2)(i)(B) for a condition prohibited by Technical Specifications. One qualified circuit between the offsite transmission network and the onsite Class 1E AC electrical power distribution subsystem(s), required by TS 3.8.10, was OPERABLE and the station blackout EDG was also available. Additionally, had a loss of offsite power occurred, the 1H EDG would have been able to supply power in the isochronous mode to the emergency bus. Therefore, the health and safety of the public were not affected by the event.
3382013002 | North Anna 1 | 10/11/2013 | 12/06/2013 | ML14002A24 | <strong>Automatic Reactor Trip following Actuation of the 1C Station Service Transformer Lockout Relay</strong><br /><i>Abstract:&nbsp;</i>On October 11, 2013, at 1319 hours with Unit 1 operating at 48 percent power (Mode 1), an automatic turbine trip and subsequent reactor trip occurred due to a lockout relay actuation for the 1C Station Service Transformer (1-EP-SST-1C). The lockout occurred simultaneously with the start of the 1C Condensate Pump (1-CN-P-1C). The direct cause of the 1-EP-SST-1C lockout is that current transformer terminal block shorting screws were left installed inside the 1- EP-BKR-15C2 breaker cubicle. The root cause of the event was less than adequate written instructions for documenting the installation and removal of the terminal block shorting screws. All safety system responded as expected. The Auxiliary Feedwater Pumps actuated as designed following the reactor trip and provided makeup flow to the Steam Generators. 1-EP-SST-1C was inspected and no signs of damage or abnormal conditions were observed. At 1507 hours, a 4 hour report was made to the NRC in accordance with 10CFR50.72(b)(2)(iv)(B) for a Reactor Protection System (RPS) actuation and a 8 hour report in accordance with 10CFR50.72(b)(3)(iv)(A) for a Auxiliary Feedwater system actuation. The event is reportable pursuant to 10CFR50.73(a)(2)(iv)(A) for a condition that resulted in the automatic actuation of the RPS and AFW Systems. The health and safety of the public were not affected by the event.
3382013003 | North Anna 1, North Anna 2 | 11/21/2013 | 01/16/2014 | ML14035A06 | <strong>Units 1 and 2 Outside Recirculation Spray Pumps Declared Inoperable</strong><br /><i>Abstract:&nbsp;</i>On November 21, 2013, at 2006 hours with Units 1 and 2 operating at 100 percent power (Mode 1), Engineering personnel determined that the Casing Cooling tank low level setpoint does not account for vortexing. During a review of the Channel Statistical Allowance (CSA), it was identified that the final Casing Cooling tank level would be below the top of the pump suction nozzle when accounting for the full CSA on the low level bistable and closure time for tank isolation motor operated valves. This condition could have allowed air entrainment and caused a reduction in Recirculation Spray system flow during a Containment Depressurization Actuation. As a result, the Outside Recirculation Spray (ORS) pumps for both units were declared inoperable and Technical Specification (TS) 3.0.3 was entered for each unit. A prompt report was made to the NRC and an Operability Determination was completed with actions to isolate the Casing Cooling tank on a low level at less than or equal to 10% versus the current setpoint of 4%. This change restored operability of the ORS pumps and TS 3.0.3 was exited at 2217 hours, prior to ramping the units. This event is reportable pursuant to 10CFR50.73(a)(2)(v)(D) for a condition that could have prevented the fulfillment of a safety function. The health and safety of the public were not affected by this event.
3392013001 | North Anna 2 | 05/10/2013 | 07/02/2013 | ML13205A17 | <strong>Manual Reactor Trip Due To Increased Vibrations on Main Turbine/Generator Bearing Number 9</strong><br /><i>Abstract:&nbsp;</i>On May 10, 2013, at 0612 hours with Unit 2 in Mode 1, 60 percent power following a refueling outage, a manual reactor trip was initiated as a result of increased vibrations on the number 9 main turbine/generator bearing and a report of a luminous discharge in the main generator exciter enclosure. All systems responded as expected following the manual trip. The auxiliary feedwater (AFW) pumps received an automatic start signal due to the resulting low-low level in "C" Steam Generator (SG). The AFW System operated as designed with no abnormalities noted and was subsequently returned to automatic operation. The SG levels were restored to normal operating level. When resetting AMSAC, a second AFW system automatic start occurred due to a procedure sequence error and was determined to be an invalid signal. At 0820 hours, a 4 hour report was made in accordance with 10CFR50.72(b)(2)(iv)(B) for Reactor Protection System (RPS) actuation and 8 hour report in accordance with 10CFR50.72(b)(3)(iv)(A) for the first AFW pump automatic start. This event is reportable per 10 CFR 50.73(a)(2)(iv)(A) for a condition that resulted in automatic actuation of the RPS and AFW System. The health and safety of the public were not affected by the event since the equipment responded as designed.
3392013002 | North Anna 2 | 05/28/2013 | 07/23/2013 | ML13212A08 | <strong>Manual Reactor Trip due to Closure of 2-FW-MOV-250C and Auto-Start of 2-FW-P-1B</strong><br /><i>Abstract:&nbsp;</i>On May 28, 2013, at 1507 hours with Unit 2 operating at 98 percent power (Mode 1), a manual reactor trip was initiated due to a main feedwater system transient. The main feedwater system transient resulted from the spurious closure of the "C" Main Feedwater Pump Discharge Motor-Operated Valve, 2-FW-MOV-250C, that subsequently resulted in the tripping of "A" Main Feedwater pump on low suction pressure. The cause of the spurious closure of 2-FW-MOV- 250C was a loss of conductivity in the upper cell switch of breaker 2-EP-BRK-25C5 which indicated that one motor on 2-FW-P-1C had tripped. At 1809 hours, a 4 hour report was made to the NRC in accordance with 10CFR50.72(b)(2)(iv)(B) for a Reactor Protection System (RPS) actuation and a 8 hour report in accordance with 10CFR50.72(b)(3)(iv)(A) for a Auxiliary Feedwater system actuation. The event is reportable pursuant to 10CFR50.73(a)(2)(iv)(A) for a condition that resulted in the automatic actuation of the RPS and AFW Systems. The health and safety of the public were not affected by the event.
3392013003 | North Anna 2 | 07/04/2013 | 08/30/2013 | ML13254A20 | <strong>2A Station Service Bus Under Frequency Protection Relay Inoperable Greater Than Technical Specification Completion Time</strong><br /><i>Abstract:&nbsp;</i>On July 1, 2013, at 2217 hours with Unit 2 operating at 100 percent power (Mode 1), Unit 2 annunciator, 2G-B5 "Station Service Busses 2A-2B-2C UV Relay Trouble" alarmed and locked in. Troubleshooting indicated that the under voltage (UV) relay monitoring B-C phase for Station Service Bus 2A had actuated. The 2A UV channel was placed into trip on July 3, 2013, per Technical Specification 3.3.1 Condition L, but the 2A under frequency (UF) channel was not placed into trip. On July 3, 2013, a multidiscipline team, including the vendor, determined that the UF relay would remain operable with the degraded voltage. An Operability Determination was developed and approved to document the conclusion. However, on July 10, 2013, it was revealed through additional testing that the operability determination contained inaccurate information and the 2A UF relay would not operate within the required time frame. The 2A UF relay channel was subsequently placed in trip on July 10, 2013. A potential transformer blown fuse was replaced and the UV and UF channels were restored to operable on July 22, 2013. This event is reportable pursuant to 10CFR50.73(a)(2)(i)(B) for a condition prohibited by Technical Specifications (TS) when the inoperable UF channel was not placed into trip within the time limits of TS. The health and safety of the public were not affected by the event.
3412013001 | Fermi 2 | 01/22/2013 | 03/18/2013 | ML13078A05 | <strong>Loss of Secondary Containment Function</strong><br /><i>Abstract:&nbsp;</i>On January 22, 2013, at approximately 0113 hours EST, during startup of the Reactor Building Heating Ventilation and Air Conditioning (RBHVAC) system, with the Standby Gas Treatment System operating, Secondary Containment pressure went positive for 27 seconds, reaching approximately +0.15 inches of water column (WC). The RBHVAC Center Exhaust Fan discharge damper appears to have opened after the Supply Fan discharge damper opened contrary to design, causing the Secondary Containment pressure increase. The System was returned to normal with two RBHVAC trains running and Standby Gas Treatment System shutdown and in standby. Reactor building pressure stabilized at less than -0.125 inches WC. The causes of this event appear to be delayed operation of the center RBHVAC exhaust fan discharge damper and relay timing out of tolerance for the RBHVAC Center Supply and Exhaust fan dampers. Work Management procedures are being followed to troubleshoot the actuator for the discharge damper and the supply and exhaust fan relay timing. This event has been entered into the Fermi 2 Corrective Action Program. Investigation continues and could result in additional corrective actions.
3412013002 | Fermi 2 | 08/30/2013 | 10/22/2013 | ML13296A58 | <strong>Reactor Core Isolation Cooling Isolation Instrumentation Misconfigured Wiring</strong><br /><i>Abstract:&nbsp;</i>On August 30, 2013 at approximately 0017 hours, while performing a routine surveillance procedure, Instrumentation and Control (I&C) technicians discovered that a thermocouple was improperly wired which resulted in an inoperable Division I Reactor Core Isolation Cooling (RCIC) area room temperature input to the associated steam line isolation logic. The improper wiring was determined to be in place for approximately 14 days without isolation of the RCIC steam line which is greater than allowed by Technical Specification 3.3.6.1. The event was caused by technicians incorrectly replacing terminal block knife switches on August 16, 2013. Insufficient rigor was applied by the technicians during concurrent verification activities for interim alterations of the associated isolation circuitry. The thermocouple wiring was promptly corrected, the associated Channel Functional Test was satisfactorily completed at 0145 hours on August 30, 2013, and the equipment was returned to service. The qualifications of the technicians involved were removed until such time as the individuals were retrained. Re-training on verification practices was conducted with I&C Group personnel.
3412013003 | Fermi 2 | 11/24/2013 | 01/22/2014 | ML14022A26 | <strong>Loss of Secondary Containment Function due to Exceedance of Technical Specification Required Vacuum Pressure</strong><br /><i>Abstract:&nbsp;</i>On November 24, 2013, at approximately 00:01 hours EST, during normal plant operations, the non-safety related Reactor Building Heating Ventilation and Air Conditioning (RBHVAC) system tripped on low steam coil heater temperature. Secondary Containment differential pressure exceeded the Technical Specification (TS) Surveillance Requirement limit of -0.125 inches water column (WC), reaching a maximum of +0.08 inches WC. At 00:04 hours EST, the Standby Gas Treatment System (SGTS) was started and Secondary Containment differential pressure decreased to less than -0.125 inches WC. The RBHVAC system tripped due to lack of steam flow through a heating coil caused by inadequate draining of the downstream steam trap. Investigation revealed the presence of some corrosion and a cracked drain seat in the associated steam drain. The degraded steam drain was then replaced and tested. RBHVAC was returned to normal operation and SGTS was shutdown and returned to standby at 23:46 hours EST on November 24, 2013. Preventive maintenance is being scheduled to inspect, and clean or replace the RBHVAC steam traps and strainers.<br /><br /> With Secondary Containment differential pressure exceeding -0.125 inches WC, TS Surveillance Requirement 3.6.4.1.1 was not met and Secondary Containment was declared inoperable. No other degradation of Secondary Containment existed at the time of the event. This event was reported per the guidance of NUREG-1022, Rev. 3, section 3.2.7, as a loss of Safety Function. There were no radiological releases associated with this event.
3412013004 | Fermi 2 | 12/14/2013 | 06/20/2014 | ML14171A43 | <strong>Condition Prohibited by Technical Specifications for 480 Volt Bus Inoperable due to Failed Voltage Regulator</strong><br /><i>Abstract:&nbsp;</i>On April 21, 2014, an Engineering past operability evaluation of the electrical 72E Bus Voltage Regulator determined that the AC power distribution bus would have been inoperable under degraded grid voltage conditions during a design basis accident. After reviewing weekly voltage readings from December 2013, it was concluded the 72E Bus Voltage Regulator had stopped functioning between December 14, 2013 and December 21, 2013, while the plant was in Mode 1. Limiting Condition for Operation 3.8.7 for the loss of one 480V bus required completion time was exceeded and is reportable under 10 CFR 50.73(a)(2)(i)(B) as an operation or condition which was prohibited by the plant's Technical Specifications.<br /><br /> Inspection of the 72E Bus Voltage Regulator revealed significant wear on the worm gear assemblies. This wear was found on all three worm assemblies and contributed to looseness and excess movement causing binding to occur. Binding caused the drive motors to draw a higher current and overheat, leading to motor failure. After replacing all worn and degraded parts, the voltage regulator was reassembled and satisfactorily passed post maintenance testing.
3462013001 | Davis-Besse | 06/29/2013 | 08/27/2013 | ML13247A66 | <strong>Reactor Trip Due to Reactor Coolant Pump Motor Faulty Electrical Connection</strong><br /><i>Abstract:&nbsp;</i>On June 29, 2013, at 2120 hours, with the Davis-Besse Nuclear Power Station'operating at approximately 100 percent power, the Reactor Coolant Pump (RCP) Motor 1-2 tripped due to actuation of a differential trip relay in the motor source breaker. This resulted in a reactor trip at 2122 hours from the Reactor Protection System on Flux/Delta-Flux/Flow. Investigation determined the cause of the RCP motor trip to be a failure in the current transformer (CT) circuit. A screw on the RCP Motor 1-2 CT terminal block had a stress/fatigue related failure which caused the wire to detach in the CT circuitry causing an open circuit and actuation of the differential trip. The investigation also found degraded wiring in the CT circuit because it was touching the high voltage buss bar insulation in the RCP motor termination box and experienced degradation caused by corona discharge. The CT wiring and terminal block including all screws were replaced. The screws were replaced with a different type of material. Procurement documents will be revised to ensure replacement hardware is of appropriate quality to meet ANSI standards. The CT wiring, terminal blocks and screws in all four RCPs will be inspected during the next scheduled outage. <br /><br /> This report is being submitted in accordance with 10 CFR 50.73(a)(2)(iv)(A) as an event that resulted in automatic actuation of the Reactor Protection System.
3462013002 | Davis-Besse | 07/01/2013 | 08/27/2013 | ML13247A66 | <strong>Leak from Reactor Coolant Pump Seal Piping Socket Weld due to High Cycle Fatigue</strong><br /><i>Abstract:&nbsp;</i>On July 1, 2013, with the Davis-Besse Nuclear Power Station in Mode 3 and the Reactor Coolant System at normal operating temperature and pressure, a leak from Reactor Coolant Pump (RCP) 1-2 first stage seal vent cavity line was identified. The 8 to 9 drops per minute leak was from a flange socket weld of the small bore ASME Section III Class 2 piping between the RCP seal and the first isolation valve. The station cooled down to Mode 5 and replaced the spool piece containing the weld. <br /><br /> Laboratory failure analysis concluded the cause of this leak to be high cycle fatigue of the seal cavity vent line socket weld. The high cycle fatigue was due to a less than adequate design modification to minimize vibration of the line. Planned corrective actions, based upon a weld leak identified in 2012 on the same line, include either replacement of this and similar seal piping for all four RCPs with flexible hoses or increasing the socket weld size during the next refueling outage, and performing walkdowns of risk significant socket welded piping susceptible to vibration fatigue failures. <br /><br /> This event is being reported pursuant to 10 CFR 50.73(a)(2)(ii)(A) as degradation of a principal safety barrier.
3482013001 | Farley 1 | 06/11/2013 | 08/08/2013 | ML13221A27 | <strong>Automatic Reactor Trip and B-Train Loss of Off-Site Power Caused by the Failure of a Startup Transformer Lightning Arrester</strong><br /><i>Abstract:&nbsp;</i>On June 11, 2013 at 2105, Unit 1 automatically tripped from 100% power due to a Reactor Coolant Pump (RCP) undervoltage condition on the 1B and 1C RCPs and experienced a BTrain loss of off-site power (LOSP). The RCP undervoltage condition and B-Train LOSP were caused by the trip of the 1B Startup Transformer. The B-Train LOSP resulted in the automatic start and load sequencing of the 1B Emergency Diesel Generator. All three Auxiliary Feedwater (AFW) Pumps auto-started during the event. All systems responded as expected to the reactor trip and B-Train LOSP. The reactor trip, diesel generator auto-start, and AFW auto-start are reportable as system actuations per 10 CFR 50.73(a)(2)(iv)(A). The direct cause of the trip of the 1B Startup Transformer was the failure of a lightning arrester on the switchyard supply to the startup transformer. The 1B Startup Transformer was returned to service following replacement of the failed lightning arrester. The root cause of the event was determined to be a compromise of the lightning arrester sealing plate during factory assembly which led to moisture ingress into the arrester. Corrective actions for this event will include replacement of similar vintage lightning arresters.
3482013002 | Farley 1 | 10/04/2013 | 01/31/2014 | ML14031A40 | <strong>1B Emergency Diesel Generator in a Condition Prohibited by Technical Specifications due to an Unreliable Mechanism Operated Cell Switch</strong><br /><i>Abstract:&nbsp;</i>At 1202 CDT on October 4, 2013, while Unit 1 was in Mode 6, the B-Train Emergency Safeguards System (ESS) sequencer failed to actuate during the performance of procedure FNP-1-STP-40.0B (B-Train Safety Injection with Loss of Off-Site Power Test - B Train). Immediate investigation of the actuation failure identified that the Mechanism Operated Cell (MOC) Switch for the 1B Emergency Diesel Generator output breaker failed to actuate which resulted in no start signal for the B-Train ESS sequencer. At the time of the test, B-Train systems were not required by Technical Specifications to be in an operable condition. However, subsequent reviews of historical data have identified that the 1B Diesel Generator output breaker MOC switch failed to operate several times since August of 2010 during surveillance testing. Due to the history of this MOC switch, the 1B Diesel Generator is considered to have been inoperable for extended periods. This is reportable as a condition prohibited by Technical Specifications per 10 CFR 50.73(a)(2)(i)(B). Due to opposite train equipment being removed from service for various reasons during the affected periods this is also reportable as a condition that could have prevented fulfillment of a safety function per 10 CFR 50.73(a)(2)(v)(B,C,D). The direct cause of the MOC switch failure was determined to be inadequate lubrication.
3482013003 | Farley 1 | 11/05/2013 | 02/21/2014 | ML14052A43 | <strong>1C Steam Generator Flow Transmitter Inoperable Longer Than Allowed by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On November 5, 2013, with Unit 1 operating in Mode 1 at 100% power, Engineering personnel performing normalization calculations using beginning-of-cycle power ascension data identified that 1C Steam Generator Steam Flow Transmitter, FT-495, did not meet the acceptance criteria for normalization. Based on this information, the steam flow instrument was declared inoperable and the required actions of the appropriate Technical Specification were performed. However, since the data utilized in the engineering calculation was obtained on October 31, 2013, it is known that the channel had been inoperable since October 31, 2013. Consequently, the time limits of the applicable Technical Specification Required Action were not met. This represents a condition prohibited by Technical Specifications and is reportable under 10 CFR 50.73(a)(2)(i)(B). As an immediate corrective action, the steam flow loop was re-calibrated and returned to service on November 6, 2013. The apparent cause of this event was determined to be ineffective responses to previous events involving steam flow instruments not meeting normalization acceptance criteria. Corrective actions include providing additional margin in the normalization process and to pursue improvements in the scaling methodology to allow more timely identification of scaling inaccuracies.
3482013004 | Farley 1, Farley 2 | 12/16/2013 | 02/14/2014 | ML14045A34 | <strong>Unfused DC Ammeter Circuits Result in an Unanalyzed Condition</strong><br /><i>Abstract:&nbsp;</i>On December 16, 2013, while Farley Units 1 and 2 were both operating at 100 percent power in Mode 1, a review of industry operating experience related to unfused direct current (DC) ammeter circuitry was concluded. This review determined that the condition of unfused DC ammeter circuitry was applicable to both Farley units and that a postulated fire could result in concurrent shorts to ground of a DC ammeter cable and a DC cable of opposite polarity. Due to a lack of overcurrent protection, the resultant excessive current flow in the ammeter cable could result in a secondary fire in another fire area. The secondary fire could adversely affect alternate safe shutdown capability contrary to 10 CFR 50, Appendix R, requirements.<br /><br /> This condition is reportable pursuant to 10 CFR 50.73(a)(2)(ii)(B) as an unanalyzed condition that significantly degraded plant safety.<br /><br /> The cause of the condition was a latent design deficiency due to original plant design not providing DC ammeter circuits with overcurrent protection. Compensatory measures have been implemented for affected areas of the plant. Plant modifications are in development to provide these circuits with overcurrent protection.
3522013001 | Limerick 1 | 03/20/2013 | 05/20/2013 | ML13140A32 | <strong>High Pressure Coolant Injection System Pressure Switch Lubricating Oil Leak</strong><br /><i>Abstract:&nbsp;</i>The high pressure coolant injection (HPCI) system was rendered inoperable during a pump, valve, and flow surveillance test. The cause of the HPCI inoperability was a turbine lube oil system bellows actuated pressure switch failure which resulted in an oil leak. The apparent cause of the pressure switch bellows failure was corrosion and cyclic stresses fatigue. The failed pressure switch was replaced and the HPCI system was tested successfully. Additionally, a similar service pressure switch will be replaced. A review of HPCI and reactor core isolation cooling (RCIC) turbine lube oil system components will be performed to determine if any additional components are potentially susceptible to failure as a result of historical exposure to oil with high moisture content.
3522013002 | Limerick 1, Limerick 2 | 08/05/2013 | 10/04/2013 | ML13277A60 | <strong>Condition That Could Have Prevented Fulfillment of the Offsite Power Safety Function</strong><br /><i>Abstract:&nbsp;</i>The quarterly 201-D23 4.16 kV Emergency Bus Undervoltage (Degraded Voltage) relay functional test could not be completed within the 1-hour Technical Specification (TS) 3.3.3 allowed outage time (AOT) due to an out of calibration undervoltage relay reset setpoint. As a result, the 201-D23 offsite source breaker was racked out to satisfy the TS 1-hour action. The 101-D23 offsite source was already inoperable due to planned monthly emergency diesel generator (EDG) testing which caused both offsite sources to be concurrently inoperable. The cause of the undervoltage relay inoperability was setpoint drift. The inoperable relay was recalibrated during the test. The affected EDG operating procedures will be revised to add specific guidance to place the 101 or 201 safeguard transformer tap changer to auto if undervoltage testing will be performed in conjunction with the diesel generator being run in parallel with the offsite source.
3532013001 | Limerick 2 | 04/16/2013 | 06/12/2013 | ML13163A35 | <strong>Valid Manual Actuation of the Reactor Protection System During Refuel Outage Testing</strong><br /><i>Abstract:&nbsp;</i>A valid manual actuation of the reactor protection system (RPS) occurred during a refueling outage with all control rods inserted. The manual actuation of the RPS system was initiated when the mode switch was placed in the "Shutdown" position following an automatic actuation of RPS. The event was initiated by an unplanned automatic actuation of the turbine stop valve closed trip logic during an RPS surveillance test. The automatic RPS system actuation was caused by a failure to follow the existing procedure change processes. A corrective action was completed which reinforced the requirements for partial procedure use and temporary procedure changes. The corrective action also established expectations for the review and approval of partial procedures and temporary procedure changes.
3532013002 | Limerick 2 | 09/03/2013 | 10/31/2013 | ML13305A12 | <strong>Inoperable Reactor Enclosure Secondary Containment Integrity due to Open Airlock</strong><br /><i>Abstract:&nbsp;</i>Both airlock doors were opened simultaneously when moving equipment through a reactor enclosure airlock causing an unplanned inoperability of reactor enclosure secondary containment integrity. This event was caused by a non-functional airlock door open indicating light not providing the correct door status. The nonfunctional door open indicating light magnetic switch has been replaced. A review was conducted and no other non-functional door open indicating lights were identified. A periodic routine test of the airlock door open indicating lights will be implemented to identify non-functional door open indicating lights.
3532013003 | Limerick 2 | 10/30/2013 | 12/26/2013 | ML14007A14 | <strong>Inoperable Reactor Enclosure Secondary Containment integrity Due to Open Airlock</strong><br /><i>Abstract:&nbsp;</i>A worker in the reactor enclosure was using the equipment airlock when a simultaneous opening of both airlock doors occurred. The breach occurred when the outboard door was opened with the inboard door not properly latched. Both doors were closed in less than 10 seconds and the breach of secondary containment was terminated. The cause of the airlock breach is the reactor enclosure airlock design does not prevent both doors from being opened simultaneously. A contributing cause was the airlock door self-closing feature failed to fully close and latch the airlock door and the worker did not properly verify the door was latched following use. The airlock door self-closing feature was verified to be working properly but may require assistance to fully latch. A reactor enclosure airlock design change will be evaluated.
3542013001 | Hope Creek | 04/08/2013 | 06/05/2013 | ML13161A15 | <strong>High Pressure Coolant Injection System Inoperable due to Control Relay Failure</strong><br /><i>Abstract:&nbsp;</i>At 11:15 a.m., on April 8, 2013, the High Pressure Coolant Injection (HPCI) system was declared INOPERABLE during the performance of HC.IC-FT.BJ-0007 "Logic System Function Test - Containment High Pressure/Low Water Level/Reactor High Water Level HPCI Actuation." During the test, l&C technicians inserted a reactor low water level initiation (Level 2) signal to initiate a start of the HPCI Auxiliary Oil Pump (10-P-213). The operator noted that the HPCI Stop Valve (FV-4880) did not open as expected and observed that the HPCI Auxiliary Oil Pump (HCPI AOP) failed to start. Upon recognizing the HPCI AOP failure to start, the Shift Manager declared the HPCI system INOPERABLE.<br><br> Troubleshooting identified that the HPCI AOP control relay (1BJYY-K056-E41A), a normally de-energized relay, had failed. The relay was replaced and the HPCI AOP start signal was successfully retested. Upon completion of the functional test at 6:18 p.m., the Shift Manager declared the HPCI system OPERABLE.<br><br> The cause of the relay failure was age-related. The failure analysis reported that the relay coil had electrically opened. There was no indication of stress or fatigue of the wire.<br><br> This condition is reportable under 10 CFR 50.73(a)(2)(v)(D) for a condition that could have prevented fulfillment of a safety function of structures or systems that are needed to mitigate the consequences of an accident.
3542013002 | Hope Creek | 06/12/2013 | 10/12/2013 | ML13288A14 | <strong>Reactor Scram due to Degrading Condenser Vacuum</strong><br /><i>Abstract:&nbsp;</i>On June 12, 2013, at 13:33, Hope Creek Unit 1 was manually scrammed from approximately 100 percent rated thermal power due to degrading main condenser vacuum. This condition occurred due to the trip of the 'B' circulating water (CW) pump with the 'B' CW discharge valve stuck in the full-open position. Operators initiated a manual scram when condenser vacuum reached 6.5 inches of mercury absolute (HgA). During the scram response, the operating reactor feed pump tripped due to degrading vacuum and the operators manually placed the reactor core isolation cooling (RCIC) system in service for reactor inventory control. Operators completed the scram response procedures and placed the plant in a stabilized hot shutdown condition. <br /><br /> Immediate corrective actions included replacing the 'B' CW discharge valve and replacing the auxiliary relay card for the 'B' CW pump trip during the forced outage. Additional corrective actions include establishing a program for performing failure analysis, "metallic whisker" evaluations, and trending of circuit card failures in accordance with IN PO and EPRI recommendations, and establishing a preventative maintenance program for replacement of the Bailey auxiliary relay cards. <br /><br /> The cause of the 'B' CW pump trip was due to conductive filament growth that bridged across two solder traces on the auxiliary relay card, creating a short circuit, and generating a CW pump trip signal. <br /><br /> This event is reportable in accordance with 10 CFR 50.73(a)(2)(iv)(A) as a valid manual actuation of the reactor protection system and manual initiation of the RCIC system.
3542013003 | Hope Creek | 06/13/2013 | 09/06/2013 | ML13252A16 | <strong>Through-wall Flaw Discovered on RHR Shutdown Cooling Return Vent Line</strong><br /><i>Abstract:&nbsp;</i>On June 13, 2013, Hope Creek Unit 1 was in Operational Condition (OPCON) 3 following a scram that occurred on June 12, 2013. At approximately 02:52 EDT, during the initial drywell walk down, operators observed water leaking from the `B' Residual Heat Removal (RHR) Shutdown Cooling Return Vent Line. The source of the leak was identified as a through-wall flaw at the pipe/weld interface on the upstream side of the `B' RHR vent line outboard isolation valve (BC-V597), which is inside the reactor coolant system pressure boundary. The estimated leakage rate through the through-wall flaw was determined to be less than one gallon per minute. The RHR vent line is 1" ASME Class 1 piping. <br /><br /> Corrective actions included replacing the vent line, including both inboard (BC-V589) and outboard (BC-V597) isolation valves, during the forced outage. <br /><br /> The cause of the leak was determined to be a human performance deficiency in completion of work in the drywell. A failure analysis performed by an external vendor indicated that the through-wall flaw was caused by grinding. <br /><br /> This condition is reportable under 10 CFR 50.73(a)(2)(ii)(A) for a condition that resulted in a principal safety barrier being seriously degraded. Based on the visual inspection performed during the drywell walkdown, the leak existed during plant operation. The Technical Specification limits Reactor Coolant System pressure boundary leakage to zero; therefore, this condition is also reportable under 10 CFR 50.73(a)(2)(i)(B) for a Condition Prohibited by Technical Specifications.
3542013004 | Hope Creek | 10/15/2013 | 12/10/2013 | ML13345A10 | <strong>Operations with a Potential to Drain the Reactor Vessel (OPDRV) without Secondary Containment</strong><br /><i>Abstract:&nbsp;</i>On October 15, October 20, and October 23, 2013, with Hope Creek Generating Station (HCGS) in a planned refueling outage and the reactor cavity flooded up in OPCON 5, HCGS performed operations with a potential to drain the reactor vessel (OPDRV) without an operable secondary containment. These operations are prohibited by Technical Specification (TS) 3.6.4.1; however, recent NRC guidance provided in Enforcement Guidance Memorandum (EGM) 11-003, Revision 1, allowed the implementation of interim actions as an alternative to full compliance. These actions were compiled in a plant procedure for the OPDRV activities performed at HCGS during Refueling Outage (H1R18) in October 2013.<br /><br /> These OPDRV activities were planned activities that were completed under the guidance of plant procedures and confirmed to have low safety significance based on the interim actions taken. Since these actions were deliberate, no cause determination was necessary. Consistent with the guidance provided in EGM 11-003, Revision 1, HCGS will submit a license amendment request to adopt a Technical Specifications Task Force (TSTF) traveler associated with generic resolution of this issue within four months after the issuance of the Notice of Availability of the TSTF traveler.<br /><br /> These conditions are being reported in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by TS.
3542013005 | Hope Creek | 10/18/2013 | 12/17/2013 | ML13352A35 | <strong>Low-Low Set Safety/Relief Valve Pilot Solenoid Operated Valve Failed As-Found Testing</strong><br /><i>Abstract:&nbsp;</i>On October 18, 2013, Hope Creek Generating Station (HCGS) was notified by NWS Technologies that the solenoid operated valve (SOV) (S/N 481) associated with the pilot valve assembly for safety relief valve (SRV) 1ABHV-F013P (SRV-P) failed its required 'as-found' functional and air-leakage testing. The SOV failure affected the operability of the relief valve function and the low-low set function of SRV-P required by Technical Specification (TS) 3.4.2.2. The SOV was sent to an external vendor for failure analysis. On December 12, 2013, HCGS received the results of the failure analysis confirming that the SOV failure occurred at some point during the operating cycle. Technical Specification 3.4.2.2 requires the relief valve function and the low-low set function for the SRV-H and SRV-P to be OPERABLE in Operational Condition 1, 2, and 3. With one SRV inoperable, the TS action requires that the valve be restored to operable within 14 days or be in Hot Shutdown within the next 12 hours and in Cold Shutdown in the following 24 hours. Therefore, the SRV-P was inoperable for a period longer than the TS allowed outage time. This condition is reportable in accordance with 10 CFR 50.73(a)(2)(i)(B) as an operation or condition which was prohibited by the plant's Technical Specifications.<br /><br /> The cause of the SOV's failure was determined to be a manufacturer's assembly error. The anti-rotation pin that secures the adjustable plunger in place was not installed. Without the pin, the plunger was allowed to rotate and unthread until contacting the internal stop, which prevented the solenoid from picking up when energized.<br /><br /> Corrective actions included replacing the failed single SOV.
3542013006 | Hope Creek | 10/31/2013 | 12/24/2013 | ML13360A06 | <strong>Operations with a Potential to Drain the Reactor Vessel (OPDRV) without Secondary Containment Operable</strong><br /><i>Abstract:&nbsp;</i>On October 31, 2013, at approximately 09:30, during a refueling outage, the Reactor Water Cleanup (RWCU) system was placed in letdown to radwaste to control reactor pressure vessel (RPV) inventory. Because the automatic isolation function was not available for either valve in the drain-down path, the guidance in Enforcement Guidance Memorandum (EGM) 11-003, Revision 1 could not be utilized. EGM 11-003, Revision 1 states: "The addition and removal of small volumes of water inventory from the RPV, for example control rod drive cooling water, is considered steady-state water level control and not an OPDRV provided the instrumentation and valves for automatic isolation of the drain-down path remain available." This placed the plant in an operation with the potential to drain the reactor vessel (OPDRV). Technical Specification 3.6.5.1 requires secondary containment to be set if the plant is in an OPDRV. Secondary containment was not set; therefore, the plant was in a condition prohibited by Technical Specifications.<br /><br /> The Shift Manager identified the condition at 16:31. The condition was corrected at 17:21 by placing an inoperable level channel in a tripped condition, which restored the instrumentation and valve for automatic isolation of the drain path.<br /><br /> This event is reportable in accordance with 10 CFR 50.73(a)(2)(i)(B) as an operation or condition which was prohibited by the plant's Technical Specifications.
3542013007 | Hope Creek | 11/22/2013 | 01/16/2014 | ML14017A02 | <strong>As-Found Values for Safety Relief Valve Lift Set Points Exceed Technical Specification Allowable Limit</strong><br /><i>Abstract:&nbsp;</i>On November 22, 2013, Hope Creek Generating Station (HCGS) received results of the 'as-found' setpoint testing for the safety relief valve (SRV) pilot stage assemblies. The results indicated that five SRV pilot stage assemblies' setpoints had exceeded the lift settings prescribed in the Limiting Condition for Operation (LCO) for Technical Specification (TS) 3.4.2.1. The TS LCO requires the SRV lift settings to be within +/- 3% of the nominal setpoint value. All five of the valves failing to meet the limits were Target Rock Model 7567F two-stage SRVs. During the eighteenth refueling outage (H1R18), all 14 SRV pilot stage assemblies were removed and tested at an offsite test facility. A total of five of the 14 SRV pilot stage assemblies experienced setpoint drift outside of the TS 3.4.2.1 specified values. This is a condition reportable under 10 CFR 50.73(a)(2)(i)(B) as an Operation or Condition Prohibited by Technical Specifications.<br /><br /> The cause of the setpoint drift for the five SRV pilot stage assemblies is attributed to corrosion bonding between the pilot disc and seating surfaces, which is consistent with industry experience. This conclusion is based on previous cause evaluations and the repetitive nature of this condition at HCGS and within the BWR industry.<br /><br /> There was no actual safety consequence associated with this event.
3542013008 | Hope Creek | 12/01/2013 | 04/02/2014 | ML14092A21 | <strong>Automatic Actuation of the Reactor Protection System due to a Main Turbine Trip</strong><br /><i>Abstract:&nbsp;</i>On December 1, 2013, at 06:13 EST, Hope Creek Unit 1 automatically scrammed from 100 percent rated thermal power due to a main turbine trip. The main turbine trip was due to high level in the 'A' moisture separator (MS). As a result of the scram, both reactor recirculation pumps tripped and three safety relief valves opened. The plant was stabilized in hot shutdown Operational Condition 3.<br /><br /> The MS normal level controller failed due to a ruptured bellows causing the MS drain valves to close. The MS dump valve controller attempted to maintain MS level and cycled the dump valve as required. After multiple cycles, the dump valve failed in the closed position. This caused the MS level to increase above the main turbine trip setpoint, resulting in the main turbine trip and the subsequent automatic reactor scram.<br /><br /> A root cause evaluation determined the cause of the MS dump valve failure was thermal binding.<br /><br /> The MS drain and dump valve controllers were replaced, calibrated, and functionally tested. The root cause evaluation performed after a second scram on high MS level on December 5, 2013, determined that the MS dump valve clearances need to be modified to prevent thermal binding.<br /><br /> This is an event reportable under 10 CFR 50.73(a)(2)(iv)(A) as an event that resulted in actuation of the reactor protection system.
3542013009 | Hope Creek | 12/05/2013 | 04/04/2014 | ML14094A11 | <strong>Automatic Actuation of the Reactor Protection System due to a Main Turbine Trip</strong><br /><i>Abstract:&nbsp;</i>On December 5, 2013, at 03:25 EST, Hope Creek Unit 1 automatically scrammed from approximately 75 percent rated thermal power due to a main turbine trip that was caused by a high level in the 'A' moisture separator (MS). The MS high level control loop was in the process of being tuned when the dump valve cycled repeatedly and subsequently failed closed. The main turbine trip automatic reactor scram resulted in a trip of both reactor recirculation pumps. The plant was stabilized in hot shutdown Operational Condition 3. During the recovery of the recirculation pumps, the digital electro-hydraulic control system was mis-operated which caused the turbine bypass valves to cycle. This caused reactor level to swell above Level 8 then shrink below Level 3 resulting in a second actuation of the reactor protection system.<br /><br /> A root cause evaluation determined the cause of the MS dump valve failure was thermal binding.<br /><br /> MS dump valve control has been modified from a modulating function to a full open function on high level to prevent valve cycling. The root cause determined that the MS dump valve clearances need to be modified to prevent thermal binding.<br /><br /> This is an event reportable under 10 CFR 50.73(a)(2)(iv)(A) as an event that resulted in an automatic actuation of the reactor protection system.
3542013010 | Hope Creek | 12/20/2013 | 03/14/2014 | ML14073A56 | <strong>Loss of Both Control Room Chillers</strong><br /><i>Abstract:&nbsp;</i>On 12/20/13 at 1303, while th Control Room Chiller was out of service in support of maitenance, the A Control Room Chiller was manually secured due to excessive fluctuations in load. The Technical Specification action statement (TS 3.7.2.2 Action a.2) for both Control Room Air Conditioning subsystems inoperable was entered. <br /><br /> Concurrent inoperability of both control room chillers is reportable per 50.73(a)(2)(v)(D), an event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident . <br /><br /> At 2120 on 12/20/13 the B Control Area Ventilation Train and Chiller were placed in service for post maintenance testing, returned to an operable status , and the action statement was exited. Throughout the time both chillers were inoperable, the control room temperature was maintained below the TS limit of 90 degrees F. <br /><br /> The A Control Room Chiller excessive load fluctuations were determined to be the result of an inoperable chiller condenser pressure control valve. The valve inoperability was due to an age-related positioner component failure caused by a legacy issue with implementation of a design change. The failed positioner was replaced and the A Control Area Ventilation Train and Chiller were returned to operable status.
3542013011 | Hope Creek | 06/10/2013 | 03/25/2015 | ML15084A11 | <strong>Filtration, Recirculation, and Ventilation System Exceeded Technical Specification Allowed Outage Time</strong><br /><i>Abstract:&nbsp;</i>A review of plant conditions from June 2013, revealed two instances of an operation or condition that was prohibited by Technical Specifications. The reportable conditions were the result of improper operability assessment when the B Filtration, Recirculation and Ventilation System (FRVS) recirculation unit failed to start on a manual start demand on 6/24/13. As a result, two instances of Tech Spec non-compliance were identified. The first occurred on 6/10/13, and the second on 6/17/13. This was discovered during a review conducted in February 2015. In addition, routine Emergency Diesel Generator (EDG) activities created a condition that could have prevented the fulfillment of a safety function due to the failure to recognize the B FRVS recirculation unit inoperability.<br /><br /> The conditions were determined to be reportable per 10 CFR 50.73(a)(2)(i)(B) as any operation or condition prohibited by Technical Specifications and per 10 CFR 50.73(a)(2)(v)(D) as an event or condition that could have prevented fulfillment of a safety function to mitigate the consequences of an accident.
3622013001 | San Onofre 3 | 11/27/2012 | 01/25/2013 | ML13028A47 | <strong>Emergency Diesel Generator (EDG) Governor Actuator Hydraulic Fluid Contamination</strong><br /><i>Abstract:&nbsp;</i>On October 23, 2012, during engineering walkdowns, the hydraulic fluid in the level sight glass of the San Onofre Nuclear Generating Station (SONGS) Unit 3 Train A Emergency Diesel Generator (EDG) governor actuator was found with an abnormal color (purple) and higher than normal indicated level. On November 27, 2012, during subsequent investigation, additional reliable and substantive information including physical evidence was identified that supported a reason to believe (at that time) that tampering may have caused the abnormal condition. This event was reported as a one-hour notification to the NRC in accordance with 10 CFR 73, Appendix G, 1(a)(3). Subsequently, while tampering could not be confirmed, it also could not definitively be ruled out as a possible cause. As such, this followup 60-day written report is being submitted. This event did not affect plant operation or safety, since the EDG was out of service and not required to be operable during the period of time the governor actuator hydraulic fluid was contaminated. Unit 3 has been shutdown since January 31, 2012, due to an unrelated event.
3642013001 | Farley 2 | 05/29/2013 | 09/13/2013 | ML13259A03 | <strong>2C Steam Generator Flow Transmitter Inoperable Longer Than Allowed by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On May 29, 2013, with Unit 2 operating in Mode 1 at 100% power, Engineering personnel performing a review of Unit 2 beginning-of-cycle power ascension data identified that 2C Steam Generator Steam Flow Transmitter FT-494 did not meet Technical Specification calibration accuracy requirements. Based on this information the steam flow instrument was declared inoperable and the required actions of the appropriate Technical Specification were performed. However, since the data utilized in the engineering review was obtained on May 14, 2013, it is known that FT-494 has been inoperable since May 14, 2013. Consequently, the time limits of the applicable Technical Specification required action were not met. This represents a condition prohibited by Technical Specifications and is reportable under 10CFR50.73(a)(2)(i)(B). Steam flow transmitter FT-494 was re-calibrated and returned to service on June 1, 2013. This out-oftolerance condition of FT-494 also occurred at the beginning of the previous fuel cycle. This supplemental report contains causal analysis and corrective action information that was not available for the original report.
3662013001 | Hatch 2 | 02/16/2013 | 04/12/2013 | ML13102A24 | <strong>Unplanned RPS Actuation due to Scram Discharge Volume High Level During Surveillance Test</strong><br /><i>Abstract:&nbsp;</i>On 2/16/2013, at approximately 0310 eastern standard time (EST), Unit 2 was in the refueling mode, when a valid unplanned reactor protection system (RPS) actuation occurred as a result of scram discharge volume (SDV) high level. Following shutdown for refueling the scram vent and drain valves would not open as expected which resulted in water remaining in the SDV. The refueling interlocks surveillance testing was being performed in accordance with the Operations surveillance procedure with the SDV water level above the setpoints for the "rod withdrawal block" and the "scram trip" in conjunction with closed SDV vent and drain valves. Jumpers had been installed to bypass the rod block signal, and the scram signal had been bypassed using the "Disch Vol Hi Level Byp" switch. When the Reactor Mode Switch was placed in the "Start & Hot Standby' position, a full reactor protection system (RPS) actuation occurred. Subsequent investigation revealed that the SDV high level bypass is only active with the mode switch in the "Shutdown" or "Refuel" positions. <br /><br /> The RPS actuation was caused by the presence of a water level in the SDV above the trip setpoint and by a less than adequate procedure. The absence of procedure prerequisites to confirm the SDV Hi Level Rod Block and RPS trip signals were not present prior to performing the refueling interlocks surveillance procedure resulted in positioning the reactor mode switch to the "STARTUP' position with the SDV trip signal present. This caused the SDV high level trip signal to no longer be bypassed resulting in the RPS actuation. The SDV high level condition was cleared and beginning of shift training (BOST) was issued to inform licensed operators of the event. Actions to prevent recurrence involved revision of Units 1 and 2 refueling interlocks surveillance procedures.
3662013002 | Hatch 2 | 02/19/2013 | 04/19/2013 | ML13109A42 | <strong>Performance of Operations with Potential for Draining the Reactor Vessel (OPDRV) without Operable Secondary Containment</strong><br /><i>Abstract:&nbsp;</i>On February 19, 2013, February 20, 2013 and February 25, 2013, OPDRV activities were performed while HNP-2 remained in Mode 5 without an operable secondary containment. These activities are prohibited by Technical Specifications (TS) 3.6.4.1, however recent NRC guidance provided in Regulatory Issue Summary (RIS) 2012-11 and in Enforcement Guidance Memorandum (EGM) 11-003, Revision 1 allowed the implementation of interim actions as an alternative to full compliance. These actions were compiled in an operating procedure for the OPDRV activities performed at HNP-2 during the 2R22 Refueling Outage in February. The OPDRV activities were planned activities that were completed under the guidance of plant procedures and confirmed to have low safety significance based on interim actions taken. Since these actions were deliberate, no cause determination was necessary. A license amendment request will be submitted following NRC approval of the Technical Specifications Task Force (TSTF) traveler associated with generic resolution of this issue.
3662013003 | Hatch 2 | 03/18/2013 | 06/14/2013 | ML13165A26 | <strong>HPCI Declared Inoperable Due to Error in Connecting Tubing to a Hydraulic Actuator</strong><br /><i>Abstract:&nbsp;</i>On March 18, 2013 at 0910 EDT, the Unit 2 High Pressure Coolant Injection (HPCI) system was declared inoperable after the Turbine Control Valve (TCV) did not open as expected during the HPCI Pump Operability 165 psig Test. Unit 2 was in Mode 2 (Startup) and was not in power production at the time of the event. The TCV failed to open because the hydraulic lines between the hydraulic actuator and the remote servo had been interchanged during performance of the 10-year preventive maintenance (PM) procedure in the 2013 refueling outage for Unit 2.<br><br> The lines were properly reconnected, and the HPCI system returned to Operations at approximately 1033 EDT on 3/19/2013. The HPCI operability surveillance was successfully performed at approximately 1056 EDT on 3/19/2013. Additionally, the PM Procedure was revised to include more detailed instructions on the labeling of the hydraulic actuator and remote servo piping prior to removal and to include additional post-maintenance testinc criteria for the hydraulic actuator and remote servo.
3662013004 | Hatch 2, Hatch 1 | 08/13/2013 | 04/01/2014 | ML14094A01 | <strong>Postulated Inter-cable Fault Vulnerability for RHR Shutdown Cooling Isolation Valves During a Postulated Fire Event Results in Unanalyzed Condition</strong><br /><i>Abstract:&nbsp;</i>On 8/13/2013, at 1545 EDT, Unit 2 was operating at 100 percent RTP when it was determined that inter-cable analyses for the safe shutdown analysis had not been done using the guidance of Reg Guide 1.189 and NEI 00-01. An initial analysis for some of the components in the high/low pressure interface systems was performed considering inter-cable shorts as a plausible vector in the Safe Shutdown Analysis. Vulnerabilities were subsequently identified during this circuit analysis, in that postulated fire scenarios can cause two valves required for safe shutdown to open during power operation. At risk are Residual Heat Removal (RHR) valves with controls in Fire Area 2203 (Fire Zone 2203F) and Fire Area 0024. Specifically, during a postulated fire scenario on the affected unit, an inter-cable hot short could occur on the control cables for inboard RHR shutdown cooling isolation valves causing the valves to open while at rated power. In addition, a spurious opening of outboard RHR shutdown cooling isolation valves could occur due to an intra-cable hot short on the control cables in the same postulated event. An intersystem LOCA could then occur when the low pressure system piping is subjected to higher reactor pressures as a result of the postulated conditions.<br /><br /> The cause of the event is attributed to ineffective monitoring and follow-up of regulatory activities involving inter-cable hot shorts in identifying the vulnerabilities associated with these RHR isolation valves. Upon notification, plant operators took actions to de-energize affected valves in the "closed" position to remove the vulnerability.
3662013005 | Hatch 2 | 09/13/2013 | 01/08/2014 | ML14008A41 | <strong>Main Steam Isolation Valve Failed to Close During Surveillance Test</strong><br /><i>Abstract:&nbsp;</i>On September 13, 2013 at 1438 EDT, with the unit in Mode 1 at 100 percent power, the Unit 2 'D' outboard main steam isolation valve (MSIV) failed to move during surveillance testing that involved partial closure testing of the valve. Based on previous operating experience this test result typically indicated a problem with a solenoid used for partial valve closure testing and was not indicative of a problem with the MSIV. A plan was made to cycle the MSIV to the "closed" position and return it to the "open" position during a planned power reduction on September 14, 2013. If the failure was indeed due to the test solenoid, the affected MSIV would function as expected after the power reduction. <br /><br /> At 1105 EDT on September 14, 2013, following power reduction to approximately 65 percent power, the 'D' outboard MSIV failed to close using its control switch. Actions were taken to isolate the MSIV penetration as required by Technical Specifications. Maintenance activities were completed and the MSIV underwent rigorous testing with successful results to confirm the operability of the 'D' outboard MSIV.
3682013001 | Arkansas 2 | 01/02/2013 | 02/21/2013 | ML13053A07 | <strong>A Degraded Plant Protection System Test Switch Results in Invalid System Actuations During Testing</strong><br /><i>Abstract:&nbsp;</i>On January 02, 2013 at 1308 CST, Arkansas Nuclear One Unit-2 (ANO-2) experienced an invalid Safety Injection Actuation Signal (SIAS), Containment Isolation Actuation Signal (CIAS), and Containment Cooling Actuation Signal (CCAS) while technicians were performing Plant Protection System (PPS) matrix testing, resulting in the auto start of the Emergency Diesel Generators, High Pressure Safety Injection (HPSI) Pumps and Low Pressure Safety Injection (LPSI) Pumps in the standby mode, and the re-positioning of numerous safety related components to their actuated state. The operating crew appropriately entered the Abnormal Operating Procedures (AOP) for inadvertent SIAS and inadvertent CIAS. In accordance with the inadvertent SIAS AOP, the operating crew restored Auxiliary Cooling Water flow from the Service Water (SW) System and restored SW flow to the Component Cooling Water (CCW) System by overriding the SIAS to the respective flow path valves. HPSI and LPSI Pumps were placed in pull-to-lock to prevent pump overheating, as procedurally directed. In accordance with the inadvertent CIAS AOP, the operating crew overrode the CIAS to CCW isolation valves to restore CCW flow to the Reactor Coolant Pumps. The SIAS initially aligned boric acid injection into the Reactor Coolant System as designed, and resulted in a reactor power decrease to approximately 87%. The invalid actuation signals were reset and HPSI/LPSI pumps were restored within one hour of actuation. ANO-2 returned to full power operation the same day. A failure modes analysis determined that the direct cause of the event was the degradation of a PPS matrix test switch, with the Root Cause determined to be failure to implement a preventative maintenance strategy for the switch during a 1986 modification.
3682013002 | Arkansas 2, Arkansas 1 | 02/04/2013 | 04/04/2013 | ML13094A09 | <strong>Inoperable Emergency Control Room Chiller due to Maintenance Error Results in a Prevented Safety Function</strong><br /><i>Abstract:&nbsp;</i>On February 4, 2013, at 1255 CST, Control Room Emergency Chiller 2VE-1A breaker tripped shortly after the chiller was started. 2VE-1A is one of two control room emergency chillers common to both Arkansas Nuclear One (ANO) Unit-1 and ANO Unit-2. The 2VE-1A breaker (2B-52D5) is a Siemens 480 volt, 100 amp molded case circuit breaker. An Apparent Cause Evaluation determined that the the “C” phase load side wire lug was not properly connected when the breaker was installed on November 15, 2012, resulting in a loose connection between the lug and the breaker stab. The condition was corrected and 2VE-1A was declared operable on February 6, 2013. The apparent causes of the condition were determined to be a human performance error during breaker replacement due to the inadequate use of human performance tools and an inadequate molded case circuit breaker testing procedure which did not provide a step to perform a visual inspection of the wire grip style lug after installation. Initial corrective actions included a human performance error review and a requirement for visual verification of the wire lugs for remaining breaker replacement work orders. The Apparent Cause Evaluation provided firm evidence that the condition existed since the breaker was incorrectly installed on November 15, 2012, resulting in the inoperability of 2VE-1A. The redundant 2VE-1B Chiller was considered inoperable from November 26, 2012 to December 3, 2012, resulting in the potential inoperability of both control room emergency chillers and a condition that could have prevented the fulfillment of a safety function.
3682013003 | Arkansas 2 | 08/20/2013 | 10/21/2013 | ML13295A07 | <strong>An Inoperable Offsite Power Supply Transformer due to an Inadequate Design Configuration Results in a Condition Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On August 20, 2013, a switchyard walkdown by engineering revealed an undocumented wiring configuration associated with the Arkansas Nuclear One Unit 2 (ANO-2) Startup Transformer 3 (SU3) voltage regulator (VR) circuit. (SU3 is one of two offsite power source transformers designed to supply ANO-2). Subsequent investigation revealed that the wiring configuration would have prevented the SU3 VR from operating as designed. The VR has an automatic tapchanger designed to step up SU3 voltage in response to a low voltage condition after a twenty second time delay to maintain a pre-defined voltage control band. This twenty second time delay is designed to be bypassed for three minutes in the event of a Main Turbine Generator lockout, to allow immediate voltage adjustments as ANO-2 station loads are fast transferred from the Unit Auxiliary Transformer to the offsite SU3 transformer during worst case accident load sequencing. The discovered wiring configuration of the SU3 VR prevented the bypass of the twenty second time delay, resulting in SU3 being declared inoperable. The wiring configuration for the SU3 VR appears to have been introduced in the 2005-2006 time frame, during a switchyard improvement project by Entergy Arkansas Transmission and Distribution, which was responsible for ownership of the subject VR at that time. On August 21, 2013, a temporary modification was installed to remove the SU3 VR tap change controller twenty second time delay, which restored the SU3 operability.
3682013004 | Arkansas 2, Arkansas 1 | 12/09/2013 | 02/05/2014 | ML14037A20 | <strong>Fire and Explosion of the Unit Auxiliary Transformer Resulted in an Automatic Reactor Scram and Initiation of the Emergency Feedwater System</strong><br /><i>Abstract:&nbsp;</i>On December 9, 2013, at approximately 0747 CST, Arkansas Nuclear One, Unit 2 (ANO-2), experienced an electrical fault on the Unit Auxiliary Transformer (2X-02) buses resulting in a fire and catastrophic failure of the transformer. This caused an automatic reactor and main turbine trip, lockout of the Switchyard Auto Transformer, lockout of (ANO-2) Startup 3 Transformer (2X-03) and loss of power to Arkansas Nuclear One, Unit 1 (ANO-1) Startup 1 Transformer (X-03) The switchyard auto transformer supplies one of the two credited offsite sources supplying both Startup 3 Transformer (2X-03) and Arkansas Nuclear One, Unit 1 (ANO-1) Startup 1 Transformer (X-03). A loss of one of the two available offsite power sources for ANO-2 resulted in an auto-start of the ANO-2 Emergency Diesel Generator (2K-4B) to supply ANO-2 safety bus 2A-4 and initiation of the Emergency Feedwater (EFW) System. Investigations determined the most probable cause of the event that led to failure of the Unit Auxiliary Transformer began with a phase-to-ground fault on the 6900V ‘C’ phase non-segregated bus flexible link for 2X-02. Transformer 2X-02 protective relays designed to isolate the bus from an electrical fault actuated, but due to a disconnected lead, the Main Generator Lockout relays failed to actuate leading to 2X-02 failure. A root cause evaluation determined a flexible link for 2X-02 was not properly installed which led to an insulation breakdown at the bolted connection. The subsequent 2X-02 explosion and fire resulted from a non-landed wire due to a human performance error most likely occurring in 1995 that failed to connect the DC conductor to the output contacts for the protective relays.
3692013001 | McGuire 1 | 02/21/2013 | 04/22/2013 | ML14107A10 | <strong>Valid Actuation of Unit 1 Reactor Protection and Auxiliary Feedwater Systems</strong><br /><i>Abstract:&nbsp;</i>On February 21, 2013 Unit 1 tripped (Reactor Protection System actuation) from 100% power as a result of a turbine trip signal initiated after operating main feedwater system (CF) pumps tripped. The CF pumps tripped as a result of the operating Condensate Booster Pumps (CBPs) tripping on emergency low suction pressure following an inadvertent trip of the 1C3 Heater Drain Tank (HDT) Pump. The 1A and Turbine Driven Auxiliary Feedwater System (CA) pumps automatically started (Engineered Safety Feature actuation) as designed following the CF pumps tripping. The 1B CA pump was removed from service prior to the event to support maintenance.<br /><br /> The 1C3 HDT Pump was inadvertently tripped by an operator investigating the cause of an extinguished "on" indicating light bulb which is part of the HDT pump start/stop pushbutton switch. The cause of the HDT pump trip was attributed to an administrative procedure that did not explicitly prohibit intrusive investigation of light bulbs having transient/trip potential. The HDT pump trip caused a secondary system pressure transient that resulted in premature tripping of the CBPs which ultimately led to the reactor trip and CA pump auto-start. The CBP trip was caused by inadequate venting of CBP Suction Header Pressure Switches (PS) and an accumulation of air voids in PS process tubing due to an inadequate slope configuration.<br /><br /> Immediate actions were taken to revise an administrative procedure to prevent intrusive investigation of bulbs having transient/trip potential. The slope of process tubing to the CBP suction header PSs was corrected and the PSs were vented, calibrated, and verified functional. Planned action will be taken to ensure the condensate system (CM) is filled and vented and a hotwell pump is running prior to venting the CBP suction header PSs.
3692013002 | McGuire 1 | 06/13/2013 | 08/12/2013 | ML13234A33 | <strong>Inoperable Auxiliary Feedwater components resulting in Technical Specification prohibited operation or condition.</strong><br /><i>Abstract:&nbsp;</i>During a review of pressure switch (PS) setpoints, it was determined the calibration procedure for Unit 1 Auxiliary Feedwater System PS 1CAPS5390 utilized a water leg value that did not reflect the actual water leg value in the field. This water leg error resulted in a non-conservative 1CAPS5390 actuation setpoint outside the limits required by Technical Specification (TS) 3.3.2, "Engineered Safety Feature Actuation System (ESFAS) Instrumentation", which rendered this PS inoperable. 1CAPS5390 actuates on a Unit 1 Turbine Driven Auxiliary Feedwater Pump (TDCAP) suction pressure - low condition to align the safety related assured water source to this pump. With 1CAPS5390 inoperable, TS 3.3.2 requires the PS be returned to an OPERABLE status within 48 hours or the Unit 1 TDCAP be declared inoperable. Since the inoperable condition with 1CAPS5390 was unknown, the applicable TS Required Actions were not completed within the specified Completion Times. <br /><br /> With this condition, 1CAPS5390 would still have actuated and aligned the safety related assured water source to the Unit 1 TDCAP in time to support the pump's safety function. Therefore, this event was not safety significant. <br /><br /> The cause of this event is weaknesses in the McGuire Nuclear Station (MNS) program for measuring and calculating water leg setpoint corrections. This resulted in the use of an incorrect water leg value for 1CAPS5390. <br /><br /> MNS implemented a modification to correct the 1CAPS5390 setpoint based on actual waterleg value for this PS. The MNS program for determining water legs will be revised to address identified weaknesses. Applicable procedures will be revised.
3692013003 | McGuire 1 | 11/14/2013 | 03/06/2014 | ML14087A00 | <strong>Manual Reactor Trip and Auxiliary Feedwater Start due to Dropped Control Rods</strong><br /><i>Abstract:&nbsp;</i>On November 14, 2013, at 13:13, Unit 1 was manually tripped from 100% power due to 10 dropped control rods associated with Rod Control Power Cabinet 1AC. The remaining control rods fully inserted into the core following the manual reactor trip. Unit 1 was stabilized in Mode 3 at normal operating temperature and pressure. The motor-driven Auxiliary Feedwater Pumps 1A and 1B were manually started for steam generator level control. This event did not impact public health and safety.<br /><br /> The cause of the event was an inadequate modification, resulting in an over-voltage protection (OVP) setpoint too close to the normal output of both the primary and backup -24 VDC rod control power supplies. The design called for the OVP function to be implemented with an installed jumper configuration that set the OVP setpoint too close to the normal output voltage.<br /><br /> Actions were taken to replace other Unit 1 power supplies with available power supplies that will not shut down under similar conditions. Due to limited spares, immediate replacement was limited to all applicable primary supplies and two backup supplies on Unit 1. The remaining backup power supplies installed in Unit 1 and the susceptible Unit 2 power supplies will be replaced as part of the planned corrective actions.
3732013001 | LaSalle 1 | 02/28/2013 | 03/26/2014 | ML14085A46 | <strong>Secondary Containment Inoperable ue to Interlock Doors Open</strong><br /><i>Abstract:&nbsp;</i>On February 28, 2013, Unit 1 was in Mode 1 at 100% power and Unit 2 was in Mode 5 for refueling outage L2R14. At 0400 hours CST, it was reported that both air lock doors on the Unit 1 Reactor Building 710' elevation between the Chemistry Hot Lab and the Reactor Building were open at the same time for approximately 10 seconds. While both interlock doors were open, Technical Specification (TS) Surveillance Requirement (SR) 3.6.4.1.2 ("Verify one secondary containment access door in each access opening is closed") was not met for Unit 1. Secondary containment was declared INOPERABLE for the time that both interlock doors were open. TS 3.6.4.1 Required Action A.1 to restore secondary containment to OPERABLE status within 4 hours was entered and exited for Unit 1 at 0400 CST on February 28, 2013.<br /><br /> The cause of the event was determined to be a less than robust design of the door interlock assembly. Troubleshooting found that the mounting fasteners that secure the entire locking assembly to the frame of door # 226 (Reactor Building side of the interlock) were loose, which prevented the electro-mechanical solenoid operated bolt from properly aligning with the door-mounted catch. This misalignment prevented the bolt from entering the catch on door # 226 when door 225 (Chemistry Hot Lab side) was opened. This malfunction resulted in the capability to open both interlock doors at the same time, and was similar to a previous occurrence on September 18, 2012.<br /><br /> In addition to repairing the interlock assembly, corrective actions include identifying, procuring and installing a more robust design, and creating a periodic preventative maintenance task to inspect, tighten and replace fasteners as necessary.
3732013002 | LaSalle 1, LaSalle 2 | 04/17/2013 | 01/22/2014 | ML14022A06 | <strong>Unusual Event Declared due to Loss of Offsite Power and Dual Unit Reactor Scram</strong><br /><i>Abstract:&nbsp;</i>On April 17, 2013, LaSalle Units 1 and 2 were operating in Mode 1 at 100% power, with a severe thunderstorm in progress. At 1457 hours CDT, lightning struck 138KV Line 0112, resulting in a phase-to-ground fault which subsequently cleared. At 1459 hours, a second phase-to-ground fault on Line 0112 occurred and all 345 KV oil circuit breakers (OCBs) in the main switchyard opened, resulting in a loss of offsite power and reactor scrams on both Units. All emergency diesel generators automatically started and loaded onto their respective busses. All control rods fully inserted, and all systems responded as expected.<br /><br /> An Unusual Event was declared due to a loss of offsite power for greater than 15 minutes. Offsite power was restored to all ESF busses by 2301 hours on April 17, 2013, and the Unusual Event was terminated at 0814 hours on April 18, 2013.<br /><br /> The root cause of the event was determined to be degradation of the 138kV switchyard grounding system that allowed a lightning induced fault to flash over onto the DC protective system. The ground system in the 138kV switchyard was repaired, and corrective actions include improving lightning shielding in the 138kV switchyard.
3732013003 | LaSalle 1 | 04/18/2013 | 06/17/2013 | ML13168A57 | <strong>Low Pressure Core Spray System Declared Inoperable Due to Faulty Control Switch</strong><br /><i>Abstract:&nbsp;</i>On April 18, 2013, at approximately 1325 hours CDT, Unit 1 was in Mode 3 following a loss of offsite power event and dual unit scram the previous day. While attempting to raise Unit 1 reactor water level with the Low Pressure Core Spray (LPCS) system, LPCS injection motor-operated valve 1E21-F005 failed to open when the control switch (1E21A-S002) was held in the "OPEN" position. The LPCS system was declared inoperable but available, and Technical Specification (TS) 3.5.1 Required Action A.1 was entered, requiring that LPCS be restored to operable status within seven days. <br><br> The cause of the event was the failure of the 1 & 1T contact set on General Electric SBM switch 1E21A-S002 due to the buildup of oxidation on the contact surfaces. All other contacts in the switch were found to be working normally. The corrective action was to replace the control switch. A sample of SBM switches will be tested to determine if electrical contact erosion is starting to occur on other switches with similar in-service life installed in similar electrical circuits.
3732013004 | LaSalle 1 | 04/22/2013 | 06/21/2013 | ML13172A40 | <strong>Reactor Pressure Exceeded 150 psig With Reactor Core Isolation Cooling Inoperable</strong><br /><i>Abstract:&nbsp;</i>On April 22, 2013, Unit 1 was in Mode 2, Startup. At approximately 0723 hours CDT, reactor pressure was increased above 150 psig with the Reactor Core Isolation Cooling (RCIC) system isolated and inoperable. Technical Specification (TS) LCO 3.5.3 requires RCIC to be operable in Mode 1, and in Modes 2 and 3 with reactor steam dome pressure greater than 150 psig. TS Required Actions (RA) A.1 and A.2 were entered. <br><br> At approximately 0815 hours, it was recognized that increasing reactor pressure greater than 150 psig with RCIC isolated and inoperable was a violation of TS LCO 3.0.4, which requires that entry into another Mode with an LCO not met shall only be made when the associated actions allow continued operation for an unlimited period of time. This was not the case for TS 3.5.3, and thus TS LCO 3.0.4 was not satisfied. Control rod withdrawals were stopped, and control rod insertion commenced in order to reduce reactor pressure and bring the Unit back into compliance with TS. At 0900 hours RCIC was declared operable, and control rod insertion was stopped. <br><br> The cause of this event was a weakness in Normal Unit Startup procedure LGP-1-1 in that there was no specific procedure step to verify RCIC operability prior to exceeding 150 psig. LGP-1-1 does contain a limitation stating that RCIC operability is required prior to exceeding 150 psig but this would have been more effective if it had been a specific procedural step. In addition, there was a lack of recognition of the impact of TS LCO 3.0.4 by Operations with respect to RCIC operability. Corrective actions include reviewing the event with all licensed operators and revisions to the Normal Unit Startup procedure LGP-1-1.
3732013005 | LaSalle 1 | 04/27/2013 | 06/26/2013 | ML13177A27 | <strong>Technical Specification Required Shutdown due to Pressure Boundary Leakage</strong><br /><i>Abstract:&nbsp;</i>On April 27, 2013, LaSalle Unit 1 was in Mode 2 (Startup) following a forced outage. At 1800 hours CDT, during a walk down of the drywell, a steam leak was observed coming from the Reactor Core Isolation Cooling Steam Supply Inboard Isolation Bypass/Warm up Valve (1E51-F076), a normally-closed, one inch, motor operated valve. The leak was determined to be on the valve bonnet extension-to-bonnet upper seal weld. At 2124 hours CDT the leak was classified as reactor coolant pressure boundary leakage, and Technical Specification (TS) 3.4.5 Condition C was entered. TS 3.4.5 Required Actions C.1 and C.2 require that the unit be in Mode 3 within 12 hours, and Mode 4 within 36 hours.<br><br> Unit 1 entered Mode 4 at 0841 hours on April 28, 2013, as required by TS 3.4.5 to allow for repair of the leak on 1E51-F076.<br><br> The apparent cause was a weld defect or discontinuity from the original weld construction (i.e., manufacturing, installation/construction errors, etc.) of the upper seal weld that propagated through wall as a result of system loading and conditions (i.e., high pressure steam) during normal plant operations. Corrective actions included repair of the defective seal weld area.
3732013006 | LaSalle 1 | 08/13/2013 | 10/14/2013 | ML13288A14 | <strong>Inadvertent Automatic Start of the 1A Diesel Generator Cooling Water Pump Due to Improper Adjustment of Mechanically Operated Contact Switch</strong><br /><i>Abstract:&nbsp;</i>On August 13, 2013, at approximately 1007 hours CDT, technicians were performing a circuit breaker cubicle inspection for the 1C Residual Heat Removal (RHR) pump. While the technicians were cleaning the lower cubicle, the 1A Diesel Generator (DG) cooling water pump automatically started. Investigation determined that the contacts of a mechanically operated contact (MOC) switch in the bottom of the circuit breaker cubicle had momentarily closed during the cleaning. This caused the RHR Pump B/C Cubicle Cooler Fan 1VY03C fan to start, which in turn made up the start logic for the 1A DG cooling water pump. <br /><br /> The cause of the event was maladjustment of the MOC switch linkages, which allowed the contacts of the MOC switch to close from casual contact of the switch linkage during cleaning. Corrective actions included procedure revisions to provide guidance to verify correct adjustment and actuation of MOC switch contacts, and to lift leads or install jumpers as needed prior to performing circuit breaker cubicle inspections.
3732013007 | LaSalle 1, LaSalle 2 | 10/22/2013 | 03/26/2014 | ML14085A46 | <strong>Secondary Containment Inoperable due to Interlock Doors Open</strong><br /><i>Abstract:&nbsp;</i>On October 22, 2013, both Units 1 and 2 were in Mode 1 at 100% power. At 1129 hours CDT, it was reported that both air lock doors on the Unit 1 Reactor Building 710' elevation between the Chemistry Hot Lab and the Reactor Building were open at the same time for approximately 10 seconds. While both interlock doors were open, Technical Specification (TS) Surveillance Requirement (SR) 3.6.4.1.2 ("Verify one secondary containment access door in each access opening is closed") was not met. Secondary containment was declared INOPERABLE for the time that both interlock doors were open. TS 3.6.4.1 Required Action A.1 for both Units 1 and 2 to restore secondary containment to OPERABLE status within 4 hours was entered and exited at 1129 CDT on October 22, 2013.<br /><br /> The cause of the event was a less than robust design of the door interlock assembly. Troubleshooting found that the mounting fasteners that secure the entire locking assembly to the frame of door # 226 (Reactor Building side of the interlock) were loose, which prevented the electro-mechanical solenoid operated bolt from properly aligning with the door-mounted catch. This misalignment prevented the bolt from entering the catch on door # 226 when door # 225 (Chemistry Hot Lab side) was opened. This malfunction resulted in the capability to open both interlock doors at the same time, and was similar to a previous occurrence on February 28, 2013.<br /><br /> Corrective actions from the previous occurrence to identify, procure and install a more robust interlock assembly design were still in progress at the time of the event.
3732013008 | LaSalle 1, LaSalle 2 | 11/22/2013 | 01/21/2014 | ML14034A24 | <strong>Control Room HVAC Inoperable due to Failed Fan Motor</strong><br /><i>Abstract:&nbsp;</i>On November 22, 2013, both Units 1 and 2 were in Mode 1 at 100°/0 power. The 'A' train of Main Control Room ventilation (VC) was inoperable due to an emergent repair of a Freon leak. Technical Specification (TS) 3.7.5 Required Action (RA) A.1 had been entered to restore the control room area ventilation AC subsystem to operable status within 30 days. <br /><br /> At 1920 hours CST, the Main Control Room received an Auxiliary Electrical Equipment Room (AEER) HVAC (VE) Panel Trouble Alarm. The rounds operator responded to the panel and reported that the 'B' AEER Cooler Condenser Pan trip alarm was in, and the fan (OVE03CB) was not turning. An acrid smell was detected coming from the fan motor breaker compartment. The 'B' train of VC and VE was declared inoperable. <br /><br /> With both trains of VC/VE inoperable, the Station entered TS 3.7.5 RA B.1 to verify control room area temperature less than 90 degrees, and RA B.2 to restore one control room area ventilation AC subsystem to operable status within 72 hours. <br /><br /> The cause of the event was a winding failure of the 'B' Auxiliary Electric Equipment Room Cooler Condenser fan motor. Corrective actions included replacing the failed fan motor, and performing a failure analysis to determine the cause of the winding failure.
3742013001 | LaSalle 2 | 04/18/2013 | 06/17/2013 | ML13168A57 | <strong>Pin Hole Leaks Identified in High Pressure Core Spray Piping</strong><br /><i>Abstract:&nbsp;</i>On April 18, 2013, Unit 2 was in Mode 3 following a scram and a loss of offsite power that had occurred on both LaSalle Units the previous day. At 1400 hours CDT, three pin hole through-wall leaks in the U2 High Pressure Core Spray (HPCS) minimum flow line piping were discovered. The leaks were on the outside bend of the first elbow downstream of the minimum flow restricting orifice, and appeared to be leaking a total of approximately 0.5 gpm with the HPCS pump not running. <br><br> Unit 2 HPCS was declared inoperable and, because the HPCS minimum flow line is in direct communication with the suppression pool, primary containment was also declared inoperable. <br><br> The direct cause of the event was a combination of cavitation and mechanical wear/erosion of the piping wall. The apparent cause was procedural inconsistencies that allowed operation of the HPCS system in minimum-flow for extended periods. Corrective actions included replacing the leaking pipe elbow, and performing ultrasonic inspections of susceptible piping on both Units. Also, HPCS operating procedures will be reviewed and revised as required to provide consistent guidance for minimizing operation of HPCS in minimum flow mode.
3742013002 | LaSalle 2 | 04/25/2013 | 06/24/2013 | ML13175A22 | <strong>Manual Reactor Scram following Trip of Circulating Water Pumps</strong><br /><i>Abstract:&nbsp;</i>On April 25, 2013, Unit 2 was in Mode 1 at approximately 56% power. The east condenser waterbox was being dewatered in order to address a condenser tube leak. Waterbox isolation valves 2CW007A and 2CW007C had been closed using their motor operators; however, in order to minimize leak-by, an attempt was made to manually seat the valves. These valves are 144 inch butterfly valves with no internal stops. Outlet isolation valve 2CW007C was seated without incident, but inlet valve 2CW007A was inadvertently moved past its closed position, which allowed flow from the running circulating water pumps to fill the waterbox.<br><br> At 2005 hours CDT, the Main Control Room was informed that a large amount of water was coming from the open waterbox upper manways. An attempt was made to close the manways; however, at 2019 hours, the 2A and 2B circulating water pumps tripped on high condenser pit water level, requiring Unit 2 to be manually scrammed.<br><br> The root causes of the event were determined to be a lack of strict procedural adherence on the part of the operators performing the waterbox dewatering task, and inadequate procedure quality. Corrective actions include coaching in accordance with company policies, and clarifying revisions to the circulating water dewatering procedure.
3742013003 | LaSalle 2 | 12/07/2013 | 02/05/2014 | ML14036A18 | <strong>Average Power Range Monitors Declared Inoperable due to Non-conservative Drift During Load Drop</strong><br /><i>Abstract:&nbsp;</i>On December 7, 2013, Unit 2 was at 60 percent power during a scheduled load reduction for surveillance testing and control rod sequence exchange. At approximately 2355 hours CST, evaluation of data from the core monitoring software system determined that all three Average Power Range Monitor (APRM) channels in the 'A' Reactor Protection System (RPS) trip system were inoperable. Technical Specification (TS) Surveillance Requirement (SR) 3.3.1.1.2 requires that the absolute difference between an APRM channel output and calculated core thermal power not exceed two percent. All three APRM channels in the 'A' RPS trip system were confirmed to read less than the calculated power, which is non-conservative, by more than two percent. <br /><br /> TS 3.3.1.1 requires at least two operable APRM channels per RPS trip system, and at least one APRM channel is required to be operable to maintain the safety function. TS 3.3.1.1 allows delaying entry into the associated Conditions and Required Actions for up to two hours when Functions 2.b and 2.c are inoperable due solely to not meeting the two percent differential limit in the non-conservative direction; therefore, no TS Required Action time clocks were entered. The gains were adjusted for all three APRM channels to return indicated power to within the TS SR limit by 0017 hours CST on December 8, 2013. <br /><br /> The cause of the event was an unexpected degree of APRM indication drift, following planned control rod movement. Corrective actions include training and procedure revisions to minimize the possibility of future occurrences.
3822013001 | Waterford 3 | 01/21/2013 | 03/22/2013 | ML13081A14 | <strong>Main Feedwater Regulating Valve Closure Results in Automatic Reactor Trip</strong><br /><i>Abstract:&nbsp;</i>On January 21, 2013 at 15:51 CST, Waterford 3 experienced an automatic reactor trip from approximately 91% power due to lowering Steam Generator (SG) #1 level following the unexpected closure of Main Feedwater Regulating Valve #1 due to an instrument air line failure. Emergency Feedwater (EFW) Actuation Signals (EFAS-1 and EFAS-2) were received due to low SG levels, which is an anticipated response to the reactor trip with the plant at or near full power. SG #1 received EFW system flow for a short period of time. The plant stabilized in Mode 3 with levels in both SG’s restored to normal operating band with the Main Feedwater (MFW) system. Adequate water level was maintained in the SG’s during the transient to ensure decay heat removal from the Reactor Coolant System (RCS). This condition did not compromise the health and safety of the general public. This condition is reportable pursuant to 10CFR50.73(a)(2)(iv)(A) due to the automatic actuation of the Reactor Protection System (RPS) and due to the automatic actuation of the EFW system.
3822013002 | Waterford 3 | 01/21/2013 | 03/22/2013 | ML13081A43 | <strong>Emergency Feedwater System Flow Control Valve Fails to Close due to Valve Positioner Failure</strong><br /><i>Abstract:&nbsp;</i>On January 21, 2013 at 15:51 CST, Waterford Steam Electric Station, Unit 3 (Waterford 3) experienced a reactor trip from approximately 91% power due to lowering Steam Generator (SG) #1 level. Emergency Feedwater (EFW) Actuation Signals (EFAS-1 and EFAS-2) were received due to low SG levels, which is an anticipated response to the reactor trip with the plant at or near full power. EFW flow to SG 1 was identified to be oscillating from 0 to 800 GPM. While resetting EFAS, EFW flow to SG 1 was approximately 120 GPM without a demand signal. Valve EFW-223A (Emergency Feedwater to SG1 Backup Flow Control Valve) was declared inoperable. Subsequent evaluation determined that EFW-223A past operability was affected by the apparent cause. Plant response to the reactor trip was unaffected by the condition and all design safety function capabilities remained available. This condition did not compromise the health or safety of the general public. The past inoperability of valve EFW-223A is reportable as a Licensee Event Report pursuant to 10CFR50.73(a)(2)(i)(B), Operation or Condition Prohibited by Technical Specifications.
3822013003 | Waterford 3 | 11/16/2012 | 07/22/2013 | ML13204A04 | <strong>Failure to Test Manual Handwheels on Air Operated Valves</strong><br /><i>Abstract:&nbsp;</i>On November 16, 2012 at 03:29 CST, it was identified that periodic testing had not been established for the local manual handwheel function on twenty-four safety related Air Operated Valves (AOV) that are required by design to operate after their associated air supply accumulator is exhausted. Additionally, license basis documents had not been updated to reflect an accumulator mission time. An inadequate evaluation had been performed of the substitution of manual operator action for automatic action by the AOV. Testing revealed that three AOVs would not operate by manual handwheel. There was one inoperable AOV in each of the Emergency Feedwater (EFW) flow paths to the Steam Generators, which made both EFW trains inoperable. There was an inoperable AOV manual override in the Auxiliary Component Cooling Water System, which made and the Train B Ultimate Heat Sink (UHS) inoperable. Since testing of the three AOV’s handwheels had not been performed, it is indeterminate how long the condition existed; however, the condition had recently existed where both trains of EFW and UHS were required to be OPERABLE. At the time of discovery, Waterford 3 was defueled in a no mode condition and was in compliance with Technical Specification requirements. Actions were completed to restore the three valves’ manual handwheels to an operable status.
3822013004 | Waterford 3 | 04/29/2013 | 09/03/2013 | ML13248A10 | <strong>Tech Spec Violation During Operation in Lower Mode with Reduced Channels of Excore Nuclear Instrumentation</strong><br /><i>Abstract:&nbsp;</i>A review of plant reactor coolant temperature trends from a planned outage shows that on April 29, 2013, reactor coolant temperature was raised from approximately 135 degrees F to approximately 180 degrees F as a planned evolution. On April 30, 2013, RCS temperature was raised from approximately 180 degrees F to approximately 345 degrees F as a planned evolution. Additionally, on April 30, 2013, plant operations involving water additions to the Volume Control Tank were conducted. A review of the Station Log shows that only one ENI log channel was operable during these evolutions. These evolutions were prohibited by the plant's Technical Specifications under these conditions. <br /><br /> TS 3.3.1 Action 4 requires, with only one log power channel operable in Mode 5 or Mode 4, suspending "all operations involving positive reactivity changes," and is clarified by an applicable note which states, "Limited plant cooldown or boron dilution is allowed provided the change is accounted for in the calculated shutdown margin." <br /><br /> Planned corrective action is to revise the TS bases for TS 3.3.1 to emphasize the limitations for usage of the note applicable to Action 4. <br /><br /> The planned heatup and dilution evolutions had no discernable effect on nuclear safety.
3822013005 | Waterford 3 | 05/22/2013 | 11/07/2013 | ML13316A25 | <strong>Emergency Diesel Generator Inoperable due to Room Exhaust Fan Failure</strong><br /><i>Abstract:&nbsp;</i>Waterford 3 declared Emergency Diesel Generator B (EDG-B) inoperable on May 22, 2013 due to inability to maintain room temperature within design limits. Subsequent trouble shooting revealed that the variable pitch room exhaust fan had failed due to separation of the fan hub from the hub sleeve. Examination of recent operating data showed that the first evidence of fan failure had been during a surveillance test the previous month. An apparent cause evaluation determined the probable cause of the failure to be the result of repairs made during a previous (1999) fan motor replacement. These repairs caused additional stresses on the fan hub components which eventually resulted in fan hub separation from the hub sleeve. The EDG-B room exhaust fan was repaired and EDG-B operability was restored on May 26, 2013. Safety significance for the event is characterized as low to moderate. This condition is reportable under the following criteria: 10 CFR 50.73(a)(2)(i)(B), 10 CFR 50.73(a)(2)(ii)(B), and 10 CFR 50.73(a)(2)(v)(D).
3822013006 | Waterford 3 | 09/04/2013 | 10/31/2013 | ML13305B03 | <strong>Failure of Credited Manual Operator for Air Operated Valve Causes Train Past Inoperability</strong><br /><i>Abstract:&nbsp;</i>On September 4, 2013, personnel at Waterford 3 determined that the manual operator for a safety related air operated temperature control valve (ACC-126A) could not perform a full manual closure of the valve. Automatic operation was not affected. Manual closure is credited in safety analysis to preserve wet cooling tower inventory as part of the ultimate heat sink. The causal review determined that the cause, misalignment of the valve disc to the shaft, had occurred during planned maintenance in July of 2012. During this term of past inoperability, required systems and components in the redundant safety train were also inoperable for short periods of time for surveillance and planned maintenance reasons. The valve was repaired, retested successfully, and declared operable on September 5, 2013. There was no impact to nuclear safety due to this condition.<br /><br /> This condition is reportable under 10 CFR 50.73(a)(2)(i)(B) and 10 CFR 50.73(a)(2)(ii)(B).
3822013007 | Waterford 3 | 10/18/2013 | 12/17/2013 | ML13353A13 | <strong>Technical Specification 3.9.7 Violation, Load Over Irradiated Fuel During Dry Fuel Storage Activities</strong><br /><i>Abstract:&nbsp;</i>On October 18, 2013, personnel at Waterford 3 identified that, contrary to Technical Specification (TS) 3.9.7, during dry fuel loading activities in the Fuel Handling Building, with the transfer cask loaded with fuel, a load of over 2000 pounds was placed over the transfer cask with a crane that is not single failure proof. This condition occurred with the irradiated fuel covered with a stainless steel lid, 9.5 inches thick, welded in place covering the fuel.<br /><br /> TS 3.9.7 Limiting Conditions of Operation (LCO) requires loads in excess of 2000 pounds to be prohibited from travel over irradiated fuel assemblies in the Fuel Handling Building, except over assemblies in a transfer cask using a single-failure-proof handling system.<br /><br /> This condition is reportable under 10 CFR 50.73(a)(2)(i)(B) as an operation or condition prohibited by TS.<br /><br /> The procedure governing this activity was changed to require using the single-failure proof handling system of the FHB crane main hook instead of allowing the use of FHB auxiliary hook that is not considered single-failure proof.
3872013001 | Susquehanna 1, Susquehanna 2 | 05/07/2013 | 11/04/2013 | ML13309A63 | <strong>Diesel Generator `B' to Bus `2B' Synchronizing Selector Switch Failure</strong><br /><i>Abstract:&nbsp;</i>On 5/7/2013 at 0053 the control room noted HS-00040B (Emergency Diesel Generator (D/G) 'B' to bus 2B' synchonizing selector switch) failed in the on position during performance of SO-024-001B "Monthly Diesel Generator B Operability Test." Based on the design of the SSES synchronizing selector switch circuitry, with HS-00040B failed in the on position, all other synchronizing selector switches were rendered non-functional. The initial operability determination by the Senior Reactor Operators (SRO) for the failed synchronizing selector switch was that the switch did not have a safety function and that the D/Gs and offsite AC sources were operable. During the operability determination, the assessment of the LCO 3.8.1 Surveillance Requirements (SR) did not identify all of the SRs impacted by the failed selector switch. Therefore it was not recognized that the failed switch caused SRs 3.8.1.8 and 3.8.1.16 associated with Unit 1 LCO 3.8.1 and Unit 2 LCO 3.8.2 to not be met in accordance with SR 3.0.1.<br /><br /> The Direct Cause of the event was a failure of synchonizing selector switch HS-00040B, which failed in the on position during performance of SO-024-001B. The Apparent Cause determined that procedure guidance was not provided that operability of the synchronizing selector switch is required to meet the SR 3.8.1.8 and SR 3.8.1.16 surveillance requirements.<br /><br /> An immediate corrective action was to replace the failed synchronizing selector switch. Additional planned corrective actions include revising the affected surveillance procedures; evaluating the feasibility of synchronizing circuit design changes; and reviewing Operability Determination Training recently provided for effectiveness.<br /><br /> There were no adverse consequences to the health and safety of the public as a result of this event. This event is being reported under 10 CFR 50.73(a)(2)(i)(B) as any operation or condition which was prohibited by the SSES TS.
3872013002 | Susquehanna 1 | 06/07/2013 | 08/01/2013 | ML13214A13 | <strong>Unit 1 Manual Scram due to Failure of the EHC "B" Pressure Setpoint Potentiometer</strong><br /><i>Abstract:&nbsp;</i>At approximately 1203 hours on June 7, 2013, Susquehanna Steam Electric Station Unit 1 was manually scrammed during reactor startup. The pressure setpoint was being adjusted to the normal operating setpoint, from 750 psig to 934 psig, when all turbine bypass valves unexpectedly opened. Reactor Feed Pumps tripped and Main Turbine, High Pressure Coolant Injection (HPCI), and Reactor Core Isolation Cooling (RCIC) received trip signals on the high level setpoint Level 8 (+54 inches) due to the resultant reactor level swell. The reactor operator then inserted a manual scram. All control rods inserted. Reactor water level lowered to approximately -10 inches causing Level 3 (+13 inches) isolations. There were no automatic emergency core cooling system initiations. No steam relief valves opened during the event. All safety systems operated as expected.<br><br> This was reported as a 4-hour report in accordance with 10 CFR 50.72 (b)(2)(iv)(B) and as an 8-hour report in accordance with 10 CFR 50.72 (b)(3)(iv)(A). This event is also reportable as a Licensee Event Report (LER) in accordance with 10 CFR 50.73(a)(2)(iv)(A).<br><br> The apparent cause was failure of the Electro-Hydraulic Control (EHC) "B" pressure setpoint potentiometer due to equipment aging associated with corrosion, oxidation or dust build up on the potentiometer coil and/or wiper. Two causal factors were identified: 1) Less than adequate life cycle management based on delay in the project to replace the EHC system with a digital replacement and 2) Less than adequate periodic maintenance to prevent oxidation and corrosion buildup on the pressure set potentiometer. Key corrective actions planned include: 1) Updating the PM activity to include other motor operated potentiometers in EHC and increasing the frequency to every two years, 2) Replacing the Unit 1 and Unit 2 pressure setpoint motor operated potentiometers during next forced or refuel outage, and 3) continuing with the project to replace the EHC system.<br><br> There were no adverse consequences to the health and safety of the public as a result of this event.
3872013004 | Susquehanna 1, Susquehanna 2 | 10/13/2013 | 12/12/2013 | ML13347B23 | <strong>Loss of Secondary Containment due to Differential Pressure Not Meeting Technical Specification 3.6.4.1</strong><br /><i>Abstract:&nbsp;</i>On October 13, 2013, at 0420 hours, control room operators received an alarm for High/Low Reactor Building Differential Pressure. The Unit 2 Zone II Secondary Containment differential pressure (DP) was at 0 inches water gauge with the exhaust ventilation fans running. Technical Specifications (TS) 3.6.4.1 requires a negative DP of at least - 0.25 inches water gauge. As a result, at 0420 hours, TS LCO 3.6.4.1 was entered for both Unit 1 and 2 due to low Reactor Building DP. The Zone I (Unit 1 Reactor Building) and the Unit 1 / 2 Zone III (Common Refuel Floor Area) ventilation remained in service and stable during the event. Unit 2 Zone II Secondary Containment differential pressure was restored and LCO 3.6.4.1 was exited at 0425 hours.<br /><br /> In accordance with 10 CFR 50.72(b)(3)(v)(C), on October 13, 2013, an 8-hour ENS notification (# 49342) was made to the NRC for an event or condition that at the time of discovery, could have prevented the fulfillment of the safety function of Secondary Containment to control the release of radioactive material. As such, this LER is being submitted in accordance with 10 CFR 50.73(a)(2)(v)(C) for an event or condition that resulted in the loss of a safety function.<br /><br /> The direct cause of the loss of Secondary Containment was due to loss of Reactor Building DP. The apparent cause of the loss of Reactor Building DP is an unexplained decrease in Reactor Building exhaust flow. Monitoring equipment has been installed on the systems' pressure transmitter, pressure controller and solenoid valve. Should a repeat event occur, data needed to determine the cause of the event will be will be captured for evaluation and determination of the cause. This information will be provided in a supplement to this LER.<br /><br /> There were no actual consequences to the health and safety of the public as a result of this event.
3872013005 | Susquehanna 1, Susquehanna 2 | 10/23/2013 | 12/18/2013 | ML13353A47 | <strong>Loss of Secondary Containment</strong><br /><i>Abstract:&nbsp;</i>On October 23, 2013, at 0620 hours, control room operators received an alarm for High/Low Reactor Building Differential Pressure. The Unit 2 Zone II Secondary Containment differential pressure (DP) was at -0.17 inches water gauge. Technical Specifications (TS) 3.6.4.1 requires a DP of at least -0.25 inches water gauge. TS LCO 3.6.4.1 was subsequently entered for both Unit 1 and 2 due to low Reactor Building DP. At 0635 hours on October 23, 2013, the Zone II differential pressure was restored to within TS limits by adjusting the manual outside air supply damper in the closed direction.<br /><br /> In accordance with 10 CFR 50.72(b)(3)(v)(C), on October 23, 2013, an 8-hour ENS notification (# 49465) was made to the NRC for an event or condition that at the time of discovery, could have prevented the fulfillment of the safety function of Secondary Containment to control the release of radioactive material.<br /><br /> The apparent cause of the loss of Zone II Secondary Containment was due to controllers (PDC-17581 Zone 1, PDC-27581 Zone 2, PDC-17501 Unit 1 Zone 3 and PDC-27501 Unit 2 Zone 3) not being periodically checked to ensure that they are operating the ventilation exhaust within the controlling range.<br /><br /> Key corrective actions include: 1) The following controllers have been added to the Operator Rounds: PDC-17581 (Zone 1), PDC-27581 (Zone 2), PDC-17501 (Unit 1, Zone 3) and PDC-27501 (Unit 2, Zone 3). The rounds will ensure the output of each controller is within the range of 10 - 12 psig (Zone 1 and Zone 2) and one of the controllers for Zone 3 needs to be in manual at 100% demand and the other controller needs to be in automatic in the demand range of 60-70%. 2) Evaluate the feasibility of increasing the exhaust fan speed and permanently close the top row of manual supply dampers.<br /><br /> There were no actual consequences to the health and safety of the public as a result of this event.
3872013006 | Susquehanna 1, Susquehanna 2 | 10/31/2013 | 07/30/2014 | ML14212A06 | <strong>Loss of Secondary Containment due to Differential Pressure Not Meeting Technical Specification 3.6.4.1</strong><br /><i>Abstract:&nbsp;</i>On two separate occasions during restoration from a routine transfer of the Reactor Protection System (RPS) power supply, Secondary Containment Zone I differential pressure was lost for a few minutes due to the trip of one of the Unit 1 Reactor Building exhaust fans. As a result of each event, Zone I differential pressure did not meet the criteria (vacuum > 0.25 inch of vacuum water gauge) of Surveillance Requirement (SR) 3.6.4.1.1 and Limiting Condition for Operation (LCO) 3.6.4.1 was entered for both Unit 1 and Unit 2. The Secondary Containment Zone II and the Zone III ventilation remained in service and stable during the events. The tripped exhaust fans were subsequently started, Secondary Containment Zone I differential pressure was restored, and LCO 3.6.4.1 was exited within minutes. In both events, the direct cause of the loss of Secondary Containment Zone I differential pressure was the Zone I exhaust damper did not open enough to provide the required minimum flow prior to the time delay tripping the fan. The apparent cause was determined to be an inadequate assessment of the impacts to procedures based on the recent revision to NUREG-1022. RPS power supply transfers were not considered reportable prior to revision 3 of NUREG-1022. A causal factor was determined to be the procedure for performing the RPS power supply transfer was lacking a method to bypass the low flow condition which resulted in the Zone I exhaust fan trip. Corrective actions include procedure changes to prevent unplanned entry into LCO 3.6.4.1 during routine operations and testing. There were no actual or potential consequences to the health and safety of the public as a result of these events.
3872013007 | Susquehanna 1, Susquehanna 2 | 11/20/2013 | 01/21/2014 | ML14021A09 | <strong>Loss of Secondary Containment due to Drawdown Test Failure</strong><br /><i>Abstract:&nbsp;</i>During initial testing on November 20, 2013 at 2247 hours, Secondary Containment drawdown testing failed to meet acceptance criteria of Technical Specification (TS) Surveillance Requirement (SR) 3.6.4.1.5 due to in-leakage flow rate exceeding the allowable value. The surveillance test was being conducted on a previously untested alignment of the Unit 1 ventilation system. Prior to the test, Limiting Condition for Operation (LCO) 3.6.4.1 was entered for both Unit 1 and Unit 2 at 2247. Following the unsuccessful surveillance test, Secondary Containment was restored to an operable condition by reverting to a previously surveilled alignment of the Unit 1 ventilation system and LCO 3.6.4.1 was exited at 0240 hours on November 21.<br /><br /> During retesting on December 7, 2013, at 0950 hours, SSES Secondary Containment drawdown testing failed to meet acceptance criteria of TS SR 3.6.4.1.5 due to in-leakage flow rate exceeding the allowable value. Prior to the surveillance retest, LCO 3.6.4.1 was entered for both Unit 1 and Unit 2 at 0950. Following the unsuccessful surveillance retest, Secondary Containment was restored to an operable condition by reverting to a previously surveilled alignment of the Unit 1 ventilation system and LCO 3.6.4.1 was exited at 1349 hours.<br /><br /> Per the guidance provided in NUREG-1022, this LER is being submitted in accordance with 10 CFR 50.73(a)(2)(v)(C) for an event or condition that could have prevented fulfillment of a safety function and 10 CFR 50.73(a)(2)(i)(B) for a condition which was prohibited by TSs.<br /><br /> The direct cause of the failed tests was excessive in-leakage through the railroad bay hatch cover, doors, seals, and removable walls. Corrective actions include repairing known air leaks, revising component criticality classifications, and the institution of preventative maintenance activities for affected components. There were no actual consequences to the health and safety of the public as a result of these events.
3872013008 | Susquehanna 1, Susquehanna 2 | 11/27/2013 | 01/23/2014 | ML14023A85 | <strong>Loss of Secondary Containment due to Failed Solenoid Valve in the Reactor Building Zone I Ventilation Exhaust System</strong><br /><i>Abstract:&nbsp;</i>On November 27, 2013, at 1001 hours, Susquehanna Steam Electric Station (SSES) control room operators observed that the Zone I (Unit 1 Reactor Building) Secondary Containment differential pressure (DP) was at -0.04 inches water gauge. Technical Specifications (TS) 3.6.4.1 requires a DP of at least -0.25 inches water gauge. As a result, TS LCO 3.6.4.1 was entered for both Unit 1 and 2 due to low Reactor Building DP. The Zone 11 (Unit 2 Reactor Building) and the Unit 1 / Unit 2 Zone 111 (Common Refuel Floor Area) ventilation remained in service and stable during the event. The Zone 1 DP was restored to within the required band at 1111 hours by placing the standby train exhaust fan (which was out of service for maintenance), in operation and was verified to be stable. TS LCO 3.6.4.1 was subsequently exited at 1131 hours on November 27, 2013. In accordance with 10 CFR 50.72(b)(3)(v)(C), on November 27, 2013, an 8-hour ENS notification (# 49588) was made to the NRC for an event or condition that at the time of discovery, could have prevented the fulfillment of the safety function of Secondary Containment to control the release of radioactive material.<br /><br /> The apparent cause of the failure of Reactor Building exhaust fan discharge damper solenoid valve SV17578B was due to in-service degradation of the lubricant used during the valve manufacturing process. The valve manufacturer (ASCO Services) used a silicon-based lubricant which would migrate to the top of the plunger and become sticky during long periods of being energized. This caused the solenoid plunger to get stuck in the energized position, resulting in the valve porting air.<br /><br /> Key completed corrective action: 1) Solenoid valve SV17578B was replaced with a new ASCO 8320 Solenoid valve. Key planned corrective actions: 1) Replace solenoid valves SV17521B, SV17523B, and SV17588B, and perform a validation autopsy, and 2) Based on the results of the validation autopsy, develop a plan to replace the remaining ASCO 8320 solenoid valves.<br /><br /> There were no actual consequences to the health and safety of the public. This event will not be counted as a Safety System Functional Failure for the NRC performance indicator since no loss of safety function occurred.
3872013009 | Susquehanna 1 | 10/30/2013 | 06/18/2015 | ML15173A31 | <strong>Reactor Protection System Electrical Protection Assembly Logic Card Underfrequency Trip Setpoints Out of Calibration</strong><br /><i>Abstract:&nbsp;</i>During routine surveillance testing on 10/30/2013, the two Reactor Protection System (RPS) Electrical Protection Assemblies (EPA) in the `A' train alternate RPS power supply were found to have underfrequency trip set points outside of the Technical Specification (TS) Allowable Value, thus failing to meet TS Surveillance Requirement (SR) 3.3.8.2.2. The affected EPAs were not in service during the testing, and are only required to be operable when the associated alternate RPS power supply is in service. Upon discovery, the EPAs were successfully calibrated and restored to service. The direct cause of the failed surveillance was determined to be drift of the underfrequency set points in the EPA logic cards. The apparent cause was determined to be that the underfrequency setpoint calculation did not take into consideration the manufacturer's stated setpoint drift and temperature effects. Immediate corrective <br /> action was taken to calibrate the affected EPA logic cards. The setpoint calculation was revised to account for drift and temperature effects and recalibrations were then performed using the revised setpoints. <br /><br /> There were no actual consequences to the health and safety of the public as a result of this event.
3882013001 | Susquehanna 2 | 04/17/2013 | 06/14/2013 | ML13168A37 | <strong>Implementation of Enforcement Guidance Memorandum (EGM) 11-003, Revision 1</strong><br /><i>Abstract:&nbsp;</i>The condition reported by this LER was an expected condition, which was the result of planned activities in support of a routine refueling outage. As described in the LER, the U.S Nuclear Regulatory Commission (NRC) provided enforcement guidance, applicable to boiling water reactor licensees, that allows the reported condition. Although this allowance is provided by the NRC's enforcement guidance, the planned activities are still considered reportable in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by Technical Specifications (TS).<br><br> Between 4/17/2013 and 5/17/2013, Susquehanna performed Operations With the Potential For Draining the Reactor Vessel (OPDRV) activities on Unit 2 while in Mode 5 without an operable secondary containment, as expected and allowed by the enforcement guidance. Although NRC Enforcement Guidance Memorandum (EGM) 11-003, Revision 1 allows the implementation of interim actions as an alternative to full compliance, this condition is still considered a condition prohibited by TS 3.6.4.1. The OPDRV activities were planned activities that were completed under the guidance of plant procedures and are considered to have low safety significance based on interim actions taken. Since these actions were deliberate, no cause determination was necessary. A license amendment request will be submitted following NRC approval of the Technical Specifications Task Force (TSTF) traveler associated with generic resolution of this issue.
3882013002 | Susquehanna 2 | 05/06/2013 | 07/03/2013 | ML13186A05 | <strong>Valve Internal Misalignment Resulting in Multiple Inoperable Main Steam Safety Relief Valves</strong><br /><i>Abstract:&nbsp;</i>During the Susquehanna Unit 2 16th Refueling and Inspection Outage, three (3) Main Steam Safety Relief Valves (SRVs) failed to meet the setpoint criteria of +3/-5% set forth in Technical Specification 3.4.3. The three SRVs actuated at a setpoint less than the -5% criteria during off-site testing. The cause of the lower setpoint actuation is attributed to possible misalignment of the valve internals due to post-installation valve cycling using the actuator assembly. This event was determined to be a Common-Cause Inoperability of Independent Trains or Channels and reportable under 10 CFR 50.73(a)(2)(vii) due to having more than one failure caused by misalignment of the valve internals. In addition this event is also determined to be an Operation or Condition Prohibited by Technical Specifications and reportable under 10 CFR 50.73(a)(2)(i)(B). The SRVs remained functional and would have relieved pressure. There were no actual adverse consequences to the fuel, any plant equipment, or to the health and safety of the public as a result of this event. To correct the condition, the SRVs were replaced with SRVs having a setpoint tolerance of +/- 1 % of nameplate setpoint pressure. The SRVs that failed their setpoint tolerance will be refurbished to have an actuation pressure within +/- 1% of nameplate pressure. Pending a license amendment and In-Service Testing (IST) Relief Request, the procedures for post-installation testing of SRVs will be modified to test the SRVs using an alternative method.
3882013003 | Susquehanna 2 | 09/14/2013 | 11/13/2013 | ML13317B90 | <strong>Unit 2 Manual Reactor Scram due to Loss of Reactor Feedwater Pumps</strong><br /><i>Abstract:&nbsp;</i>On September 14, 2013, at approximately 0330 hours, the SSES Unit 2 reactor was manually scrammed following the loss of all Reactor Feedwater Pumps (RFPS) due to high reactor water level. This occurred while transitioning the feedwater Integrated Control System (ICS) for the 'A' RFP from flow control mode to discharge pressure mode. Reactor water level rose to +54 inches causing a trip of the reactor feedwater pumps. Operations subsequently took the mode switch to shutdown to manually scram the reactor. All control rods inserted. There were no automatic Emergency Core Cooling System initiations. No steam relief valve opened during the event. No containment isolations occurred. All safety systems operated as expected. The Reactor Core Isolation Cooling (RCIC) system was manually initiated for reactor water level control until a RFP was recovered. RCIC was manually shut down once a RFP was restored. This LER is being submitted in accordance with 10 CFR 50.73(a)(2)(iv)(A), for an event or condition that resulted in the manual actuation of the RPS and RCIC system.<br /><br /> Root cause of the event: The overall process for implementation of ICS logic block code changes lacked the required level of process rigor and formality for maintaining digital control systems with the potential to affect reactivity and reactor water level. This challenged the operator's ability to maintain precise control of the plant.<br /><br /> Key planned corrective actions: 1) Develop procedural guidance to implement the HURST software configuration management tool for post-maintenance testing of ICS software changes, and 2) Develop procedural guidance for installing/verifying code changes to the ICS software.<br /><br /> There were no actual consequences to the health and safety of the public as a result of this event.
3882013004 | Susquehanna 2 | 09/15/2013 | 11/13/2013 | ML13317B90 | <strong>Unit 2 RHR Pump Room Flooding</strong><br /><i>Abstract:&nbsp;</i>On 9/15/2013 at approximately 0320 during alignment from 2B Residual Heat Removal System (RHR) Shutdown Cooling (SDC) to standby Low Pressure Coolant Injection (LPCI), a pressure transient (water hammer) event occurred. At approximately 1123, the RHR Loop B Pump Room Flooded alarm annunciated in the Unit 2 Control Room. Operations concurrently entered the Emergency Operating Procedure for Secondary Containment Control and the Off Normal Procedure for Flooding in the Reactor Building. At approximately 1130, it was identified that the Unit 2 RHR Pump B Suction Relief Valve was leaking from a 1 inch diameter pipe and approximately 3 inches of water was in the 2B RHR Pump Room. The Emergency Plan was entered at Unusual Event Emergency Action Level (EAL) OU5 at approximately 1138 due to the RHR room flooding. The Unusual Event was terminated on 9/15/13 at 1555. At approximately 1455 on 09/16/13, Engineering determined the leakage from the 2B RHR Pump Suction Relief Valve caused the Engineered Safety Feature (ESF) leakage to exceed the 2.5 gpm limit which was provided to the NRC during the implementation of Alternate Source Term (AST) submittal. This LER is being submitted in accordance with 10 CFR 50.73(a)(2)(ii)(A) for an event or condition that resulted in the condition of the nuclear power plant, including its principal safety barriers, being seriously degraded.<br /><br /> The cause of the event was less than adequate analysis applied to the review of industry and internal Operating Experience (OE) for similar pressure spike events and the failure to recognize the need to revise Operating Procedures.<br /><br /> The key corrective actions include the revision to the procedure on review and evaluation of Operating Experience to clearly identify the expectations for the review of OE. Also, the development and implementation of a strategy for transitioning from Shutdown Cooling (SDC) to Low Pressure Injection (LPCI) lineup while in MODE 3 that produces acceptable thermal hydraulic results.<br /><br /> There were no actual consequences to the health and safety of the public as a result of this event.
3892013001 | St. Lucie 2 | 05/31/2013 | 12/23/2013 | ML14002A24 | <strong>Unplanned Manual Reactor Trip due to Algae</strong><br /><i>Abstract:&nbsp;</i>On May 31, 2013 at 0712 EDT, St. Lucie Unit 2 was in Mode 1 at 40% reactor power when it was manually scrammed. Unit 2 was scrammed prior to securing the 2A1 Circulating Water Pump (CWP) due to high differential pressure on the debris filter system (DFS) as a result of an algae intrusion. At the time of the trip, the 2A2 Circulating Water Pump had been removed from service for maintenance.<br /><br /> The reactor trip event is reportable pursuant to 10 CFR 50.73(a)(2)(iv)(A) as a manual actuation of reactor protection system (RPS). This event had no significant safety consequence. Given the response of the plant and the actions taken, the health and safety of the public was not affected by this event.<br /><br /> The high differential pressure on the 2A1 DFS was the result of the incorrect installation of a debris backwash valve and internal binding of a flush-water check valve. The bound check valve caused a false low DFS transmitter differential pressure that prevented the DFS strainer from initiating a backwash and masked the problem with the debris backwash valve. To correct the problem, the debris backwash valve was properly reinstalled, and the flushwater check valves associated with the DFS differential pressure transmitter were replaced with a more robust design.
3892013002 | St. Lucie 2 | 06/03/2013 | 07/29/2013 | ML13219A31 | <strong>Failure to Invoke Technical Specification Action Statement for Failed Containment Isolation Valve</strong><br /><i>Abstract:&nbsp;</i>On June 3, 2013 at approximately 2000, Unit 2 was in Mode 1 at 8 percent power. During monthly functional testing on the 2A hydrogen analyzer by Instrumentation and Controls (I&C) personnel, the containment dome sample valve did not close when the selector switch was placed in the "OFF" position. The valve was not recognized as a containment isolation valve (CIV) and consequently the applicable technical specification (TS) action statement to de-energize a downstream isolation valve within 4 hours was not entered. The downstream valve was however, in its normally closed position. Subsequently, the TS action statement was met by de- energizing the downstream valve. <br><br> This event is reportable pursuant to 10 CFR 50.73 (a)(2)(i)(B) as a condition prohibited by Technical Specifications. Since the sample valve is designated as a Class E piping penetration, and is designed to be open during a design basis event, this event had no significant safety impact. An apparent cause evaluation identified that the cause was a human error in evaluating the impact to plant operation caused by the failure of the hydrogen analyzer CIV. Contributing causes included: 1) an inadequate procedure, and 2) ineffective hydrogen analyzer labeling. Corrective actions include: 1) revision of the hydrogen analyzer procedure, 2) relabeling the hydrogen analyzers to clearly demonstrate that the valves on the hydrogen analyzer are CIVs, and 3) operator briefing on lessons learned from the event.
3892013003 | St. Lucie 2 | 06/10/2013 | 08/08/2013 | ML13233A31 | <strong>2A Emergency Diesel Generator Failed to Start</strong><br /><i>Abstract:&nbsp;</i>On June 10, 2013, during the monthly surveillance run of the 2A Emergency Diesel Generator (EDG), the EDG did not start when the local idle start pushbutton was depressed. This was accompanied by Control Room and local alarms. The 2A EDG was subsequently declared inoperable. Troubleshooting revealed an electrical short circuit caused by an uninsulated butt splice which caused a fuse in the EDG control circuit to clear. The butt splice was at a diode and arced across the coil mounting plate for the priming pump contactor. <br /><br /> A previous event that occurred in March 2013 led to the conclusion that this condition unknowingly existed for greater than the allowable Technical Specification action time of 14 days per Technical Specification 3.8.1.1.b and is reportable pursuant to 10 CFR 50.73(a)(2)(i)(B). Had this intermittent failure occurred while the 2B EDG was unavailable during three monthly surveillances, this condition could have prevented the fulfillment of a safety function. Therefore, this event is also reportable pursuant to 10 CFR 50.73(a) (2) (v) (A) & (D).<br /><br /> To correct the problem, the diode with the uninsulated butt-splice was replaced, and the new diode has been insulated. <br /><br /> This event had no effect on the health and safety of the public. During this period the 1A EDG, 1B EDG and station blackout crosstie were available to supply Unit 2 with emergency AC power if required.
3892013004 | St. Lucie 2 | 11/14/2013 | 01/13/2014 | ML14024A60 | <strong>Manual Trip Following Spurious Closure of Main Feedwater Isolation Valve (MFIV) and Lowering of Steam Generator Levels</strong><br /><i>Abstract:&nbsp;</i>On November 14, 2013 Unit 2 was in Mode 1 at 100 percent power when the 2B Steam Generator Train A main feedwater isolation valve (MFIV) HCV-09-2A spuriously stroked closed. This resulted in a manual reactor trip of Unit 2 due to rapidly lowering steam generator water level. The reactor trip was normal and uncomplicated. All safety related systems functioned as designed. There were no automatic safety system actuations as a result of the trip. <br /><br /> The MFIV closure was a result of corrosion of two relays (3Y/671 or 20X/671) located inside the relay box caused by internal water intrusion in the conduits. Immediate corrective actions included replacing the degraded relays and installing internal conduit seals. An immediate extent of condition inspection and replacement resulted in installation of conduit seals and replacement of three degraded relays. <br /><br /> This event is reportable pursuant to 10 CFR 50.73(a)(2)(iv)(A) as a manual actuation of reactor protection system (RPS). All plant systems responded as designed and there was no safety significance associated with this event.
3892013005 | St. Lucie 2 | 12/19/2013 | 02/18/2014 | ML14057A45 | <strong>Unanalyzed Condition Affecting Emergency Diesel Generators</strong><br /><i>Abstract:&nbsp;</i>On December 19, 2013, with St. Lucie Unit 2 in Mode 1 at 100% reactor power, it was identified that the Emergency Diesel Generator (EDG) air-cooled radiators may lose their cooling function during high sustained winds when the wind direction opposes the flow of cooling air through the radiator. This had the potential to lead to a loss of the radiators' ability to cool the diesel engine cooling water system.<br /><br /> The potential for sustained winds to adversely impact the Unit 2 EDG radiator fan performance was not considered in the original plant design.<br /><br /> Temporary wind barriers have been installed as a compensatory measure, and permanent wind deflectors are being installed to direct the radiator fan discharge flow vertically to restore full design qualification of the EDGs.<br /><br /> This licensee event report is being reported in accordance with 10 CFR 50.73 (a) (2) (ii) (B) as an unanalyzed condition. Had these sustained winds been experienced at the EDGs without the currently installed compensatory measures, this condition could have prevented the fulfillment of a safety function. Therefore, this event is also reportable pursuant to 10 CFR 50.73 (a) (2) (v) (A) & (D).<br /><br /> This event had no effect on the health and safety of the public. During this period other sources of emergency AC power were available through the 1A and 1B EDGs.
3902013001 | Watts Bar 1 | 02/06/2013 | 04/08/2013 | ML13101A30 | <strong>Latent Design Input Inconsistencies Adversely Affect Probable Maximum Flood Analysis</strong><br /><i>Abstract:&nbsp;</i>On July 28, 2009, the Tennessee Valley Authority (TVA) identified latent design input inconsistencies in hydrological computer modeling used for probable maximum flood (PMF) calculations. <br /><br /> The root causes of the condition were an organizational behavior which allowed the latent input inconsistencies to go undetected and management failure to provide oversight of the impact of river system changes on the calculated value of the PMF. The corrective actions to prevent recurrence are to procedurally require a Flood Protection Program, develop formal Flood Protection Program Management Implementing Procedure(s) and Design Standards/Guides, create a formal documented risk management process for all engineering products, formalize the elements of engineering technical rigor, and implement an upper tier integrated risk management process. <br /><br /> Upon discovery, TVA implemented both immediate and interim corrective actions to ensure the Fort Loudoun, Cherokee, Tellico and Watts Bar dams would not overtop during an assumed PMF event.`
3902013002 | Watts Bar 1 | 05/03/2013 | 06/27/2013 | ML13182A69 | <strong>Two Trains of Emergency Gas Treatment System Inoperable</strong><br /><i>Abstract:&nbsp;</i>On May 2, 2013 at 0845, B-train Emergency Gas Treatment System (EGTS) was removed from service for planned maintenance and Operations declared Technical Specification (TS) Limiting Condition for Operation (LCO) 3.6.9 not met and entered Condition A for one EGTS train inoperable. On May 3, 2013 at 0111, the Main Control Room was notified that the A-A Auxiliary Air Compressor Air Dryer was not purging due to failure of the Auxiliary Control Air System (ACAS) A-A dryer central timing unit. Operations declared A-train ACAS and supported Technical Specification systems inoperable, including A-train EGTS. <br><br> WBN operations entered LCO 3.0.3 due to the inoperability of two trains of EGTS and began preparations to initiate an orderly shutdown within one hour. Operations initiated actions to restore B-train EGTS to standby in accordance with System Operating Instruction (SOI)-65.02, Emergency Gas Treatment System. At 0155, B-train EGTS was declared operable and the actions of LCO 3.0.3 exited. No action was taken to reduce reactor power while in LCO 3.0.3. <br><br> The A-A Auxiliary Air Compressor Air Dryer central timing unit motor was replaced. The apparent cause of this event was that there were missed opportunities to identify the need for replacement preventive maintenance (PM) for the central timing unit. Change requests have been initiated for periodic replacement of the ACAS dryer central timing unit. Components in other systems which could be subject to the same failure mechanism will be reviewed and PM activities initiated as necessary.
3902013004 | Watts Bar 1 | 06/28/2013 | 10/02/2014 | ML14276A33 | <strong>Plant Trip on 500kV Transmission Line Fault</strong><br /><i>Abstract:&nbsp;</i>On June 28, 2013, an A-phase ground fault occurred on the Roane 500kV transmission line approximately 22 miles from Watts Bar Nuclear Unit 1 (WBN1). Concurrently, WBN1 experienced a reactor trip due to the actuation of the 1A Main Bank Transformer Feeder Differential Relay. The 500kV transmission line fault was caused by a tree that fell onto the A-phase of the transmission line. The tree was cut by a local land owner.<br /><br /> Operations personnel stabilized the plant using the Auxiliary Feedwater (AFW) System and the main steam dump valves. The secondary-side steam generator (SG) atmospheric relief valves, SG power operated relief valves (PORVs) and SG safety valves were not challenged during the transient. The Reactor Coolant System (RCS) responded to the initial plant transient as expected without actuating Pressurizer PORVs or initiating Safety Injection signals.<br /><br /> The cause of the event was determined to be an incorrectly de-terminated current transformer neutral conductor that caused a differential relay imbalance in the summation circuit during the faulted conditions.
3902013005 | Watts Bar 1 | 11/14/2013 | 01/13/2014 | ML14013A31 | <strong>Postulated Fire Induced Failure of Chemical and Volume Control System Centrifugal Charging Pumps</strong><br /><i>Abstract:&nbsp;</i>On November 14, 2013, Watts Bar Nuclear Plant (WBN) discovered an unanalyzed condition where a potential fire induced failure of both Unit 1 Chemical and Volume Control System Centrifugal Charging Pumps (CCPs) could occur due to a fire in the Auxiliary Building. A postulated fire in either of two fire areas in the Auxiliary Building could cause a spurious closure of CCP suction valves from the Volume Control Tank and could disable the control circuit which opens the flow from refueling water storage tank (RWST) suction valves resulting in failure of the available CCP and a loss of RCP seal injection. RCP seal cooling would also be impacted by the loss of both Thermal Barrier Booster Pumps (TBBPs) since their control cables are located in the affected fire areas. The inability to establish the RWST suction path for the CCPs, and loss of TBBPs could lead to RCP seal failure and a small break loss of coolant accident. In addition, existing operator manual action would not have been sufficient to establish RCP seal cooling from charging flow in the event of a fire in the affected fire areas. Therefore, WBN was in an unanalyzed condition that significantly degraded plant safety and this condition could have prevented the fulfillment of a safety function. Immediate action was to establish fire watches to ensure a fire in affected fire areas will not cause a spurious closure of the CCP suction valves.<br /><br /> The cause of this event was inadequate review for fire protection program design changes prior to commercial operation of WBN Unit 1.
3952013001 | Summer 1 | 03/24/2013 | 11/19/2013 | ML13330A01 | <strong>Grid Disturbance Results in an Engineered Safeguard Features Actuation of the "A" EDG</strong><br /><i>Abstract:&nbsp;</i>On 3/24/2013 at 0458, a grid disturbance caused an undervoltage relay actuation on the "A" train 7200 Volt Switchgear Bus and the automatic start of the standby "A" Emergency Diesel Generator (EDG). At the time of the event, the "A" train Switchgear Bus was aligned to its normal offsite 115 kV power source. The grid disturbance was longer in duration than the associated undervoltage relay delay time. However the undervoltage event did not exist long enough to trip open the normal incoming breaker or initiate the Engineered Safety Features Load Sequencer (ESFLS). The EDG came up to the rated frequency and voltage, but the output breaker did not close, which was as expected. At 0520 the EDG was secured and restored to standby. The station was in Mode 5 for a mid cycle outage. All station equipment and all transmission system equipment operated as designed. Corrective actions to minimize the probability of reoccurrence have been added to the station's corrective action program. The event is reportable per 10CFR50.73(a)(2)(iv)(A), and 10CFR50.73(a)(2)(iv)(B)(8).
3952013002 | Summer 1 | 10/31/2012 | 08/28/2014 | ML14245A40 | <strong>Component Cooling System Emergency Makeup Valve Failed to Stroke Open Rendering Train of Component Cooling Inoperable</strong><br /><i>Abstract:&nbsp;</i>On April 22, 2013 the past operability determination identified that valve XVG09627B-CC was inoperable for a period of time greater than allowed by Technical Specification 3.7.3 for the Component Cooling Water System. On October 31, 2012, while performing a surveillance test, the normally closed Component Cooling (CC) System emergency makeup valve (XVG09627B-CC) failed to stroke open. The valve stroked open successfully on a subsequent test and was returned to service. On April 14, 2014, XVG09627B-CC failed to stroke open while performing the same surveillance test. The emergency makeup supply to the CC System is provided by the Service Water (SW) System. The SW System functions in the event of a complete loss of the normal makeup capability provided by the Demineralized Water System or if leakage exceeds the normal makeup capacity. The safety related function of XVG09627B-CC is to open to allow SW from the B Train to makeup to the B train CC system. By failing to open, this valve was unable to perform its design function without additional operator action.<br /><br /> The causes of this event are attributed to a low valve manipulation frequency, added frictional forces and possible spring degradation. XVG09627B-CC has been rebuilt with new closure and trip springs and new packing that has a lower friction resistance. The valve supports were adjusted to enhance the alignment of the operator and the pressure regulator closing force was reduced. The valve was stroke tested satisfactorily after being rebuilt. This report is submitted in accordance with 10CFR50.73(a)(2)(i)(B).
3952013003 | Summer 1 | 06/25/2013 | 08/21/2013 | ML13254A31 | <strong>Trip Setpoint Renders Chiller and Control Room Emergency Filtration Inoperable</strong><br /><i>Abstract:&nbsp;</i>On June 25, 2013 with the plant in Mode 1, the "A" Chiller (XHX0001A) shut down during a fast bus transfer of its 7.2 kV bus power supply due to the tripping of two molded case circuit breakers (MCCBs) located on the "A" Chiller skid. The "A" Chiller was running prior to a planned fast transfer of its 7.2 kV bus power supply from the normal power source (115kV) to the alternate source (230kV). Troubleshooting found both compressor motor MCCBs in the tripped condition. The instantaneous trip calibration of the MCCBs was designed to trip the breakers with an incoming current greater than the nominal value of 2000A, and a current greater than this magnitude was experienced during this event. Trips of the MCCBs require local operator action to restart the chiller. A subsequent restart attempt resulted in both compressor motors not starting. The "A" Chiller has been considered to be inoperable since being placed into service August 5, 2011 due to the inability of the chiller to respond to Engineered Safety Features (ESF) sequencer demand following a grid perturbation similar to the bus voltage transient that occurred with a "fast transfer" scenario. The Chilled Water System is an attendant cooling water system that supports the Control Room Emergency Filtration System (CREFS). VCSNS Technical Specifications (TS) 3.7.6 requires two trains of CREFS to be operable while in Mode one through four. <br /><br /> The MCCBs on the Chiller skid have been adjusted to trip at higher amperage. The instantaneous trip setting for the MCCBs has been changed from 2000A to an instantaneous trip range of 3063A to 3938A.
3952013004 | Summer 1 | 07/30/2013 | 09/30/2013 | ML13275A13 | <strong>Spray System Relief Valve Failure to Lift at Required Setpoint Renders the Reactor Building Spray System Inoperable</strong><br /><i>Abstract:&nbsp;</i>On July 30, 2013 V. C. Summer Nuclear Station (VCSNS) Unit 1 completed a past operability review of a relief valve XVR03026-SP for a Reactor Building Spray (SP) System Containment Isolation Valve XVG03004B-SP that failed to lift at its required setpoint during Refueling Outage (RF) 20 in November 2012. An Apparent Cause Evaluation of this event concluded that the cause was a time based failure. This failure resulted in inoperability for "Er train SP system for a period of time greater than allowed by Technical Specifications. Prior to RF-20, the relief valve was last tested during RF-16 in October 2006. Current operability is not challenged due to satisfactory RF-20 corrective actions and return-toservice surveillance testing. The Preventative Maintenance (PM) frequency was revised from every fourth refueling outage to every other refueling outage. This condition had no notable safety consequences to the public or the plant. This event is reportable under 10 CFR 50.73(a)(2)(i)(B).
3952013005 | Summer 1 | 10/16/2013 | 12/11/2013 | ML13350A01 | <strong>Unfused Direct Current (DC) Ammeter Circuits in Control Room Result in 10CFR50 Appendix R Unanalyzed Condition</strong><br /><i>Abstract:&nbsp;</i>As a result of recent industry operating experience (OE 305419, EN 49411, EN 49419) regarding the impact of unfused Direct Current (DC) ammeter circuits in the Control Room, Virgil C. Summer Nuclear Station (VCSNS) performed a review of ammeter circuitry. On October 16, 2013, the review determined the described condition to be applicable to VCSNS resulting in an unanalyzed condition with respect to 10CFR50 Appendix R analysis requirements. <br /><br /> The wiring design for the ammeters contains a shunt in the current flow from each DC battery or charger. The ammeter wiring attached to the shunt does not contain fuses. It is postulated that a fire could cause one of the ammeter wires to hot short to ground. Concurrently, the fire could cause another DC wire from the opposite polarity on the same battery or the same battery charger to also short to ground. This would cause a ground loop through the unfused ammeter cable. The potential exists that the cable could heat up causing a secondary fire in the ammeter raceway. The secondary fire could adversely affect safe shutdown equipment and potentially cause the loss of the ability to safely shutdown per 10CFR50 Appendix R. <br /><br /> The apparent cause of this event is double short to ground faults of opposite polarity were not considered during the design process of the Battery System. A corrective action has been added to the National Fire Protection Association (NFPA) 805 implementation to provide a permanent solution to address this unanalyzed Appendix R condition. As an interim action, roving fire watches have been established for the affected areas.
3952013006 | Summer 1 | 12/04/2013 | 01/31/2014 | ML14035A22 | <strong>Securing Control Room Ventilation Emergency Recirculation While Associated Radiation Monitor Was Out of Service</strong><br /><i>Abstract:&nbsp;</i>On December 4, 2013, at approximately 1027 EST, 'B' train Control Room (CR) ventilation was in the emergency recirculation mode of operation as required by Technical Specification (TS) 3.3.3.1, Action 29. This Technical Specification action requires that the CR ventilation be in the emergency recirculation mode of operation when the Control Room Supply Air monitor is out of service. <br /><br /> An Instrument and Controls (I&C) technician was calibrating the Control Room Supply Air Atmospheric Radiation Monitor using station procedures. An operator was assisting using the system operating procedure for the Control Building Ventilation System. The (I&C) technician could not complete the test because the relay room recirculation damper position could not be verified. The technician communicated to the operator he needed to back out of the procedure. The operator mistakenly proceeded to a step in the system operating procedure to return the system to normal which resulted in securing Control Room Emergency Ventilation. The Control Room Emergency Ventilation was out of TS Action requirements for approximately 30 seconds, thus violating TS 3.3.3.1, Table 3.3-6 Action 29.
3972013001 | Columbia | 01/07/2013 | 03/08/2013 | ML13079A26 | <strong>Secondary Containment Inoperable due to Both Airlock Doors Being Open</strong><br /><i>Abstract:&nbsp;</i>On January 7, 2013, Columbia was operating at 100% power. At 1427 PST both doors of the 501 elevation airlock entrance of the Reactor Building were simultaneously opened for a short period of time. This was the result of the failure of the interlock between the outer door (R304), and the inner door (R305). Maintenance personnel were moving scaffolding through the Reactor Building outer security door when an equipment operator opened the inner door to exit the Reactor Building. This equipment operator immediately closed the inner door and contacted the Main Control Room. The outer door was key locked closed until corrective actions could be implemented. Having a condition where both doors in a Reactor Building airlock were opened simultaneously while not undergoing a planned evolution for maintenance or surveillance testing, results in an unintended entry into Technical Specification (TS) 3.6.4.1 Secondary Containment due to a failure to satisfy Surveillance Requirement (SR) 3.6.4.1.3. It was determined that this condition resulted in a loss of safety function (Secondary Containment) and was reported to the NRC (Event Notification 48656) at 1629 PST on January 7, 2013.
3972013002 | Columbia | 03/02/2013 | 05/01/2013 | ML13141A28 | <strong>Main Control Room Cooler Failed Surveillance</strong><br /><i>Abstract:&nbsp;</i>In October 2012, it was determined that the Technical Specification (TS) surveillance procedure to verify that each control room air conditioning (AC) subsystem has the capability to remove the assumed heat load for TS Surveillance Requirement (SR) 3.7.4.1 did not satisfy the surveillance requirement. The methodology for the existing surveillance had been in use since 1998 around the time Energy Northwest converted to the Improved Technical Specifications. TS SR 3.0.3 was invoked and a new surveillance procedure was developed. On March 2, 2013, while performing the new surveillance procedure, the test results revealed that the air handler thermal performance for the "A" train did not meet the acceptance criteria. This failure to satisfy SR 3.7.4.1 in March, following entry into SR 3.0.3, is reportable under 10 CFR 50.73(aX2)(i)(B) - Any operation or condition which was prohibited by the plant's technical specifications.<br><br> The control room AC subsystem has been cleaned, retested, and returned to operable status.
3972013003 | Columbia | 06/03/2013 | 08/01/2013 | ML13231A11 | <strong>Operation Prohibited by Technical Specifications due to Valve Leakage</strong><br /><i>Abstract:&nbsp;</i>On June 3, 2013, with Columbia Generating Station in a planned refueling outage and the reactor cavity flooded up (Mode 5), leakage past a closed isolation valve associated with one hydraulic control unit on the control rod drive system was observed through a drain line. This leakage originated from the reactor vessel and constituted an operation with the potential to drain the reactor vessel (OPDRV). When the leakage was initially identified, it was not recognized as an OPDRV. The leakage rate was estimated to be less than 10 gallons per hour. This leakage persisted for 16 hours until the maintenance activities were completed. During this time period, the secondary containment was inoperable. Technical Specifications (TS) require that with secondary containment inoperable during OPDRV activities, action must be initiated immediately to suspend OPDRVs. Contrary to this requirement, action was not taken to suspend the OPDRV. This represents a condition prohibited by TS. The cause of this event was inadequate procedure guidance for actions to take when unexpected OPDRV conditions are encountered. Immediate corrective actions were taken to establish expectations regarding the appropriate actions to take for discovered unplanned OPDRV conditions. This event is not safety significant since the leakage rate was so small that there was no measurable loss of level in the reactor cavity.
3972013004 | Columbia | 06/04/2013 | 10/04/2013 | ML13290A15 | <strong>Jumper makes Suppression Pool Spray Valve Remote Transfer Switch Inoperable</strong><br /><i>Abstract:&nbsp;</i>When performing a logic system functional test (LSFT) of the Remote Shutdown Panel transfer switch during refueling outage R21 on June 4, 2013, the procedure for testing the remote transfer switch for the suppression pool spray valve failed because a jumper had been left installed following a new bucket (breaker) installation at the Motor Control Center during the previous refueling outage R20. A satisfactory LSFT was performed prior to the installation of the new bucket Into the MCC but this LSFT was not re-performed to verify the operability of the new bucket after installation. The problem went undetected until the R21 LSFT test failed. The remote transfer switch was inoperable from May 16, 2011 until June 4, 2013 when the condition was discovered. This resulted in failure to meet Surveillance Requirement (SR) 3,3.3.2.4 and non-compliance with Technical Specifications (TS) Limiting Condition for Operation (LCO) 3.3.3.2.<br /><br /> The preliminary apparent causes have been identified as: (1) a lack of a standard for Work Order instructions involving the removal and installation of Jumpers, resulting in personnel having to rely on experience and skill of the craft for the proper way of executing and documenting required modifications; and (2) Inadequate decision making resulting in the use of a post maintenance testing procedure after the installation of the Spectrum bucket in May 2011 that did not adequately prove operability.
3972013005 | Columbia | 06/15/2013 | 08/12/2013 | ML13234A33 | <strong>Momentary loss of 115kV offsite power</strong><br /><i>Abstract:&nbsp;</i>On 6/15/2013 at 1222 PDT Columbia Generating Station was in a refueling outage in Mode 4 when valid Essential Safety Function (ESF) actuation signals of Division .1 and 2 Emergency Diesel Generators were received due to a momentary loss of 115kV (1 of 2) offsite power sources. In addition valid actuation signals of Division 1 and 2 Essential Service Water System pumps were also received due to the start of Division 1 and 2 Emergency Diesel Generators. The 4.16kV Division 1 and 2 critical switchgear buses were de-energized resulting in load shed of several systems and an invalid actuation of containment isolation valves for multiple systems. Power to the 4.16kV critical switchgear was automatically restored by the Emergency Diesel Generators. <br /><br /> Plant systems which had been load shed were returned to operating status. The 4.16kV critical switchgear buses were subsequently realigned to an offsite power source. <br /><br /> The momentary toss of the 115kV offsite power source was due to relays opening and reclosing to clear a line fault associated with a range fire under the transmission line.
3972013006 | Columbia | 06/27/2013 | 08/20/2013 | ML13254A00 | <strong>Accidental switch bump makes High Pressure Core Spray and Diesel Inoperable</strong><br /><i>Abstract:&nbsp;</i>On June 27, 2013 at 17:58 hours a laborer was exiting the Diesel Generator [DG] 3 Room when he inadvertently brushed against the control switch [JS] for the Diesel Mixed Air fan [FAN] causing it to turn to the OFF position. In response to an annunciator alarm in the main control room, an operations supervisor proceeded to the Diesel Generator 3 Room. After ascertaining what had happened by questioning the laborer, the operator turned the fan control switch back to ON and the switch operated smoothly. The Diesel Mixed Air fan was back in service at 18:19 hours, so the fan was inoperable for approximately 21 minutes. <br /><br /> With the Diesel Mixed Air fan switch in the OFF position, the following supported equipment were declared inoperable and the appropriate Technical Specifications were entered: Diesel Generator 3, High Pressure Core Spray (HPCS) [BJ], Division 3 125 VDC battery charger [BYC], Division 3 battery [BTRY], and the Division 3 AC electrical power distribution system [JX]. <br /><br /> The loss of the HPCS system resulted in the temporary loss of safety function for a single train system. There was no radiological release associated with this event. No safety system actuations or isolations occurred. The licensee notified the NRC Resident Inspector and Event Notification No. 49152 was submitted.
3972013007 | Columbia | 08/25/2013 | 05/29/2014 | ML14160B12 | <strong>Secondary Containment Pressure Exceeded During Severe Weather Conditions</strong><br /><i>Abstract:&nbsp;</i>On August 25, 2013 at 1818 hours secondary containment was declared inoperable during a suddenly occurring thunderstorm. Secondary containment pressure was not maintained greater than or equal to 0.25 inches of vacuum water gauge as required by Technical Specification 3.6.4.1. This condition was experienced for a period of no greater than 160 seconds. Operations took manual control of the system and quickly adjusted Reactor Building Exhaust Air flow to restore secondary containment to less than -0.25 inches water gauge. While Technical Specification limits were exceeded, the resulting pressure excursion was bounded by analytical results, and thus there were no safety consequences for this event. <br /><br /> The cause for the event was determined to be failure of the Reactor Exhaust Air/Reactor Outside Air system to automatically maintain a stabilized negative differential pressure in the Reactor Building at the controller setpoint value of -0.6 inches water gauge due to less than optimal control system tuning for the system. Corrective actions include determining, Implementing, and documenting the optimum control system tuning for the system, increasing margin by lowering differential pressure set point, and alerting operations before the Technical Specification limit for secondary containment pressure is reached.
4002013001 | Harris | 05/15/2013 | 07/12/2013 | ML13193A34 | <strong>Reactor Pressure Vessel Head Penetration Nozzle Indications Attributed to Primary Water Stress Corrosion Cracking</strong><br /><i>Abstract:&nbsp;</i>On May 15, 2013, while at 98% power in Mode 1, HNP commenced a Technical Specification required shut down to Mode 6 to repair a flaw that was identified in nozzle 49 of the reactor pressure vessel head. Nozzle 49 was subsequently repaired on May 31, 2013, utilizing the inside diameter temper bead welding process. In 2012, four nozzles (5, 17, 38, 63) were identified with similar indications that exhibited characteristics of PWSCC, and were subsequently repaired using the inner diameter temper bead welding process. However, nozzle 49 was not identified as having an indication at that time. Because the indication in nozzle 49 was identified while at power, a shut down was required by Technical Specifications. <br><br> The cause of the flaws in nozzle 49 and the other four nozzles was attributed to PWSSC. The root cause evaluation determined that the missed identification of the indication in nozzle 49 was due to the lack of mitigating programmatic governances to specify process independence and fatigue/distraction controls. The planned corrective action to prevent recurrence is to create mitigating programmatic governance for providing oversight for complex automated Non-Destructive Examination (NDE) inspections through the generation of new procedure(s).
4002013002 | Harris | 10/23/2013 | 12/19/2013 | ML13353A62 | <strong>Main Steam Safety Valve Setpoint Drift</strong><br /><i>Abstract:&nbsp;</i>On October 23, 2013, while operating at 100% power in mode 1, two main steam safety valve setpoints were found outside the +/- 1% tolerance of table 3.7-2 of technical specification 3/4.7.1.1. Three other valves were tested and setpoints were found to be within tolerance. Upon discovery of the out of tolerance conditions, the two setpoints were adjusted to within technical specification tolerances which restored compliance with the technical specifications. The cause was determined to be setpoint drift incompatible with analysis specified criteria. The corrective action will be implementation of a revised safety analysis that accommodates increased setpoint drift and supports revised technical specification setpoints. <br /><br /> Main steam safety valves are used to satisfy American Society of Mechanical Engineers code requirements for overpressure protection. The limiting accident analysis has more margin available than the measured deviation from setpoint, so the impact on safety is very minor.
4002013003 | Harris | 11/18/2013 | 01/15/2014 | ML14013A07 | <strong>Reactor Pressure Vessel Head Penetration Nozzle 37 Indication Attributed to Primary Water Stress Corrosion Cracking</strong><br /><i>Abstract:&nbsp;</i>On November 18, 2013, the reactor vessel head penetrations were being examined while the Harris Nuclear Plant was shut down for a scheduled refueling outage. Ultrasonic examinations identified an indication in head penetration nozzle 37. The indication was approximately 0.46 inches long with an axial orientation. An inspection of the exterior surfaces of the reactor head confirmed there was no leakage. Nozzle 37 was repaired utilizing the inside diameter temper bead welding process, which was completed December 2, 2013. The repair restored compliance with the American Society of Mechanical Engineers code requirements.<br /><br /> The cause of the indication in nozzle 37 was attributed to primary water stress corrosion cracking. Per the requirement of 10 CFR 50.55a(g)(6)(ii)(D)(5), examinations are required to be performed on the reactor vessel head every refueling outage to identify flaws and ensure appropriate repairs are performed. This is similar to the conditions reported in Harris Licensee Event Report 2013-001-00.
4002013004 | Harris | 11/11/2013 | 04/10/2014 | ML14100A44 | <strong>Operation Prohibited by Technical Specification due to Exceeding Hydrogen and Oxygen Concentrations in the Waste Gas System</strong><br /><i>Abstract:&nbsp;</i>On November 11, 2013, while in Mode 5, sample results of the 'C' waste gas decay tank (WGDT) were not properly evaluated in which hydrogen results should have been documented as greater than 4 percent and oxygen at 4.03 percent. Due to this condition, it was not recognized that the conditions of Technical Specification (TS) 3.11.2.5 were not met and required immediate suspension of all additions of waste gas to the system, reduction of oxygen to less than or equal to 4 percent by volume, then reduction of oxygen to less than or equal to 2 percent within 48 hours. HNP was in this condition for 30 calendar days until the oxygen concentration in the 'C' WGDT was reduced to below the TS limit on December 11, 2013.<br /><br /> The root cause was determined to be an inadequate understanding of the risks associated with degassing the waste gas system with inoperable analyzers. Corrective actions include revising procedures, training, and reinforcing expectations for procedural use and adherence. This event is considered to have no safety significance as an engineering evaluation determined that this condition did not generate any combination of explosive gases in the system.
4102013001 | Nine Mile Point 2 | 01/23/2013 | 03/25/2013 | ML13091A37 | <strong>Reactor Core Isolation Cooling System Isolation due to a Temperature Switch Unit Failure</strong><br /><i>Abstract:&nbsp;</i>On January 23, 2013 at 15:16, Nine Mile Point Unit 2 was operating at 100 percent power when Reactor Building General Area temperature switch unit 2RHS*TS85A failed, resulting in the closure of primary containment isolation valves and causing the Reactor Core Isolation Cooling (RCIC) system to isolate from the reactor vessel and become inoperable. The failure of the temperature switch unit occurred concurrently with the High-Pressure Core Spray (HPCS) system inoperable for planned surveillance testing. With both the RCIC and HPCS systems inoperable, high pressure makeup capability to the reactor core was lost from these systems. This event is reportable in accordance with 10 CFR 50.73(a)(2)(iv)(A), as an automatic actuation of containment isolation valves in more than one system. The event is also reportable in accordance with 10 CFR 50.73(a)(2)(v), as an event that could have prevented the fulfillment of the safety function of systems that are needed to: (A) shut down the reactor and maintain it in a safe shutdown condition, and (D) mitigate the consequences of an accident. The temperature switch failed due to age-related capacitor degradation. The apparent cause of the event is insufficient use of the corrective action program to fully implement a periodic capacitor replacement program for the Riley temperature switches. Corrective actions include replacement of the failed switch and planned refurbishment of similar units.
4102013002 | Nine Mile Point 2 | 02/28/2013 | 04/25/2013 | ML13122A22 | <strong>Failure of High Pressure Core Spray System Pressure Pump due to Motor Winding Failure</strong><br /><i>Abstract:&nbsp;</i>On February 28, 2013 at 1319, Nine Mile Point Unit 2 was operating at 100 percent power when the High Pressure Core Spray (HPCS) system pressure pump failed. At the time of the failure, the HPCS system was inoperable for planned maintenance. The HPCS system pressure pump failure was due to an electrical short caused by a turn-to-turn failure in the motor.<br><br> The cause of this event was determined to be a turn-to-turn short in the motor winding, attributed to poor manufacturer quality of the original motor.<br><br> Corrective actions include replacement of the failed motor with a rewound motor and development of a new replacement strategy for these types of motors.<br><br> This event is reportable in accordance with 10 CFR 50.73(a)(2)(v)(D), as any event or condition that at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident. This report constitutes a 10 CFR 21 (Part 21) notification because the motor failure that initiated the event is attributed to a manufacturing deficiency.<br><br> There are no previous LERs similar to this event.
4102013003 | Nine Mile Point 2 | 10/22/2013 | 12/20/2013 | ML14008A10 | <strong>Unanalyzed Condition Caused by Unfused Control Room DC Ammeters</strong><br /><i>Abstract:&nbsp;</i>On October 22, 2013 it was discovered that unfused ammeter indication circuits associated with the Nine Mile Point Unit 2 (NMP2) safety-related Direct Current (DC) buses could short circuit due to a fire in the circuit cable routing. This ground fault equivalent hot short could cause the cable to self-heat and lead to secondary fires. The unanalyzed secondary fires could adversely affect safe shutdown equipment and potentially cause the loss of the ability to safely shutdown as required by 10 CFR 50 Appendix R. <br /><br /> This event is reportable in accordance with 10 CFR 50.73(a)(2)(ii)(B) as a condition that resulted in the nuclear plant being in an unanalyzed condition that significantly degraded plant safety, and 10 CFR 50.73(a)(2)(ix)(A) as a condition that as a result of a single cause could have prevented the fulfillment of a safety function for two or more trains or channels in different systems. <br /><br /> The cause of this event is that the equipment design issue was not recognized as an unacceptable configuration. The design issue is associated with an evolving industry understanding of the 10 CFR 50 Appendix R common enclosure scope. <br /><br /> Corrective actions include the isolation of the affected circuits at the DC bus in order to prevent the condition from occurring, and the development, issuance and installation of a plant modification to install fuses on the safety-related DC ammeters at NMP2 to ensure adequate circuit protection to prevent the propagation of fires in additional areas due to overcurrent conditions.
4102013004 | Nine Mile Point 2 | 12/02/2013 | 01/31/2014 | ML14043A09 | <strong>Manual Reactor Protection System Actuation due to Loss of Reactor Recirculation Flow</strong><br /><i>Abstract:&nbsp;</i>On December 2, 2013, at 0903, Nine Mile Point Unit 2 (NMP2) was lowering reactor power level to remove the main turbine from service to support maintenance. During the power reduction, the Low Frequency Motor Generators (LFMGs) did not start automatically. Attempts to manually start the recirculation system pumps in slow speed were unsuccessful and a manual reactor scram was inserted due to the sudden reduction in core flow. <br /><br /> This event is reportable in accordance with 10 CFR 50.73(a)(2)(iv)(A) as a condition that resulted in manual or automatic actuation of any of the systems listed in 10 CFR 50.73(a)(2)(iv)(B). The Reactor Protection System is listed in 10 CFR 50.73(a)(2)(iv)(B). <br /><br /> The root cause of this event is a failure to identify that the switches in the auto transfer circuits for the reactor recirculation pumps to shift from high speed to low speed are single point vulnerable (SPV) components because they were exempted from the AP-913 classification process. Since the switches were not classified as SPV components, no mitigation strategies were developed. <br /><br /> Corrective actions include revision of the operating procedures to manually start the LFMG sets and not rely on the auto transfer circuitry. <br /><br /> There are no similar Licensee Event Reports for NMP2.
4102013005 | Nine Mile Point 2 | 12/11/2013 | 01/31/2014 | ML14049A14 | <strong>Secondary Containment Inoperabilities due to Differential Pressure Not Meeting Technical Specification Surveillance Requirement 3.6.4.1.1</strong><br /><i>Abstract:&nbsp;</i>On December 11, 2013 it was discovered that Nine Mile Point Unit 2 (NMP2) has not been reporting Secondary Containment inoperabilities to the Nuclear Regulatory Commission (NRC) in accordance with the administrative guidance in NUREG-1022 (Revision 3). This condition has occurred numerous times within the past three years when the Secondary Containment has been declared inoperable as a result of the Secondary Containment differential pressure (dP) dropping below the required Technical Specification (TS) minimum value of negative 0.25 inches water gauge. These historical events are reportable in accordance with 10 CFR 50.73(a)(2)(v)(C) as conditions that could have prevented the fulfillment of the safety function of a structure or system needed to control the release of radioactive material. In each of these occurrences the safety function of the Secondary Containment remained available. The apparent cause of these events is that training has not been effective in providing personnel the level of understanding required in order to consistently recognize when the failure of safety systems are reportable under 10 CFR 50.72(b)(3)(v)(C) and 50.73(a)(2)(v)(C). Corrective actions include briefings and detailed training on 10 CFR 50.72(b)(3)(v)(C) and 50.73(a)(2)(v)(C) reporting requirements.
4122013001 | Beaver Valley 2 | 06/24/2013 | 08/23/2013 | ML13239A23 | <strong>Gas Void in Emergency Core Cooling System Pump Suction Header Results in a Condition Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On 6/24/2013, Beaver Valley Power Station (BVPS) Unit No. 2 was at 100 percent power. At 0836 hours, the Control Room was notified of a void in the suction piping of the "A" train High Head Safety Injection (HHSI) pump. During a routine performance of a void monitoring procedure, a void of approximately 0.62 cubic feet was discovered at the suction of the "C" HHSI pump which was aligned to the "K train. The pump was declared inoperable and Technical Specification (TS) LCO 3.5.2, ECCS Operating, was entered. The "B" HHSI pump, aligned to the "B" train, was operable and in service. The "A" HHSI pump was inoperable, due to planned maintenance. Following venting and verification that the suction piping of the "C" HHSI pump was sufficiently full of water, the "A" train of HHSI was declared operable and TS LCO 3.5.2 was exited at 1623 hours on 6/24/2013. It was subsequently determined that the gas void had existed prior to the "C" pump being credited as the stand-by HHSI pump on the "A" train eight days previously. The "C" HHSI pump was inoperable during the eight day time frame. TS LCO 3.5.2, ECCS Operating, requires two trains of ECCS to be operable. As this condition existed for greater than the allowed restoration and shut down completion times of this LCO, a condition prohibited by technical specifications had existed. At no time during this event were both trains of ECCS inoperable simultaneously.<br /><br /> The void source was determined to be from an inadequate fill and vent of the reactor coolant pumps seal return line. The root cause of this event is the minimum flow required to move entrained air through the seal water return piping was not present. The procedure used to fill and vent the seal return lines did not ensure a minimum flow was obtained that would move the entrained air to the vent location. The plant risk associated with this event was evaluated to be very low.
4132013001 | Catawba 1, Catawba 2 | 08/13/2013 | 10/10/2013 | ML13284A12 | <strong>Each Diesel Generator (DG) Was Determined to be Unknowingly Inoperable During its Monthly Surveillance Test Due to Technical Specification (TS) Surveillance Requirment (SR) 3.8.1.17 not being Met</strong><br /><i>Abstract:&nbsp;</i>On August 13, 2013, following the completion of an Engineering evaluation, it was determined that each DG had been unknowingly inoperable during its monthly surveillance test. Prior to this determination, Catawba had always considered the DG to remain operable during its monthly surveillance test. It was determined that under certain loading conditions, SR 3.8.1.17 could not be met while the DG was, being tested. SR 3.8.1.17 verifies that with the DG operating in the test mode and connected to its bus, an actual or simulated Engineered Safety Features (ESF) actuation signal overrides the test mode by retuming the DG to standby operation and automatically energizing the emergency load from offsite power. The DG control circuit is to return voltage and frequency to their pre-position settings if a load sequencer actuation occurs while the DG is operating paralleled to offsite power. However, it was determined that the control circuit will not return to its pre-position frequency setting if the DG is operating at greater than a threshold load value (the threshold load value varies with each DG). Operating outside of the TS required frequency range renders the DG inoperable. With the DG unknowingly inoperable, SR 3.8.1.1 was not performed within one hour as required. There was one instance where a DG was unknowingly inoperable during testing and the opposite train DG was simultaneously inoperable. The cause of this issue is an inadequate design of the DG pre-position control circuit attributed to a legacy design error that was transported from the original manufacturer to Catawba. Following the discovery of this issue, affected DG test procedures were revised to require declaring the DG inoperable during its monthly surveillance test. The Unit 1 DG control circuit will be revised (Unit 2 is complete) such that when the DG is operating paralleled to offsite power at full load, the pre-position circuit will energize to reset voltage and frequency to their required settings following an actuation of the DG load sequencer. There was minimal safety significance to this event. The DGs were operable except for those time periods when they were being tested while operating paralleled to offsite power at greater than the threshold load value. Therefore, this event did not affect the health and safety of the public.
4132013002 | Catawba 1 | 12/16/2013 | 02/10/2014 | ML14050A12 | <strong>Technical Specification Limiting Conditions for Operation (LCOs) 3.6.3 and 3.7.3 were Violated due to the Isolation of Nitrogen Supply to Two Unit 1 Main Feedwater Isolation Valves</strong><br /><i>Abstract:&nbsp;</i>On December 16, 2013, following the completion of an engineering evaluation, it was determined that main feedwater isolation valves (MFIVs) 1CF42 and 1CF60 had been unknowingly inoperable since the completion of the last Unit 1 refueling outage in December of 2012. The MFIVs have the possibility of becoming thermally bound or pressure locked following heat up of the feedwater system. To aid in opening the valves, they are procedurally "soft seated" by reducing the nitrogen pressure in the system. After the MFIV is opened, the nitrogen system is restored to its normal pressure. Following maintenance work to "soft seat" MFIVs 1CF33, 1CF42, 1CF51 and 1CF60 near the end of refueling outage 1EOC20, the nitrogen supply to 1CF33, 1CF42 and 1CF60 remained partially isolated. This condition went undetected until subsequent maintenance activities in November 2013 identified the issue. A review for the periods of time that the partial isolation existed identified that 1CF33 remained operable; however, during the time period of 7/13/13 - 11/8/13, 1CF-42 nitrogen accumulator pressure was below the operability limit for operation with the remote accumulator isolated and from 1/19/13 - 10/25/13, 1CF-60 nitrogen accumulator pressure was below the same limit. The cause is attributed to human errors related to inadequate job preparation and procedure use and adherence. The pre job brief was deficient and steps were inappropriately marked "not applicable" in the procedure. Planned corrective actions include updating model work orders used to plan this work to include a requirement to review corrective action program documents related to this event prior to performing this work and including this issue in the 2014 training covering operating experience for the Maintenance organization. There was minimal safety significance to this event. The closed system provided an inside containment isolation and the ability to perform at least one method of main feedwater isolation was maintained, therefore, this event did not affect the health and safety of the public.
4162013001 | Grand Gulf 1 | 01/04/2013 | 03/05/2013 | ML13064A37 | <strong>Reactor Protection System Actuation due to a Main Turbine Generator Trip</strong><br /><i>Abstract:&nbsp;</i>At 23:37 Central Standard Time on January 4, 2013, Grand Gulf Nuclear Station experienced an unexpected Reactor SCRAM caused by a Main Generator trip. The plant was operating in Mode 1 at 94 percent thermal power. All safety systems responded per design. Safety Relief Valves opened at the onset of the event to control reactor pressure and reseated properly. All control rods inserted when the signals generated by the Reactor Protection System were received. There were no Emergency Core Cooling System actuations. The shift immediately entered the appropriate Off Normal Event Procedures. The plant was stabilized with pressure control on the main turbine bypass valves and level control on the start-up level control valve, although high pressure feedwater heater start-up outlet valve 1N21F010B did not open. The cause of the SCRAM was the Main Generator 'A' Phase Neutral Current Transformer (CT) experienced partial grounding due to inadequate clearance between the micarta plate bolts and bottom of the CT allowing the conductors to come in contact with a bolt providing a shunt path to ground. This was caused by inadequate workmanship and work instructions not specifying the clearance during installation. There were no adverse effects on the health or safety of the public as a result of this event. The micarta plate bolts were subsequently removed or cut to provide adequate clearance prior to plant restart.
4162013002 | Grand Gulf 1 | 01/14/2013 | 03/15/2013 | ML13077A05 | <strong>Reactor Protection System Actuation due to a Turbine Trip</strong><br /><i>Abstract:&nbsp;</i>At 18:05 Central Standard Time on January 14, 2013, Grand Gulf Nuclear Station experienced an automatic Reactor SCRAM caused by a Turbine Trip due to a Main Generator lockout. The plant was operating in Mode 1 at 100 percent thermal power. All safety systems responded per design. Safety Relief Valves opened at the onset of the event to control reactor pressure and reseated properly. All control rods inserted when the signals generated by the Reactor Protection System were received. There were no Emergency Core Cooling System actuations. The shift immediately entered the appropriate procedures. The plant was stabilized with pressure control on the main turbine bypass valves and level control on the start-up level control valve, although high pressure feedwater heater start-up outlet valve 1N21F010B did not open when placing the start-up level control valve in service. There were no adverse effects on the health and safety of the public as a result of this event. The cause of the SCRAM was the Main Generator Isolated Phase Bus Cooling System experienced partial grounding due to design configuration of the horizontal bushing in an energized section of the bus, in close proximity to a degraded viewing port, which allowed water accumulation that created a ground condition. Additional portions of the isophase bus with seal off bushings were de-energized, and covers were installed over the viewing ports prior to plant restart.
4162013003 | Grand Gulf 1 | 07/30/2013 | 09/26/2013 | ML13273A35 | <strong>Reactor Protection System and Reactor Core Isolation Cooling Actuation Due to a High Reactor Pressure Transient</strong><br /><i>Abstract:&nbsp;</i>At 14:32 Central Daylight Time on July 30, 2013, Grand Gulf Nuclear Station experienced an unexpected Reactor SCRAM from 100% thermal power due to high reactor pressure detected by the Reactor Protection System. Operations staff immediately entered the appropriate off-normal event procedures. Reactor Core Isolation Cooling (RCIC) initiated and injected briefly during the transient, The RCIC initiation signal was valid, but not required to maintain the reactor vessel water level. Reactor levels were verified and RCIC was subsequently secured. All other systems operated as expected. Reactor pressure was controlled by discharging steam to the main condenser via the main turbine bypass valves. Reactor water level was controlled using the condensate and feedwater systems via the startup level control valve. No safety relief valves actuated. The cause of the SCRAM was a human performance-induced error due to inadequate troubleshooting activities on the Turbine Stress Evaluator (TSE). A temperature transmitter failure was not recognized nor corrected, thereby resulting in a false high turbine stress temperature signal. Upon restoration of the TSE, the incorrect signal forced turbine control valves in the closed direction and resulted in a high reactor pressure transient. Procedures and work orders are being revised to prevent recurrence of this event. There were no adverse effects to the health and safety of the public.
4162013004 | Grand Gulf 1 | 08/06/2013 | 10/03/2013 | ML13276A48 | <strong>Operation prohibited by Technical Specifications due to inadvertent bypass of Reactor Steam Dome High Pressure Interlock for Residual Heat Removal System isolation.</strong><br /><i>Abstract:&nbsp;</i>On August 6, 2013, at 10:15 Central Daylight Time (CDT) with the unit in Mode 1 at 93.5 percent thermal power, Grand Gulf Nuclear Station (GGNS) discovered that it was not in compliance with Technical Specification (TS) 3.3.6.1, Primary Containment and Drywell Isolation Instrumentation. Function 5.c, Reactor Steam Dome High Pressure Isolation of the Residual Heat Removal (RHR) system, was inoperable due to the jumpers that disable the function not being removed prior to startup. Upon discovery GGNS entered TS 3.3.6.1 Limiting Condition of Operation (LCO) Actions A.1, B.1, C.1, F.1 and H.1. Also, TS LCO 3.0.4 was not satisfied. At 11:11 CDT the jumpers were removed making the reactor steam dome high pressure isolation function Operable and the LCO actions were exited. <br /><br /> The cause of the event was a lack of Integrated Operating Instruction (IOI) 03-1-01-3, Cold Shutdown to Generator Carrying Minimum Load. to include the requirements of EN-DC-136, Temporary Modifications, for adequate procedural control of temporary modifications. Additionally, a failure of the Shift Manager (SM) to initiate a potential TS Limiting Condition for Operation Tracking Record (LCOTR) as required by pi-ocedure 02-S-01-17, Control of Limiting Conditions for Operation was identified as a contributing cause.<br /><br /> The event posed no threat to public health and safety. This interlock is provided only for equipment protection to preveni ntersystem loss of coolant accident(LOCA) scenario. Credit for the interlock is not assumed in the az:cdent c transient analysis sections of the Updated Final Safety Analysis Report (UFSAR)
4162013005 | Grand Gulf 1 | 12/12/2013 | 10/06/2014 | ML14280A28 | <strong>Reactor Pressure Vessel steam pressure less than 0 psig During six plant startups resulting in a violation of Technical Specification 3.4.11, RCS Pressure and Temperature (PIT) Limits</strong><br /><i>Abstract:&nbsp;</i>On December 12, 2013, with the plant operating in Mode 1 at 100 percent thermal power, Grand Gulf Nuclear Station (GGNS) discovered that during six past startups, the Reactor Pressure Vessel (RPV) steam pressure was below zero (0) pounds per square inch gage (psig) with the Main Steam Isolation Valves (MSIVs) open and the Mechanical Vacuum Pumps (MVPs) running without entering LCO 3.4.11 RCS Pressure and Temperature (P/T) Limits. From 12/12/10 through 12/12/13 there were six occurrences of reactor pressure being < 0 psig. The Reactor Pressure/Temperature curves in the GGNS Pressure and Temperature Limit Report (PTLR) have a minimum pressure value of 0 psig referenced on the curve. The lowest pressure noted in the six occurrences was approximately -9.9 psig on December 13, 2012. All systems performed per design during the reactor startups with RPV pressure below 0 psig during the past 3 years. The cause of not entering LCO 3.4.11 was the condition was procedurally allowed and aligned with Operations training. There were no adverse effects on the health or safety of the public as a result of these events.
4162013006 | Grand Gulf 1 | 12/17/2013 | 02/15/2014 | ML14044A03 | <strong>Primary Containment Inoperable Due to an Inadequate Surveillance Procedure Resulting in a Loss of Safety Function</strong><br /><i>Abstract:&nbsp;</i>On December 17, 2013, at 1322 central standard time (CST) with the plant operating in Mode 1 at 100 percent thermal power, Grand Gulf Nuclear Station (GGNS) personnel utilized a procedure that was improperly revised. The event was identified at approximately 1415 CST during the performance of the surveillance when valve E51F063, RCIC Steam Line Drywell Inboard Isolation was observed to close when a test signal was applied. This was not an expected condition, the surveillance was halted and corrective actions were commenced. The improperly revised procedure resulted in the inoperability of primary containment, a loss of safety function for primary containment and the inoperability of the Reactor Core Isolation Cooling (RCIC) system. Primary containment operability was restored at approximately 1437 CST when the breaker was closed to energize valve E51F064, RCIC Steam Line Drywell Outboard Isolation which restored the penetration to an operable status. RCIC was Inoperable at 1415 CST and restored to an operable condition at approximately 1435 CST when valve E51F063 was reenergized and opened. The direct cause of the event was an improper procedure revision that resulted in an inadequate procedure. The procedure was revised to be technically adequate and an extent of condition review was performed for the affected procedure writer's work. There were no adverse effects on the health or safety of the public as a result of the event.
4232013001 | Millstone 3 | 02/19/2013 | 04/15/2013 | ML13114A05 | <strong>Improperly Secured Enclosure Caused Inoperability of Steam Generator Pressure Transmitter</strong><br /><i>Abstract:&nbsp;</i>On February 15, 2013, with Millstone Power Station Unit 3 operating in MODE 1 at 100 percent power, operators discovered that the insulating cover installed over 3MSS*PT526, "B" Steam Generator Pressure Transmitter (SGPT) Channel 3, was not properly secured. When found, it was incorrectly assessed as not impacting equipment operability. However, on February 19, 2013, upon further review by the Electrical Equipment Qualification program engineer, it was determined that the SGPT would not be adequately protected from a postulated high energy line break (HELB). Therefore, 3MSS*PT526 was declared inoperable per Technical Specification (TS) 3.3.2, Engineered Safety Features Instrumentation, on February 19, 2013. Information exists that 3MSS*PT526 was inoperable on February 15, 2013, when the problem was initially discovered. Since the condition existed for longer than allowed by TS 3.3.2, Action 20 (i.e., for more than six hours without the bistable being placed in trip), this is a reportable condition per 10 CFR 50.73 (a)(2)(i)(B) as an event or condition which was prohibited by the plant's Technical Specifications. Lack of awareness of the purpose of the enclosure boundary combined with the lack of clear labeling identifying the HELB enclosure resulted in a delay in declaring the equipment inoperable. Operations created and installed a new label for the insulating box around each SGPT clearly indicating the box is a HELB barrier and is part of the environmental qualification boundary.
4232013002 | Millstone 3 | 01/28/2013 | 03/29/2013 | ML13100A12 | <strong>Secondary Containment Boundary Breach Could Have Prevented Safety Function</strong><br /><i>Abstract:&nbsp;</i>On January 28, 2013 with Millstone Power Station Unit 3 (MPS3) in MODE 1 at 100% power, engineering completed a maintenance rule evaluation of a previously identified condition where a roll-up door in the auxiliary building at MPS3 was found not fully closed after a security test. The door was open approximately 3/8 of an inch. This door is a secondary containment boundary, specifically a supplemental leak collection release system boundary. Engineering concluded the partially open roll-up door exceeded any available margin from the previous surveillance drawdown test. Additionally, during the investigation it was determined the door had been in the partially open condition in excess of the plant's Technical Specification Action Statement (TSAS) allowed outage time. <br /><br /> The direct cause of the event was the door had not been fully closed after completion of security testing. Upon discovery the door was unlocked, fully closed and relocked. The testing procedure has been changed to test the door without requiring the door to be opened. Additional corrective actions are being taken in accordance with the station's corrective action program. <br /><br /> This condition is being reported under 10 CFR 50.73(a)(2)(v)(C) as an event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to control the release of radioactive material. Additionally, since the secondary containment boundary was not re-established within the requirements of the TSAS (24 hours) this it is also being reported under 10 CFR 50.73(a)(2)(i)(B) as any operation or condition which was prohibited by the plant's Technical Specifications.
4232013004 | Millstone 3 | 03/13/2013 | 05/08/2013 | ML13142A03 | <strong>Failed Surveillance Test of A Train Control Room Emergency Filtration System</strong><br /><i>Abstract:&nbsp;</i>On March 13, 2013, at 1741 hours with Millstone Power Station Unit 3 operating in MODE 1 at 100 percent power, a charcoal filter sample was drawn from the A Train Control Room Emergency Filtration System (CREFS). On March 19, 2013, Engineering was notified by the vendor who performs the testing that the methyl iodide penetration test performed on the charcoal filter sample had failed. Accordingly, it was concluded that the A CREFS was actually inoperable on March 13, 2013, when the sample was originally taken. Operators were notified, and the A CREFS was declared inoperable per Technical Specification (TS) 3.7.7, on March 19, 2013, at 1500 hours. The charcoal filter was replaced and retested satisfactory. The A Train CREFS was declared operable on March 21, 2013, at 2236 hours. The condition existed for longer than allowed by TS 3.7.7, Action (a), i.e., for more than 7 days. Therefore, this is a reportable condition per 10 CFR 50.73 (A)(2)(i)(B) as any event or condition which was prohibited by Technical Specifications. The apparent cause is a failure to establish administrative limits for replacement of the CREFS charcoal filters, prior to reaching its TS limit. Surveillance Procedures for performing charcoal filter testing have been updated to specify overnight shipping for charcoal samples and to request immediate feedback from vendors if the test fails.
4232013005 | Millstone 3 | 05/15/2013 | 07/15/2013 | ML13248A44 | <strong>Loss of Containment Integrity due to Failed Airlock</strong><br /><i>Abstract:&nbsp;</i>On May 15, 2013, at 0400 hours, with the Millstone Power Station Unit 3, (MPS3) in MODE 4 at 0% power, it was discovered that an equalizing valve for the outer containment door was leaking by its seat rendering the outer containment door inoperable. This condition was discovered by maintenance personnel as they were exiting containment through the inner containment door. The inner containment door was open for transit at the time the leaking equalizing valve was discovered. <br /><br /> The most likely cause of the leaking equalizing valve on the MPS3 outer containment door was personnel error in that the equalizing valve was most likely inadvertently bumped by personnel in transit causing it to be slightly open. <br /><br /> The inner containment door was immediately closed. Maintenance personnel subsequently verified the equalizing valve handle was in the closed position, inspected the containment door seals, and tested both the inner and outer containment doors with satisfactory results. Additional corrective actions are being taken in accordance with the station's corrective action program. <br /><br /> This event is being reported in accordance with 10 CFR 50.73(a)(2)(v), as an event that could have prevented the fulfillment of a the safety function of structures or systems that are needed to: (C) Control the release of radioactive material.
4232013007 | Millstone 3 | 08/09/2013 | 10/07/2013 | ML13295A22 | <strong>Reactor Trip on Low-Low Steam Generator Level</strong><br /><i>Abstract:&nbsp;</i>On August 09, 2013 at 2119, while in MODE 1 at 100 percent power, Millstone Power Station Unit 3 experienced an automatic reactor trip on steam generator (SG) low-low water level. The low-low SG water level condition resulted from all main feed water pump recirculation valves failing full open following a loss of power from non safety-related 480 volt load center 32L. This bus powered the instrumentation loops for all three main feedwater pump recirculation valve controllers. Upon the loss of power, the valves went to their failure state of "Recirculation", resulting in a loss of feedwater header pressure and flow to the steam generators causing the unit to automatically trip on low-low steam generator level. The auxiliary feedwater system started as designed and maintained steam generator levels. Safety systems functioned as expected. There were no radiological challenges as a result of the event.<br /><br /> The direct cause of the event was the loss of power to the 480V bus that powered the three main feedwater pump recirculation valve controllers. Troubleshooting efforts did not reveal the cause of the ground that led to the loss of bus 32L. Power to the three main feedwater recirculation valves has been temporarily moved to another power supply.<br /><br /> This event is being reported in accordance with 10 CFR 50.73(a)(2)(iv)(A) as an event that resulted in manual or automatic actuation of systems listed in 10 CFR 50.73(a)(2)(iv)(B).
4232013009 | Millstone 3 | 11/19/2013 | 01/15/2014 | ML14037A10 | <strong>Secondary Containment Boundary Breach Could Have Prevented Safety Function</strong><br /><i>Abstract:&nbsp;</i>On November 19, 2013 while operating in MODE 1 at 100% power, a security door in the auxiliary building at Millstone Power Station Unit 3 (MPS3) was found unlatched during a door seal check. Upon discovery, the door was successfully latched and the control room notified. In addition to being a security boundary, this door is also a secondary containment boundary, specifically a supplemental leak collection release system (SLCRS) boundary. The door was previously verified properly latched on November 16, 2013. On November 20, 2013 operators determined that the unlatched door resulted in a condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to control the release of radioactive material and mitigate the consequences of an accident. The direct cause of the condition was an unlatched door that did not ensure proper sealing of the credited SLCRS boundary. Upon discovery, the door was successfully latched and the control room notified. Since the door is a SLCRS boundary, it is sealed to tight tolerances and is stiff to open, close, and latch due to the sealing design. The stiffness of the door can be misleading to persons who pull/push on the door to verify it is latched. The door seals and latching mechanism were inspected with no apparent failure and received minor adjustment. Positive assurance of proper latching of doors continues to be reinforced at MPS. This condition is being reported under 10 CFR 50.73(a)(2)(v)(C) and 10 CFR 50.73(a)(2)(v)(D).
4242013001 | Vogtle 1 | 11/27/2013 | 01/16/2014 | ML14016A18 | <strong>Failure to Comply with Technical Specification LCO 3.8.4</strong><br /><i>Abstract:&nbsp;</i>On November 27, 2013, an internal wiring discrepancy was discovered on Class 1E battery charger 1AD1CB [EJ] following the trip of the battery charger AC input breaker. The wiring discrepancy prevented the battery charger from performing all required functions of LCO 3.8.4, DC Sources - Operating. One of two redundant battery chargers and one battery per train must be operable to meet the requirements of LCO 3.8.4. Subsequent review of battery charger maintenance activities determined that on September 30, 2013 the remaining redundant operable battery charger was removed from service for maintenance activities for approximately 14.5 hours. LCO 3.8.4, DC Sources - Operating requires restoration of the inoperable DC source within 2 hours or entry into Mode 3 within the next 6 hours, and entry into Mode 5 within the following 30 hours. Although the degraded charger was able to maintain battery terminal voltage within limits under minimal loading condition, the DC source was inoperable for a time greater than allowed by Technical Specification.<br /><br /> The safety significance of this event is very low. Unit 2 was not affected and there were no adverse effects to the health and safety of the public.
4252013001 | Vogtle 2 | 02/26/2013 | 04/22/2013 | ML13113A02 | <strong>Manual Reactor Trip due to High Reactor Coolant Pump Seal Leakoff Flow</strong><br /><i>Abstract:&nbsp;</i>On February 26, 2013, at approximately 2302 Eastern Daylight Time (EDT) time, with Unit 2 operating in Mode 1 at 94 percent rated thermal power and End of Life (EOL) Coastdown in progress, Unit 2 operators initiated a manual reactor trip due to Reactor Coolant Pump (RCP) #4 number one seal leakoff flow exceeding the operating limits. The Reactor Trip System, the Engineered Safety Feature Actuation System, and other responding equipment performed as expected. The plant was stabilized in Mode 3. The cause of the event was the addition of air into the Chemical Volume Control System (CVCS) charging system as a result of less than adequate filling and venting of the Reactor Coolant System filter.<br><br> The safety significance of this event is low. Unit 1 was unaffected and there were no adverse effects on the health and safety of the public.
4252013002 | Vogtle 2 | 10/19/2013 | 12/13/2013 | ML13350A34 | <strong>Automatic Unit 2 Reactor Trip due loss of Generator Excitation</strong><br /><i>Abstract:&nbsp;</i>On October 19, 2013 at approximately 0645 Eastern Daylight Time (EDT), Vogtle Unit 2 was operating in Mode 1 at 100% power. The main generator excitation system experienced a failure which tripped the Main Generator which subsequently tripped the Turbine and Reactor. The Reactor Trip System, the Engineered Safety Feature Actuation System, and other responding equipment performed as expected. The plant was stabilized in Mode 3. The cause of the event was a failure of the Main Generator excitation system. <br /><br /> The safety significance of this event is very low. Unit 1 was not affected and there were no adverse effects of the health and safety of the public.
4252013003 | Vogtle 2 | 10/22/2013 | 12/13/2013 | ML13350A58 | <strong>Manual Reactor Trip Due to Lowering Condenser Vacuum</strong><br /><i>Abstract:&nbsp;</i>Unit 2 Reactor was manually tripped at 11:44 on 10-22-13 due to lowering condenser vacuum. The Unit was undergoing power ascension in Mode 1 at 25 percent power. At the time of the reactor trip, maintenance was in progress on Main Feedwater Pump (MFP) B. Prior to work commencing the possibility of impacting condenser vacuum due to maintenance activities was discussed and operational limits were established. After the MFP B pump steam chest lift was initiated, condenser vacuum began lowering and maintenance was directed to lower the MFP B steam chest. Condenser vacuum approached the predetermined operational limit of 23 inches of mercury vacuum and the Shift Supervisor directed a manual reactor trip of the Unit 2 reactor. Unit 2 was stabilized in Mode 3 on Auxiliary Feedwater with the Main Condenser available for decay heat removal. All systems responded as expected. The primary cause of the event was air in leakage past the MFP B turbine exhaust valve to the Main Condenser. <br /><br /> The safety significance of this incident is very low and there were no adverse effects on the health and safety of the public.
4402013001 | Perry | 01/22/2013 | 03/21/2013 | ML13085A07 | <strong>Loss of Feedwater Results in Automatic Reactor Protection System Actuation</strong><br /><i>Abstract:&nbsp;</i>On January 22, 2013, at 0332 hours, the reactor protection system (RPS) automatically actuated due to a loss of feedwater flow to the reactor pressure vessel (RPV). There were no complications during the shutdown as all control rods fully inserted and pressure was maintained by normal means. The High Pressure Core Spray (HPCS) and the Reactor Core Isolation Cooling (RCIC) systems actuated based on a valid reactor water level initiation and injected to restore RPV water level. The cause of the event was failure of a balance-of-plant inverter/static transfer switch, which provides electrical power to the digital feedwater control system. A circuit card in the static transfer switch degraded, which affected operation of the inverter. The electrical loads serviced by the inverter/static transfer switch were placed on an alternate power source. This alignment will continue until permanent repairs are made which are currently scheduled for the next refueling outage. The safety significance of this event is considered to be small. This event is being reported in accordance with 10 CFR 50.73(a)(2)(iv)(A) as an event or condition that resulted in an automatic actuation of the RPS, HPCS, and RCIC systems, and Operational Requirements Manual section 7.6.2.1, which requires a Special Report submittal following an Emergency Core Cooling System actuation and injection into the reactor coolant system.
4402013002 | Perry | 03/25/2013 | 05/23/2013 | ML13149A23 | <strong>Condition Prohibited by Technical Specifications due to Scram Discharge Volume Level Switch Isolation</strong><br /><i>Abstract:&nbsp;</i>On March 25, 2013, at approximately 1527 hours, maintenance personnel identified that a level instrument root valve for the control rod drive system, scram discharge volume (SDV) was closed and locked. With the valve in the closed position, the associated SDV float level switch, which provides input to the reactor protection system logic, could not perform its function and resulted in noncompliance with the Limiting Condition for Operation for Technical Specification 3.3.1.1.<br><br> The cause of the event was a failure to follow procedures. During the last performance of a calibration surveillance test, the instrumentation and control technicians did not open the valve as required and left the valve in the closed position. Independent verification of the valve position and locking device attachment failed to identify the error. Maintenance personnel promptly restored the valve to the locked open position. Corrective actions were administered through the internal performance management process. There were no system failures associated with this event.<br><br> The safety significance of this event is considered to be small. This event is being reported in accordance with 10 CFR 50.73(a)(2)(i)(B) as any operation or condition that was prohibited by the plant's Technical Specifications.
4402013003 | Perry | 06/15/2013 | 10/04/2013 | ML13281A80 | <strong>Shutdown Required by Technical Specifications due to RCS Pressure Boundary Leakage</strong><br /><i>Abstract:&nbsp;</i>A planned power reduction commenced June 14, 2013, to inspect the Drywell for sources of unidentified leakage. Following a refueling outage completed in May 2013, the Drywell unidentified leakage was higher than levels prior to the outage. The Drywell inspection identified two leak sites, one of which was in the reactor coolant system (RCS) pressure boundary. A plant shutdown was conducted in accordance with Technical Specification 3.4.5, RCS Operational Leakage, to facilitate repairs. During the shutdown process and after the reactor was subcritical, the reactor protection system was actuated to insert the remaining withdrawn control rods. <br /><br /> The cause of the RCS pressure boundary leakage is a combination of stress corrosion cracking and fatigue or corrosion fatigue. A new vent valve assembly was fabricated and installed on the reactor recirculation system B flow control valve. Inspection of other vent and drain valves with similar configuration on the reactor recirculation system found no deficiencies. Design configuration options to address the cause will be evaluated. <br /><br /> The safety significance of this event is considered to be small. This event is being reported in accordance with 10 CFR 50.73(a)(2)(i)(A), 10 CFR 50.73(a)(2)(ii)(A), and 10 CFR 50.73(a)(2)(iv)(A).
4402013004 | Perry | 10/17/2013 | 12/09/2013 | ML13346A43 | <strong>Vulnerability to Cause Secondary Fire due to Unfused Control Room Ammeters</strong><br /><i>Abstract:&nbsp;</i>On October 17, 2013, at 1300 hours, a review of industry operating experience regarding the impact of unfused Direct Current ammeter circuits in the Control Room determined the described condition to be applicable to the Perry Nuclear Power Plant resulting in a potentially unanalyzed condition with respect to 10 CFR 50 Appendix R analysis requirements. The original plant wiring design and associated safe shutdown analysis for the Class 1E batteries control room ampere indications do not include overcurrent protection features to limit the fault current.<br /><br /> The cause of this event was determined to be a latent design error related to wiring and isolation that constituted a fire protection program deficiency which could adversely affect the ability to achieve and maintain safe shutdown of the plant in the unlikely event of a control room fire. A probabilistic risk assessment of this event determined the event to be of small safety significance.<br /><br /> The identified deficiency was corrected utilizing temporary modifications to the plant that eliminated the potential for a control room fire to induce a hot short. The corrective actions to permanently address this condition include the design and implementation of a permanent plant modification to isolate the indication circuits in the unlikely event of a control room fire.<br /><br /> This event is being reported in accordance with 10CFR50.73(a)(2)(ii)(B) as an unanalyzed condition
4432013001 | Seabrook | 10/30/2013 | 12/23/2013 | ML13365A00 | <strong>Failure to Enter Technical Specification following Discovery of SW Leak</strong><br /><i>Abstract:&nbsp;</i>On October 30, 2013, review of actions taken for a leak in the service water (SW) supply piping determined that the station did not declare SW inoperable and enter TS 3.7.4.d, resulting in the plant operating in a condition prohibited by Technical Specifications from August 8, 2013 to September 1, 2013.<br /><br /> On August 7, 2013 UT examination conducted in response to a small pipe leak, identified a rectangular indication of 2.327" X 1.5" on a field weld on the SW strainer bypass line. A prompt operability determination (POD) found the pipe degraded but operable. When leakage increased on both August 20 and August 28, operators determined that the increase was within the bounds of the initial POD. A relief request was approved by the NRC and a repair completed on September 1.<br /><br /> On October 30, 2013 it was determined that had available information challenging the conclusion of system operability been properly evaluated, Operators would have entered TS 3.7.4.d. The root cause is the POD process lacked sufficient barriers to ensure that the preparation error (Direct Cause) was recognized and corrected prior to POD approval. Corrective action is to revise the Operability Determination procedure to add appropriate process barriers to ensure the engineering evaluation adequately documents consideration of field input information and assumptions for safety functions.
4452013001 | Comanche Peak 1 | 01/08/2013 | 03/07/2013 | ML13079A33 | <strong>Inoperability of Unit 1 Emergency Airlock Exterior Door</strong><br /><i>Abstract:&nbsp;</i>On January 8, 2013, Maintenance personnel attempted to open the Unit 1 Emergency Air Lock (EAL) interior door, but it would not move. On January 14, 2013, it was determined the Unit 1 emergency airlock exterior equalization valve had been out of position from 12/22/2012 until 01/08/2013 resulting in the emergency airlock being inoperable. This condition exceeded the 24 hour Limiting Condition for Operation (LCO) action of Technical Specification (TS) 3.6.2 Condition A, resulting in a condition prohibited by the TS. The cause of this event was procedures did not provide adequate guidance for operating the Unit 1 EAL exterior door mechanism. Corrective actions include revising procedures to stipulate that the door handwheel should be operated in the close direction until tight.
4452013002 | Comanche Peak 1, Comanche Peak 2 | 10/08/2013 | 12/09/2013 | ML14008A20 | <strong>Unanalyzed Condition Under 10cfr50 Appendix R, Secondary Fires from Unprotected Ammeter Wiring</strong><br /><i>Abstract:&nbsp;</i>On October 8, 2013, during a review of industry operating experience OE 305419 regarding the impact of non-fused, Direct Current (DC) ammeter circuits in the control room, it was determined that the described condition was applicable to Comanche Peak Nuclear Power Plant. This resulted in a potentially unanalyzed condition with respect to 10CFR50 Appendix R analysis requirements. The original plant wiring and associated analysis for the Class 1 E batteries control room ampere indications do not include overcurrent protection features to limit the fault current. Comanche Peak Nuclear Power Plant (CPNPP) Units 1 and 2 were in Mode 1 operating at 100% power. <br /><br /> The cause of this event was the original design of the DC ammeter circuits did not adequately address fire protection program requirements. <br /><br /> Immediate corrective actions were to develop and implement compensatory measures to maintain requirements of 10CFR50 Appendix R. As a part of the CPNPP Corrective Action Program, a design change to include circuit protection for the cables routed from the Safety Related batteries to the control room DC ammeters will be developed and implemented. <br /><br /> All times in this report are approximate and Central Time unless noted otherwise.
4452013003 | Comanche Peak 1 | 12/04/2013 | 01/30/2014 | ML14043A08 | <strong>Auto Start of Both Units' Auxiliary Feedwater Pumps and Emergency Diesel Generators Due to a Loss of Both Units' Safeguards Electrical Power</strong><br /><i>Abstract:&nbsp;</i>At 1341 Central Standard Time (CST) on December 4, 2013, CPNPP experienced a loss of safeguards electrical power to both Units when 345kV (kilo-Volt) transformer XST2 lost power while the 138kV transformer XST1 was out-of-service for a modification. During the modification work for XSTI, a 6.9kV Phase B cable fed from XST2's X winding was incorrectly cut and electrical protection circuits actuated to isolate transformer XST2. At the time of the cut, the cable was energized and supplying power to various safeguards Loads. Non-safeguards electrical power remained energized. Both Units remained at power in MODE 1. All auxiliary feedwater (AFW) pumps, three per Unit, started on both Units. All four emergency diesel generators (EDGs), two per Unit, automatically started and all safeguards buses were re-energized from the EDGs. Operations declared an Unusual Event (UE). All engineered safety feature (ESF) systems functioned as expected. At 1341 CST, both Units entered Technical Specification (TS) 3.8.1, Condition C, Required Action C.2 which allowed 24 hours for restoring one offsite circuit (XST1 or XST2) to OPERABLE status. CPNPP requested and received discretionary enforcement from the Nuclear Regulatory Commission (NRC) to allow an additional 14 hours to restore XSTI or XST2 to OPERABLE. The XST2 cable repair was completed and XST2 was declared OPERABLE on. December 5, 2013 at 1717 CST and the Notice of Enforcement Discretion and UE were terminated. XSTI was declared OPERABLE on December 6, 2013 at 0019 CST. There were no injuries resulting from the cut cable. All times in this report are approximate and CST unless noted otherwise.
4462013001 | Comanche Peak 2 | 01/06/2013 | 03/07/2013 | ML13079A33 | <strong>Unit 2 Hot Shutdown Panel Transfer Switch Inoperable due to Wiring Error</strong><br /><i>Abstract:&nbsp;</i>On January 6, 2013, Comanche Peak Nuclear Power Plant (CPNPP) Unit 2 was in Mode 1 operating at 100% power. At 0345 hours while performing surveillance testing on the Hot Shutdown Panel (HSP), the Turbine Driven Auxiliary Feedwater Pump (TDAFWP) steam supply valve control transfer switch was placed in the HSP position. During the test, the steam supply valve for the TDAFWP pump opened when it should have remained closed. Therefore, the TDAFWP steam supply control transfer switch was declared inoperable. This condition existed for greater than the allowable Technical Specification (TS) required action completion of time of 30 days for TS 3.3.4, Remote Shutdown System. The cause of this event was the new circuit wiring at the Unit 2 HSP was landed on incorrect terminals. This error was not found during the verification of termination of the new circuit wiring. The post work testing requirements were ineffective in the discovery of the error. Immediate corrective actions included correct termination of the cables and completion of the surveillance testing of the HSP. As a part of the CPNPP Corrective Action Program, procedures will be revised to ensure that the conduct of field work and inspection of cable terminations is correct and post work testing training will ensure that all aspects of the modified circuit are tested. All times in this report are approximate and Central Time unless noted otherwise.
4462013002 | Comanche Peak 2 | 11/01/2013 | 12/18/2013 | ML14002A24 | <strong>Unit 2 Reactor Trip due to Relay Actuation</strong><br /><i>Abstract:&nbsp;</i>At 2146 Central Standard Time (CST) on 11/1/2013, Unit 2 was in Mode 1 at 100% power when the reactor tripped during Solid State Protection System (SSPS) slave relay testing. This test utilizes a blocking circuit to verify the operability of the slave relay which trips the main turbine and both main feedwater pump turbines, on a Hi-Hi steam generator level or safety injection (SI). While positioning the slave relay switch in a testing lineup, the relay actuated. The Unit 2 turbine tripped as well as both main feedwater pumps. The trip of both main feedwater pumps started all three Auxiliary Feedwater (AFW) Pumps. All systems responded as expected. The cause of the Unit 2 reactor trip was an original design issue with the main turbine test cabinet. The corrective action is to add a test signal electrical interlock with the blocking relay to prevent slave relay actuation until the block is established for test circuits in Units 1 and 2. All times in this report are approximate and CST unless noted otherwise.
4542013001 | Byron 1, Byron 2 | 09/17/2013 | 11/18/2013 | ML13338A58 | <strong>Failed Surveillance Test of A Train Control Room Emergency Filtration System</strong><br /><i>Abstract:&nbsp;</i>At 1140 hours on September 17, 2013, with Byron Station Unit 1 operating in Mode 1 at 100 percent power, a charcoal filter sample was drawn from the A Train Control Room Emergency Filtration System (CREFS). On September 26, 2013, Engineering was notified by the testing vendor that the methyl iodide penetration test performed on the charcoal filter sample had failed. Accordingly, it was concluded that the A Train CREFS had actually been inoperable since September 17, 2013, when the sample was originally removed from the filter unit. Operators were notified, and the A Train CREFS was declared inoperable in accordance with Byron Technical Specification (TS) 3.7.10, on September 26, 2013, at 0645 hours. The charcoal filter was replaced and retested satisfactorily. The A Train CREFS was declared operable on September 27, 2013, at 2057 hours. Since the condition existed for longer than allowed by TS 3.7.10, Required Action (A.1), i.e., for more than 7 days, this is a reportable condition per 10 CFR 50.73 (a)(2)(i)(B) as any event or condition that was prohibited by Technical Specifications. The cause of the unsatisfactory sample test result is that the applicable charcoal banks had reached their end of life.
4552013001 | Byron 2 | 03/20/2013 | 05/20/2013 | ML13137A31 | <strong>Unit 2 Manual Reactor Trip due to Loss of Main Generator Stator Cooling Water</strong><br /><i>Abstract:&nbsp;</i>At 19:51 hours on March 20, 2013, Byron Unit 2 was manually tripped due to a loss of all Generator Stator Cooling Water (GC) when the 2A Generator Stator Cooling Water pump (2A GC) tripped and the redundant (2B GC) pump was unavailable due to a previous pump failure on February 17, 2013. The 2BEP -0, "Reactor Trip or Safety Injection Unit 2" procedure was entered and a transition was made to 2BEP ES 0.1, "Reactor Trip Response Unit 2." The root cause was the failure of the inboard motor bearing on the 2A GC pump motor due to insufficient lubrication as supplied by the vendor. This failure resulted in contact between the rotor and stator windings causing the electrical failure of the motor. Corrective actions include replacement of the failed motor and inspection of the remaining GC pump motors. All other plant systems operated as designed in response to the shutdown and, there were no safety consequences impacting plant or public safety as a result of this event. The Generator Cooling System is a non-safety related design feature and is not credited in any Updated Final Safety Analysis Report chapter 15 accident and transient analyses. The actuation of the reactor protection system was reported to the NRC in accordance with 10CFR 50.72 (b)(2)(iv)(B) and 10 CFR 50.73 (a)(2)(iv)(A).
4552013002 | Byron 2 | 09/18/2013 | 11/18/2013 | ML13338A17 | <strong>Unqualified Valve Diaphragm Installed in 2RE9160A</strong><br /><i>Abstract:&nbsp;</i>On September 18, 2013, the plant was in Mode 1 with reactor power at 100 percent. At 1555, an unqualified valve diaphragm was identified to have been installed on Air Operated Valve 2RE9160A, Reactor Coolant Drain Tank to Waste Gas (GW) Compressor Inside Containment Isolation Valve, during the 2011 refuel outage.<br /><br /> The 2RE9160A valve was immediately declared inoperable based on the unqualified valve diaphragm. The associated containment penetration was isolated per the required actions in Byron Technical Specification (TS) 3.6.3, Condition A. Since the condition existed for longer than allowed by TS 3.6.3 (Containment Isolation Valves), Required Action A.1, i.e., for more than 4 hours, this is a reportable condition per 10 CFR 50.73 (a)(2)(i)(B) as any event or condition that was prohibited by Technical Specifications.<br /><br /> The cause of the event was an incorrect assumption made by the Maintenance Work Planner to use an unqualified valve diaphragm in a qualified application.
4552013003 | Byron 2 | 08/15/2011 | 11/25/2013 | ML13326B06 | <strong>Unit 2 A-Train Diesel Generator Ventilation Fan Not Reset</strong><br /><i>Abstract:&nbsp;</i>On September 26, 2013, it was identified that a previous condition had existed where the Unit 2, A-Train (2A), Diesel Generator (DG) Ventilation Fan did not automatically start in support of a DG surveillance.<br /><br /> On August 15, 2011, with Byron Station Unit 2 operating in Mode 1 at 100 percent reactor power, the 2A DG Ventilation Fan was left in a condition that made it unable to automatically start on an emergency actuation. The error was discovered two days later during a routine scheduled DG surveillance. As a result, the 2A DG was discovered to have been inoperable for two days and the station did not perform the required Technical Specification surveillances for one DG inoperable. This condition resulted in a violation of Technical Specification 3.8.1, "AC Sources - Operating", Required Condition B, and is a reportable condition in accordance with 10 CFR 50.73 (a)(2)(i)(B) as any event or condition that was prohibited by Technical Specifications.<br /><br /> The cause was that the Post Maintenance Test (PMT) work instructions did not identify the need to reset the High Differential Pressure (D/P) trip signal by placing the Ventilation Fan Control Switch in Pull-to-Lock (PTL) and did not validate that the ventilation fan would restart after a High D/P Trip.
4562013001 | Braidwood 1 | 08/01/2013 | 09/30/2013 | ML13273A47 | <strong>Inadequate Operability Determination Procedure Guidance Results in Inadvertent Missed Technical Specification Action for Diesel Generator</strong><br /><i>Abstract:&nbsp;</i>On August 1, 2013 at 1345, a through wall leak was observed on the Essential Service Water return line from the 1A Diesel Generator at a 90 degree horizontal elbow. Initial operability was determined to be supported based on the condition of the pipe and the assessment that the flaw was a localized pinhole. <br /><br /> It was later determined that based on the location of the flaw (on an elbow fitting), ASME Code Case 513-3 did not apply and Diesel Generator operability could not be supported. Due to the initial assessment of operability, Operations did not perform the Technical Specification (TS) 3.8.1 required 1 hour and 8 hour Diesel Generator availability TS Surveillance Requirements (SR) at the time of discovering the leak. The performance of the TS SRs is to verify the correct breaker alignment and indicated power availability for each required qualified circuit. <br /><br /> The cause of this event was determined to be the complexity of applying the procedure OP-AA-108-115, "Operability Determinations" section on ASME flaw evaluation/Class 1, 2 and 3 leakage. <br /><br /> Corrective actions to prevent recurrence include revising the Operability Determination procedure, OP-AA-108-115, to provide clearer guidance when applying the requirements of ASME Code Case 513-3,
4562013002 | Braidwood 1 | 09/14/2013 | 11/13/2013 | ML13318A09 | <strong>Liquid Penetrant Indications in Embedded Flaw Repair of Control Rod Drive Mechanism Penetration 69 During Refueling Outage</strong><br /><i>Abstract:&nbsp;</i>On September 14, 2013 at 0100 hours, indications exceeding ASME Section 111 acceptance criteria were discovered in the embedded flaw repair weld of Control Rod Drive Mechanism (CRDM) Penetration 69. A total of 22 recordable indications located within the embedded flaw repair weld were documented, with 13 rounded indications exceeding the acceptance criteria (ASME Section III 1971 Edition through the Summer 1973 Addenda) of dimensions greater than 3/16". The indications in Penetration 69 were removed/reduced to acceptable size or reduced and weld repaired to restore the embedded flaw repair as approved by the NRC in Braidwood Relief Request I3R-09. This LER is being submitted in follow-up to ENS 49343 that was made at 0447 hours on September 14, 2013.<br /><br /> Based on industry experience, the cause of this event was determined to be mechanical discontinuities/minor subsurface voids opening up to the weld surface due to thermal and/or pressure stresses during plant operation.<br /><br /> Corrective actions to prevent recurrence include consideration of a long term Alloy 600 mitigation plan and other potential alternatives for the remaining acceptable but unrepaired penetrations on the Braidwood Units 1 and 2 RPV closure heads. This corrective action plan is under development and will also evaluate peening of the remaining acceptable but unrepaired CRDM penetrations.
4582013001 | River Bend | 03/02/2013 | 04/18/2013 | ML13116A00 | <strong>Operations Prohibited by Technical Specifications for Operations with a Potential to Drain the Reactor Vessel</strong><br /><i>Abstract:&nbsp;</i>On March 2, 2013, at approximately 1448 CST, with the plant in a refueling outage, maintenance on the reactor recirculation system was commenced without taking the required actions to comply with the applicable Technical Specifications. This maintenance constituted operations with a potential to drain the reactor vessel, and the required action for such an activity is restoration of the integrity of primary containment. This action was not taken, and the provisions of NRC Enforcement Guidance Memorandum 11-003 (Rev. 1) were instead invoked. The maintenance was completed and compliance with Technical Specifications was restored at 0830 CST on March 7. This event is being reported in accordance with 10 CFR 50.73(a)(2)(i)(B) as operations prohibited by Technical Specifications, as additionally specified by the Enforcement Guidance Memorandum.
4582013002 | River Bend | 09/19/2013 | 11/06/2013 | ML13317B62 | <strong>Potential Loss of Safety Function of Secondary Containment due to Employee Leaving a Door Unsecured</strong><br /><i>Abstract:&nbsp;</i>On September 19, 2013, at approximately 1437 CDT, with the plant operating at 100 % power, a door in the secondary containment pressure boundary was left unsecured by an employee entering the building. Upon closing the door, the employee mistakenly rotated the handwheel slightly, caused the latch bolts to extend partially. The latch bolts then contacted the outside of the keepers in the door frame, blocking the door open. The employee did not notice that the door was slightly open when he rotated the handwheel to the "closed" position, and then did not properly confirm its security prior to leaving the area. A security officer responded to the resultant alarm, and fully closed the door approximately four minutes later. This event was caused by improper use of human performance techniques by the employee, in that he failed to confirm that he had operated the door correctly. This event is being reported in accordance with 10 CFR 50.73(a)(2)(v) as a condition that could have caused the loss of the safety function of the secondary containment pressure boundary. Since the plant's safety analysis does not assume the function of secondary containment for the first 30 minutes of the design basis accident, safety function was actually maintained. This event was of minimal significance with regard to the health and safety of the public.
4612013001 | Clinton 1 | 02/18/2013 | 04/17/2013 | ML13122A26 | <strong>Inadequate Risk Identification Results in Loss of Safety Function</strong><br /><i>Abstract:&nbsp;</i>On 2/18/13, the Division 4 Nuclear System Protection System (NSPS) inverter transferred to its alternate power source. Instrument maintenance technicians were performing a surveillance when a technician inadvertently dropped a test cable and connector. The cable connector swung down and by pendulum motion went under a robust operational barrier in the cabinet coming in contact with the bottom edge of a fuse block staple jumper. The momentary shorting to ground caused the Division 4 NSPS bus to transfer from its normal inverter power source to its alternate power source. Per Technical Specifications (TS), the NSPS is inoperable when powered by its alternate source. With the NSPS inoperable, per the TS, operators declared the High pressure Core Spray System, a single train safety system, inoperable and reported the condition as a loss of safety function. The cause of this event was an inadequate risk identification related to pendulum motion of the cable connector during jobsite planning and set up for the job. Corrective actions include an Instrument Maintenance Department stand down, use of a checklist to aid in challenging jobsite conditions for risk/hazards assessment and management observations, and a case study of this event for Maintenance personnel. There were no safety consequences; the HPCS was capable of initiating with the operable Division 3 NSPS inverter.
4612013002 | Clinton 1 | 03/07/2013 | 05/02/2013 | ML13141A25 | <strong>Deficient Fuse Causes Main Generator Trip, Turbine Trip and Reactor SCRAM</strong><br /><i>Abstract:&nbsp;</i>On 3/7/13, at 0756 hours, the main generator tripped followed by a main turbine trip and an automatic reactor SCRAM at 0758 hours. A troubleshooting team was immediately dispatched to investigate the cause of the event and found that a fuse was blown/open on the C phase of the main generator's voltage regulating potential transformer (PT). This fuse is designed to fast blow. A voltage balance relay is installed to sense a fast blow failure and prevent a generator trip. Investigation found that the fuse did not fast blow and instead degraded gradually and did not allow the voltage balance relay to detect a problem, thus the relay did not prevent the main generator trip and subsequent SCRAM. A failure analysis of the fuse identified that the cause of the C phase potential transformer fuse failure was a manufacturing defect in a solder connection in the fuse. The poor solder connection was caused by deficiencies in the manufacturing process. Corrective actions include replacing the fuse that failed with a fuse that was not manufactured at the affected facility. An evaluation is being performed to determine when to inspect and replace the population of other potentially affected fuses.
4612013003 | Clinton 1 | 04/26/2013 | 06/24/2013 | ML13191A82 | <strong>Manual Reactor SCRAM Due To Main Electro-Hydraulic Control System Failure</strong><br /><i>Abstract:&nbsp;</i>On 4/26/13, with the plant at 97 percent power, the Main Control Room received a Main Electro-Hydraulic Control (EHC) pressure alarm due to lowering level in the EHC Oil Reservoir. An operator reported Main EHC Oil Reservoir level was at minus 4.25 inches and rapidly lowering. In response, Operators initiated a manual reactor SCRAM. All control rods fully inserted and the plant responded as expected to the SCRAM. The EHC oil leak was caused by a broken socket head cap screw used to attach a hydraulic shutoff valve to a Main Steam Turbine Control Valve and three remaining cap screws were loose, with one slightly bent. The faulty shutoff valve was replaced, properly torqued, and the EHC system was pressurized to verify it was free of leaks. The bolting torque was verified to be proper for all hydraulic shutoff valves for control valves, stop valves, and intermediate valves. The most probable cause for this event is inadequate work instructions that led to failure to install appropriate lock washers on the shutoff valve connection, resulting in cap screws becoming loose and ultimately failing due to fatigue. Corrective action includes correcting work instructions, initiating work orders to install lock washers on hydraulic shutoff valves, and ensuring the bill of materials in model work orders specifies the appropriate lock washers for the application.
4612013004 | Clinton 1 | 08/15/2013 | 10/11/2013 | ML13304A50 | <strong>Loss of Emergency Diesel Room Ventilation due to Damper Hydramotor Failure</strong><br /><i>Abstract:&nbsp;</i>On 8/15/13, maintenance personnel were performing planned performance testing of the Division 3 Emergency Diesel Generator (EDG) Room Ventilation System and noticed the supply air damper did not open when the EDG room ventilation fan started, and noticed the flow data results were not consistent with previous testing data. The damper is required to stroke to full open and then modulate with the fan running if supply air temperature is above 70 degrees. Operators restarted the fan with the temperature controller set at 70 degrees and actual air temperature reading 84 degrees, but the damper again failed to open. Operators immediately declared the Division 3 EDG and the supported High Pressure Core Spray System inoperable based on low confidence that the ventilation system was capable of controlling EDG room temperature to support the EDG mission time and entered the required Technical Specification actions. Troubleshooting found that the internal hydraulic pump in the dampers hydramotor had failed. The cause of this event is that the damper hydramotor experienced an end-of-life failure due to being installed beyond its recommended service life. Corrective actions include replacing the hydramotor that failed and identifying the extent of hydramotors installed beyond the recommended life and replacing them.
4612013005 | Clinton 1 | 09/20/2013 | 11/18/2013 | ML13338A58 | <strong>Safe Shutdown Analysis Noncompliance for Diesel Generator Room Ventilation</strong><br /><i>Abstract:&nbsp;</i>On September 20, 2013, a self assessment of the Clinton Power Station fire protection program identified a potential noncompliance with License Condition 2.F due to the inability to achieve safe shutdown in the event of a fire in Zones CB-1e, CB-1f, CB-2, and CB-4. Circuit failure analysis and post-fire recovery guidance for the Diesel Generator (DG) room ventilation system were found to be technically incorrect, rendering the DG room ventilation systems unable to be restored for certain fire scenarios that credit them. Fire-induced circuit failures could inadvertently actuate the DG carbon dioxide (CO2) fire suppression system, which send a maintained-trip signal to the associated DG room ventilation system. The Safe Shutdown Analysis for this scenario directs operators to restart the fans from the main control room (MCR). However, this action will not bypass the CO2 trip signal to the fans, thus the affected DG unit(s) may eventually fail due to high room temperatures. This condition is reportable under 10 CFR 50.73(a)(2)(ii)(B) as an unanalyzed condition that significantly degraded plant safety. The cause of this event was determined to be an historical error that occurred in 1998. Plant procedures have been revised to direct operators to remove a fuse located in a MCR panel to enable the trip logic to be bypassed should a fire occur outside the DG rooms.
4612013006 | Clinton 1 | 10/13/2013 | 12/11/2013 | ML13357A20 | <strong>Implementation of Enforcement Guidance Memorandum (EGM) 11-003, Revision 1</strong><br /><i>Abstract:&nbsp;</i>The condition reported by this LER is the result of planned activities in support of Refueling Outage C1R14 at Clinton Power Station (CPS). As described in the LER, the NRC provided enforcement guidance, applicable to boiling water reactor licensees, that allows the reported condition. Although this allowance is provided by the NRC's enforcement guidance, the planned activities are still considered reportable in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by Technical Specifications (TS). Between 10/13/2013 and 10/27/2013, CPS performed Operations With the Potential For Draining the Reactor Vessel (OPDRV) activities while in Mode 5 without an operable secondary containment, as expected and allowed by NRC Enforcement Guidance Memorandum (EGM) 11-003, Revision 1. The EGM allows the implementation of interim actions as an alternative to full compliance; however, this condition is still considered a condition prohibited by TS 3.6.4.1. The OPDRV activities were planned activities that were completed following the guidance of the EGM and are considered to have low safety significance based on interim actions taken. Since these actions were deliberate, no cause determination was necessary. A license amendment request will be submitted following NRC approval of the Technical Specifications Task Force traveler associated with generic resolution of this issue.
4612013007 | Clinton 1 | 10/28/2013 | 12/27/2013 | ML14008A11 | <strong>Failed to Enter Tech Spec Action for Exceeding Reactor Coolant Heatup Rate</strong><br /><i>Abstract:&nbsp;</i>On 10/28/13, reactor startup was in progress. At 2100 hours, reactor coolant temperature was 156 degrees Fahrenheit (F) and the reactor was at the point of adding heat. During this startup, the main steam isolation valves (MSIVs) could not be opened, as planned, due to the Main Steam Lines being full of water following the RPV pressure test and RPV temperature and pressure continued to rise. Operators attempted to slow the heatup by inserting a control rod, but were unsuccessful. At 2130 hours, the Shift Manager (SM) was notified of the heatup trend and that the reactor coolant temperature had increased by about 111 degrees F over a one-hour period. The SM determined the reactor pressure vessel (RPV) metal temperatures recorded on the log were still well under a rate of change of 100 degrees F per hour. The SM incorrectly applied the Technical Specification (TS) requirement for RPV coolant heatup as he applied this limit to the rate of change of metal temperatures. As a result, the TS required actions, including a requirement to complete a review for continued operation, were not entered or completed for exceeding the coolant heatup rate of 100 degrees F per hour. This error was identified on 11/1/13 during a review of the heatup logs. The cause of the failure to enter the appropriate TS was the SM did not reference the available guidance for acceptance criteria.
4612013008 | Clinton 1 | 12/08/2013 | 06/28/2016 | ML16188A19 | <strong>Failure of Division 1 Transformer Leads to Isolation of Instrument Air Supply to Containment, Lowering Scram Pilot Air Header Pressure, and Manual Reactor Scram</strong><br /><i>Abstract:&nbsp;</i>On 12/8/13 at 2026 hours with the plant in Mode 1 at 97.3 percent reactor power, operators received multiple alarms due to the trip of 4160 volt 1A1 breaker which resulted in a loss of power to two Division 1 480 volt unit substations. Operators were immediately dispatched and found a 4160/480 volt stepdown transformer failed. Many Division I components lost power. The loss of power caused an instrument air (IA) containment isolation. The loss of IA affected various containment loads, including the scram pilot air header, the main steam isolation valves and the reactor water cleanup system. At 2036 hours, the scram pilot air header low pressure alarm was received, and in response to an anticipated automatic reactor scram, operators immediately initiated a manual reactor scram. All control rods fully inserted into the core. Reactor pressure vessel water level dropped to the low reactor water level 3 setpoint (normal result of a scram from high power) and operators entered the Reactor Pressure Vessel Control Emergency Operating Procedure. The most probable cause of the transformer failure was a tum to turn failure of the high side windings due to insulation breakdown over time, prior to its expected end of life. An installed spare was connected to replace the failed Division 1 transformer.
4612013009 | Clinton 1 | 12/13/2013 | 02/10/2014 | ML14268A08 | <strong>Software Errors in New Digital Feedwater Control System Result in Manual Reactor Scram due to Approaching High Reactor Pressure Vessel Water Level Setpoint Setpoint</strong><br /><i>Abstract:&nbsp;</i>On 12/13/13 the plant was in Mode 1 at 18 percent reactor power with power ascension in progress. Operators were transitioning from the Motor Driven Reactor Feed Pump (MDRFP) to the 'A' Turbine Driven Reactor Feed Pump (TDRFP). Operators opened the 'A' TDRFP Discharge Valve and placed the 'A' TDRFP Recirculation Valve in Automatic, which positioned the recirculation valve to 25% open. When the `A' TDRFP began to feed, the MDRFP began to reduce flow as designed. Over the next few minutes, flow from the two feed pumps began to fluctuate, and reactor water level began to oscillate outside the normal control band. Operators recognized the level swings were growing in amplitude and took manual control of the MDRFP flow control valve (FCV). At this time, the speed of the 'A' TDRFP increased causing an increase in Reactor Water Level. As reactor water level approached the high Level 8 trip set point, operators placed the Reactor Mode Switch into the Shutdown position, initiating a manual scram. The cause for this event is errors in the recently installed digital feedwater control system software. The installed digital feedwater programming will be revised to correct the identified software errors. Interim actions were taken to revise operating procedures.
4822013001 | Wolf Creek | 01/11/2013 | 03/11/2013 | ML13079A26 | <strong>Broken Cylinder Head Stud Causes Inoperable Diesel Generator Longer than Technical Specification Completion Time</strong><br /><i>Abstract:&nbsp;</i>On January 8, 2013, at 0500 hours Central Standard Time (CST), Required Action B.4.1 of Technical Specification (TS) 3.8.1 was entered when the 'B' diesel generator (DG) was declared inoperable for performing voluntary preplanned maintenance activities. During the planned replacement of the o-ring between the cylinder head and valve housing on the number 7 cylinder, maintenance personnel contacted one of the eight cylinder head studs and identified that the stud was loose. The broken stud was removed by hand. On January 10, 2013, enforcement discretion was sought to permit noncompliance with TS 3.8.1, i.e., to permit additional time to complete repairs and restoration of the 'B' DG before a plant shutdown was required. An additional 96 hours was requested to restore the 'B' DG to operable status such that the Completion Time of Required Action B.4.1 would expire at 0500 hours CST on January 15, 2013. The NRC granted approval of the requested enforcement discretion on January 10, 2013. The replacement of the broken stud and two adjacent studs and testing to restore operability was completed at 2254 hours CST on January 12, 2013.
4822013002 | Wolf Creek | 02/04/2013 | 04/02/2013 | ML13101A33 | <strong>Pressure Boundary Leakage on a Seal Water Injection Drain Line due to Low Stress High Cycle Fatigue</strong><br /><i>Abstract:&nbsp;</i>On February 4, 2013, during the Reactor Coolant System (RCS) pressure boundary integrity walk down, an active through-wall leak was discovered in the pipe-to-valve circumferential butt weld upstream of valve BBV0130, reactor coolant pump 'A' seal water injection drain line. Leakage at this location is considered not isolable from the RCS, and is considered RCS pressure boundary leakage, which exceeds the limit of "No Pressure Boundary Leakage" defined by Technical Specification (TS) 3.4.13. At 1340 Central Standard Time (CST) on February 4, 2013, Limiting Condition of Operation 3.4.13 was declared not met and Condition B entered. The unit was in Mode 4 at the time of entry into Condition B, as such, the unit was required to be in Mode 5 by 0140 CST on February 6, 2013. The unit entered Mode 5 on February 4, 2013 at 1815 CST. <br /><br /> The cause of leakage was determined to be low stress high cycle fatigue. The drain valve and pipe were replaced on March 11, 2013.
4822013003 | Wolf Creek | 02/16/2013 | 04/15/2013 | ML13114A15 | <strong>Movement of Irradiated Fuel Progressed after Non-Conservative Decision Making Resulted in Removal of One Source Range Monitor from Service</strong><br /><i>Abstract:&nbsp;</i>At 1500 hours Central Standard Time on February 16, 2013, Limiting Condition for Operation (LCO) 3.9.3 was declared not met when it was determined that the source range monitors SENI0060A and SENI0061A were not both coupled to the core and source range neutron flux monitor SENI0031 was inoperable. On February 15, 2013, fuel offload had been delayed for approximately the previous 48 hours with 85 of 193 fuel assemblies offloaded. On February 15, 2013, at 2134 hours, SENI0031 was declared inoperable for performance of maintenance activities. On February 16, 2013, fuel offload occurred from 0426 hours to 0933 hours and 1137 hours to 1500 hours.<br><br> Condition A of Technical Specification 3.9.3 was entered and core alterations were suspended and operations that would cause positive reactivity additions were suspended per Required Action A.1 and Required Action A.2. On February 16, 2013, at 1620 hours, cabinet SE054A and monitor SENI0031 were returned to service. At 1633 hours, fuel offload was recommenced. The cause of the event was non-conservative decision making by an Instrument and Control Supervisor and the Work Controls Senior Reactor Operator to perform work on nuclear instrumentation cabinet SE054A and source range monitor SENI031 when fuel offload had not been completed.
4822013004 | Wolf Creek | 03/08/2013 | 05/03/2013 | ML13137A04 | <strong>Torque Requirement Human Performance Issue Caused Nonfunctional Class 1E Electrical Equipment Air Condition Unit and an Inoperable Control Room Air Conditioning Unit</strong><br /><i>Abstract:&nbsp;</i>On 03/08/2013, Wolf Creek Generating Station was in Refueling Outage 19 with the core defueled and no movement of irradiated fuel assemblies. During replacement of the SGK05A Class 1E electrical equipment air conditioning compressor, it was discovered that the compressor terminal box mounting screws were over torqued to 50 inch pounds. A work history review determined that SGK05B and the SGK04B control room air conditioning compressor also had over torqued mounting screws. SGK04A was unaffected as no maintenance had been performed on the compressor terminal box that specified torque requirements for the mounting screws. As a result, it was determined that SGK05B had been nonfunctional and SGK04B had been inoperable during the previous cycle. This resulted in a condition prohibited by Technical Specification and a condition that could have prevented the fulfillment of a safety function.<br><br> The mounting screws were replaced with safety related screws and torqued to the proper value.
4822013005 | Wolf Creek | 03/13/2013 | 05/13/2013 | ML13142A19 | <strong>Fatigue Failure of Jacket Water Pressure Switch Diaphragm Results in Loss of the 'B' Diesel Generator</strong><br /><i>Abstract:&nbsp;</i>At 0134 Central Daylight Time (CDT) on 03/13/2013, Control Room annunciators 23B, "DG NE02 UV or UF," and 23D, "DG NE02 Trouble," were received for the 'B' diesel generator (DG). At 0149 CDT on 3/13/2013 the Shift Manager declared a Notification of Unusual Event (NUE) for Loss of Electrical Power/Assessment Capability, as both DGs were not available. At the time of the event, the reactor vessel was defueled with all fuel located in the spent fuel pool. The 'A' DG was out of service for maintenance. Power to the safety related busses were being supplied from the offsite power sources.<br><br> The cause of the event was failure of the 'B' DG Jacket Water Pressure Switch (KJPS0162) due to water intrusion in the electrical portion of the switch. Excessive pressure oscillations in the jacket water pressure sensing line led to high cycle fatigue failure of the KJPS0162 diaphragm. The pressure switch was replaced.<br><br> The 'B' DG was returned to service at 0221 CDT on 03/14/2013. The NUE was terminated at 0239 CDT on 03/14/2013.
4822013006 | Wolf Creek | 05/07/2013 | 08/14/2013 | ML13232A01 | <strong>Technical Specification Required Shutdown Due to a Nonfunctional Class 1 E Electrical Equipment Air Conditioning Unit</strong><br /><i>Abstract:&nbsp;</i>On May 6, 2013 at 1733 Central Daylight Time (CDT), the Class 1E electrical equipment air conditioning unit, SGKO5A, was declared nonfunctional due to an increasing temperature trend in the 'A' train safety related electrical equipment room. As a result, Technical Specification Limiting Condition for Operation 3.0.3 was entered and a plant shutdown was commenced. Wolf Creek Generating Station (WCGS) entered Mode 3 on May 7, 2013 at 0009 CDT. <br /><br /> Damage to the liquid line filter drier assembly was caused by over tightening of the wing screw that holds the assembly together. This caused the partial blockage of the thermostatic expansion valves feeding the SGKO5A evaporator coils resulting in the temperature increase in the 'A' train safety related electrical equipment room. <br /><br /> The thermostatic expansion valves and filter drier assembly were replaced and WCGS returned to Mode 1 on 5/13/2013 at 0832 CDT.
4822013007 | Wolf Creek | 06/17/2013 | 11/14/2013 | ML13329A34 | <strong>Nonfunctional Class 1E Electrical Equipment Air Conditioning Unit Results in Longer than Technical Specification Completion Time</strong><br /><i>Abstract:&nbsp;</i>On June 17, 2013 at 1111 Central Daylight Time (CDT), the Class 1E electrical equipment air conditioning unit, SGK05A, was declared nonfunctional due to an analysis of an oil sample that showed elevated levels of aluminum. As a result, Technical Specification (TS) Limiting Condition for Operation (LCO) 3.0.3 was entered and a plant shutdown was commenced.<br /><br /> On June 17, 2013, enforcement discretion was sought to permit noncompliance with TS 3.8.4, TS 3.8.7, TS 3.8.9, as well as LCO 3.0.3, to permit additional time to complete repairs and restoration of SGK05A before a plant shutdown would be required. An additional 168 hours was requested to restore SGK05A to a functional status such that the Completion Time of LCO 3.0.3 would expire at 1111 CDT on June 24, 2013. The Nuclear Regulatory Commission granted approval of the requested enforcement discretion on June 17, 2013. The replacement of the SGK05A compressor and testing to restore functionality was completed at 2220 CDT on June 21, 2013.
4822013008 | Wolf Creek | 09/11/2013 | 11/12/2013 | ML13323A51 | <strong>Technical Specification Required Shutdown due to a Nonfunctional Class 1E Electrical Equipment Air Conditioning Unit</strong><br /><i>Abstract:&nbsp;</i>On September 11, 2013 at 1645 Central Daylight Time (CDT), the Class 1E electrical equipment air conditioning unit, SGK05A, was declared nonfunctional due to low oil level on the SGK05A compressor, elevated vibration and an increase in motor current. As a result, Technical Specification (TS) Limiting Condition for Operation (LCO) 3.0.3 was entered and a plant shutdown was commenced. Mode 3 was entered on September 11, 2013 at 2312 CDT.<br /><br /> Following the plant shutdown, while in Mode 3, the 'A' steam generator (SG) level approached the Auxiliary Feedwater Actuation Signal setpoint of 23.5 % level. The Control Room operators initiated a manual reactor trip. As a result of the trip, a feedwater isolation signal and a motordriven auxiliary feedwater actuation signal was generated.<br /><br /> The cause of the SGK05A failure was an inadequate flush and restoration of the system following actions taken to restore SGK05A in May 2013. The cause of the manual reactor trip and auxiliary feedwater actuation was the lack of crew proficiency to maintain SG levels in Mode 3, immediately following a rapid shutdown.
4822013009 | Wolf Creek | 10/09/2013 | 12/05/2013 | ML13350A14 | <strong>Post-Fire Safe Shutdown Design Issue May Impact Ability to Achieve Safe Shutdown</strong><br /><i>Abstract:&nbsp;</i>On October 9, 2013 during a review of external operating experience, Wolf Creek Nuclear Operating Corporation (WCNOC) determined that a fire in some areas containing direct current (DC) ammeter circuits could result in secondary fires outside the primary fire area. This condition could impact the ability to achieve safe shutdown. The cause of this deficiency is that the original plant design did not specify fuse protection of these DC shunt ammeter circuits. The postulated scenario is a fire that causes a short to ground on cables associated with the DC ammeters, concurrent with a short to ground on a safety related 125 VDC circuit on the negative side of the same battery source. Since the ammeter circuits are not overcurrent protected, they could overheat and ignite anywhere along their route. The negative side of the 125 VDC circuit is fuse protected, but the fuse may not clear prior to ammeter cable ignition if a high resistance short to ground exists. <br /><br /> The safety significance of this event is considered low. An hourly fire watch was established in the affected areas. A modification will be implemented to correct this deficiency
4822013010 | Wolf Creek | 10/18/2013 | 12/17/2013 | ML13358A23 | <strong>Technical Specification Required Shutdown due to a Nonfunctional Class 1E Electrical Equipment Air Conditioning Unit Caused by Foreign Material</strong><br /><i>Abstract:&nbsp;</i>On October 18, 2013 at 1141 Central Daylight Time (CDT), the Class 1E electrical equipment air conditioning unit, SGK05A, was declared nonfunctional due to low lube oil pressure on the SGK05A compressor. As a result, Technical Specification (TS) Limiting Condition for Operation (LCO) 3.0.3 was entered and a plant shutdown was commenced. Mode 3 was entered on October 18, 2013 at 1735 CDT.<br /><br /> The cause of the SGK05A failure was a loss of lube oil pressure sensing to the pressure switch of the SGK05A compressor. Contaminates in the system caused the loss of lube oil pressure sensing to the pressure switch. An inadequate flush and restoration of the system in May 2013 allowed contaminates to remain in the system.<br /><br /> SGK05A was returned to a functional status on October 21, 2013 at 1915 CDT. Wolf Creek Generating Station returned to Mode 1 on October 27, 2013 at 2007 CDT.
4832013001 | Callaway | 12/17/2012 | 02/15/2013 | ML13050A21 | <strong>Violation of Technical Specification 3.0.3 due to a Class 1E Electrical Equipment A/C Unit lnoperability</strong><br /><i>Abstract:&nbsp;</i>On 14:35 on 12/17/2012, the A Class lE electrical equipment air conditioning unit (SGK05A) was declared inoperable due to identification of Freon leakage from the unit's low oil pressure and compressor discharge sensing lines. Following repair to address the leakage, the unit was declared operable at 11:08 on 12/18/2012. The SGK05A unit provides a support function for the A train of Class 1E electrical equipment. The Class 1E electrical equipment is addressed in the plant's Technical Specifications. Since the leakage for SGK05A had apparently existed prior to the time of discovery, it was concluded that SGK05A and the supported Class 1E electrical equipment had been inoperable for a period of time longer than the allowed by the plant Technical Specifications. The leakage was the result of two sensing lines rubbing together. The Root Cause was determined to be an inadequate scope of previously conducted equipment reliability evaluations on the HVAC system. The leaks were repaired. In addition, preventive maintenance and monitoring of vibration-susceptible Class 1E electrical equipment air-conditioners will be increased.
4832013002 | Callaway | 02/13/2013 | 06/17/2013 | ML13169A09 | <strong>Degraded Bearing on 'B' Essential Service Water Pump Motor</strong><br /><i>Abstract:&nbsp;</i>On 2/13/2013, during surveillance testing of the 'B' Train of the ESW system, an Operations Technician noticed that the oil in the sight glass of the lower motor radial bearing appeared darker than normal. Based on analysis of the oil, the 'B' ESW pump was declared inoperable on 2/14/2013 at 0721. Required Action A.1 of TS 3.7.8 was entered. Following replacement of the pump motor due to evidence of a degraded bearing, the 'B' ESW train was restored to operable status at 1345 on 2/16/2013 such that Required Action A.1 was exited after a period of 54 hours and 24 minutes. Based on a conservative evaluation of past operability, it is estimated that the 'B' ESW pump motor would not have been capable of meeting its Operability mission time of 30 days after the August to October 2012 timeframe; therefore, this condition is currently considered reportable. This determination is based on the presence of metallic contaminants found in the oil and on recently increased motor vibration, which are indicative of bearing degradation. <br><br> The direct cause is insufficient motor shaft endplay, resulting in lower bearing failure due to excessive axial loading. <br><br> Corrective actions include establishing new preventive maintenance overhaul requirements and establishing new motor shaft endplay settings.
4832013003 | Callaway | 03/23/2013 | 05/21/2013 | ML13142A44 | <strong>Inoperability of CREVS 'B' train</strong><br /><i>Abstract:&nbsp;</i>On 3/23/2013, the filtration fan associated with train 'B' of the Control Room Emergency Ventilation System (CREVS) tripped on thermal overload during restoration from surveillance testing. This occurred approximately 22 minutes after the fan was started. Based on this trip, the CREVS 'B' train was declared inoperable on 3/23/2013 at 2243. Required Action A of TS 3.7.10 was entered, and following replacement of the motor starter, the CREVS 'B' train was restored to operable status on 3/26/2013 at 0659.<br><br> Due to evidence of a loose connection and arcing at the termination for the 'C' phase of the filtration fan's starter, it was determined from this as-found condition that the CREVS 'B' train would not have been capable of meeting its Operability mission time of 30 days after 2/11/2013; therefore, this condition is considered reportable. This determination is based on the conclusion that the connection loosened slowly over time. A successful run of the fan on 2/11/2013 (without tripping) indicates that as of 2/11/2013, the connection had not loosened sufficiently to trip the fan on thermal overload.<br><br> The most probable cause of failure is tripping on thermal overload, due to a high resistance connection on the fan's starter.<br><br> Preliminary corrective actions include periodically checking the tightness of termination screws and inspecting for signs of overheating, for similar starters.
4832013004 | Callaway | 04/18/2013 | 06/17/2013 | ML13168A58 | <strong>Control Building Envelope (CBE) Boundary Door Open During Movement Of Irradiated Fuel Assemblies</strong><br /><i>Abstract:&nbsp;</i>On 04/18/2013, a small fire occurred at the Unit Auxiliary Transformer which caused a loss of all non-vital power to the plant during core offload. At this point in the core offload, a fuel assembly was suspended in the spent fuel pool due to a torn grid strap. The assembly was considered to be in movement since the assembly was not in a approved storage location. As a result of the loss of power, it was desired to restore temporary power to the 'B' train battery chargers to prevent loss (discharge) of the NK02 and/or NK04 batteries. Temporary power cables were routed through three doors in the Control Building, one of which was a Control Building Envelope (CBE) pressure boundary door. With cables running through the CBE door, mitigating actions were taken to seal the opening. Such mitigating actions are allowed in Modes 1-4 per Technical Specification (TS) 3.7.10, when Condition B applies for an inoperable CBE boundary. However, allowances for mitigating actions are not permitted for an inoperable boundary during the movement of irradiated fuel assemblies. For this situation, TS 3.7.10 Condition E applies, and its Required Actions are to immediately suspend CORE ALTERATIONS (E.1) and movement of irradiated fuel assemblies (E.2). The Control Room did not immediately recognize that Required Action E.2 was in effect; therefore, there was a delay in beginning this Action of approximately 2 hours and 24 minutes. Required Action E.2 was not met since the Action was not taken without delay.
4832013005 | Callaway | 04/04/2013 | 06/03/2013 | ML13155A23 | <strong>Inoperability of ESW Cross Connect Valve</strong><br /><i>Abstract:&nbsp;</i>On 4/4/2013, during leak testing of a Service Water to Essential Service Water cross-connect valve, leakage in excess of 10 gpm was identified. Actions to further quantify the leakage rate and determine the cause of leakage found that the motor-operated valve (MOV) actuator coupling had become decoupled from the valve stem. Based on this finding, this valve was declared inoperable on 4/7/2013 at 20:46. Required actions B.1 and B.2 of Technical Specification 3.7.9 were entered. Repair of the valve was completed on 4/8/2013 at 0445.<br><br> After review of data from MOV testing on this valve, including a subsequent uncoupled test, it is estimated that the decoupled actuator condition could have existed for a significant period of time prior to discovery, possibly since 4/2/2012 when a leak check test performed on the valve identified zero leakage. Therefore, this condition is considered reportable.<br><br> The most probable cause is that bolts used to fasten the coupling block to the valve stem gradually loosened with the passage of time and from environmental effects, such as vibration and heating and cooling cycles.<br><br> Corrective actions include adding a periodic check of MOV valve shaft coupling block bolt torque to the periodic preventive maintenance performed on this and the other three cross-connect valves.
4832013006 | Callaway | 05/08/2013 | 07/03/2013 | ML13189A26 | <strong>Degradation of Safety Injection Accumulator Vent Line</strong><br /><i>Abstract:&nbsp;</i>On May 8, 2013, during Refueling Outage 19, water was observed dripping from the insulation on piping connected to Reactor Coolant System (RCS) loop 4. Further investigation determined it was near a 3/4-inch ASME Code Class 2 line upstream of Safety Injection (EP) system valve EPV0109. The 3/4-inch vent line is located on the combined Safety Injection / Residual Heat Removal outlet piping which connects to the cold leg injection piping from Accumulator Tank D. <br><br> The RCS leakage identified at the noted location was indicative of degradation of a principal safety barrier and is considered reportable per the requirements of 10 CFR 50.73(a)(2)(ii)(A). Conditions that represent welding or material defects in the primary coolant system which cannot be found acceptable under ASME Section XI standards are reportable to this criterion. <br><br> The cracked vent line was removed and repaired on May 10, 2013. The completed weld repair was inspected and found acceptable. <br><br> An evaluation concluded that the leak was caused by induced cyclic fatigue crack at the socket weld upstream of valve EPV0109. <br><br> The safety significance of this event is low. The RCS leakage that resulted from the cracked vent line was well within the capability of the normal charging pump.
4832013007 | Callaway | 05/19/2013 | 07/23/2013 | ML13205A15 | <strong>Violation of TS 3.8.1 Due To An Inoperable Offsite AC Electrical Power Source</strong><br /><i>Abstract:&nbsp;</i>On 05/28/2013, oil was observed leaking from a 345-kV bushing on the Startup Transformer (XMR01) while the plant was in Mode 1. The leakage was addressed by tightening the bushing oil fill cap, and the Startup Transformer was declared operable on 05/30/2013 at 1648. <br><br> The Startup Transformer is part of one qualified preferred source of offsite AC power to the Class 1E buses, as required by the plant's Technical Specifications. Investigation determined that the oil leak on the Startup Transformer was determined to have existed from a certain point in time prior to the time of discovery and that the Startup Transformer would not have been capable of meeting its Operability mission time of 30 days while the oil leak existed. Consequently, it was concluded that the transformer had been inoperable for a period of time longer than allowed by the plant's Technical Specifications. <br><br> The cause of this event was a human performance error which occurred during a maintenance activity on the Startup Transformer during Refueling Outage 19. Work instructions will be revised to provide photos and additional instruction on which components to loosen when power factor testing the Startup Transformer.
4832013008 | Callaway | 07/26/2013 | 09/24/2013 | ML13268A11 | <strong>Arcing in isophase bus results in a generator trip, turbine trip, reactor trip and small fire</strong><br /><i>Abstract:&nbsp;</i>At approximately 2333 on July 26, 2013, electrical faults caused damage to the isophase bus to the unit auxiliary transformer and main generator neutral connection box. Protective relaying initiated a generator trip to isolate the faulted area and to trip the main turbine. A reactor trip from 100% power resulted from the turbine trip. A small cable insulation and oil collection pan fire initiated from the main generator neutral connection box fault and created smoke throughout the Turbine Building. An Unusual Event was declared as a result of the fire and resulting smoke.<br /><br /> The fire was extinguished within 30 minutes and smoke was removed from the building using installed equipment.<br /><br /> The electrical faults were the result of a damper blade that was loose within the isophase bus ductwork, creating arcing between the bus, damper blade, and duct. The loose damper blade is attributed to damper failure based on the determination that the operational isophase bus duct airflow rate exceeded the design flow rate for the backdraft dampers. Design and installation errors were made at the main generator neutral connection box during plant construction.<br /><br /> Redesigned backdraft dampers were installed, and grating was added to prevent debris from entering the isophase bus ducts. Modifications were also made to the generator neutral connection box.
4832013009 | Callaway | 10/09/2013 | 12/09/2013 | ML13345A10 | <strong>Appendix R Unanalyzed Condition - Direct Current Ammeter Circuits without Overcurrent Protection</strong><br /><i>Abstract:&nbsp;</i>On October 9, 2013, during a review of industry operating experience, Callaway Plant Engineering determined an unanalyzed condition exists related to Control Room fire analysis requirements (10 CFR 50 Appendix R). The original plant wiring design and associated analysis for the Class 1E Train B batteries and chargers (including the B swing charger) do not include overcurrent protection features to limit the fault current. It was identified that a postulated fire in the Control Room could cause a ground loop through unprotected (unfused) Direct Current (DC) ammeter wiring and potentially result in excessive current flow and heating to the point of causing a secondary fire outside of the Control Room in cable raceways. The postulated secondary fire could affect safe shutdown equipment and potentially cause the loss of ability to conduct a safe shutdown. This scenario has not been analyzed in accordance with 10 CFR 50 Appendix R, Section III.G. Compensatory fire watch measures have been implemented and remain in place for the affected fire areas in the plant.<br /><br /> The cause is that the original design of the DC ammeter circuits did not include fuses to protect ammeter cables. This design has been in place since construction and has only recently been identified as an issue based on testing sponsored by the NRC in 2011 and reported in NUREG/CR-7100. The NRC has been developing new guidance for addressing hot short issues within the same cable tray. Once this document is available for review, Callaway will determine if the use of Fire PRA is permitted to evaluate the issue and either leave the circuits as built or modify the affected circuits (to provide circuit protection) as necessary.
4982013001 | South Texas 1 | 04/17/2013 | 08/15/2013 | ML13248A45 | <strong>Delta Temperature / T-Average Channel A Inoperable for Longer than Allowed by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On May 1, 2013, during performance of a routine surveillance, maintenance personnel determined that the Channel A Overpower Delta Temperature (OPDT) reactor trip setpoint Delta-Flux Penalty summing amplifier (NSA card) had failed low, effectively disabling the associated OPDT setpoint correction, which caused Delta Temperature/T-Average Channel A to be inoperable. Further investigation determined that there was evidence that the failure occurred on April 17, 2013. Thus, the Delta Temperature/T-Average channel was inoperable for approximately fifteen days, which is longer than permitted by Technical Specifications 3.3.1 and 3.3.2. The failed circuit card replacement was completed on May 2, 2013 and after satisfactory surveillance testing on May 3, 2013, Delta-Temperature/T-Average Channel A was declared operable. <br /><br /> The risk significance of the event is considered very small. This event did not result in any offsite release of radioactivity or increase of offsite dose rates, and there were no personnel injuries or damage to any other safety-related equipment associated with this event. <br /><br /> The cause of the failure was determined to be random electronic component failure. Corrective actions will include revision to the channel check surveillance procedure to reduce the allowable acceptance criteria range for the OPDT setpoint.
4982013002 | South Texas 1 | 12/14/2012 | 07/29/2013 | ML13219B12 | <strong>Steam Turbine-Driven Auxiliary Feedwater (AFW) Pump Flow Regulating Valve Inoperable for Longer than Allowed by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On May 20, 2013 with Unit 1 in Mode 1 at 100 percent power, the auxiliary feedwater (AFW) flow loop 4 channel D high limit was found low out of tolerance during the performance of a scheduled surveillance. This condition resulted in the flow control valve for steam turbine-driven AFW pump not being capable of providing required flow to its respective steam generator under all accident conditions thus making the pump and flow regulating valve inoperable. Subsequently, it was determined that this condition had existed since December 14, 2012 during an earlier troubleshooting activity. The affected components were inoperable for a period longer than permitted by Technical Specifications. The steam turbine-driven AFW pump and flow regulating valve were restored to operable status on May 21, 2013. The overall AFW system safety function was met because multiple trains of AFW were available during this period. This condition was determined to be reportable on May 29, 2013. <br><br> The cause of this event was that procedures were not implemented properly due to unclear requirements. Corrective actions include clarification of procedure guidance. <br><br> The risk significance of the event is considered very small. This event did not result in any offsite release of radioactivity or increase in offsite dose rates. There were no personnel injuries or damage to any other safety-related equipment.
4982013003 | South Texas 1, South Texas 2 | 10/31/2013 | 12/23/2013 | ML14015A31 | <strong>Unanalyzed Condition - Direct Current Ammeter Circuits without Overcurrent Protection</strong><br /><i>Abstract:&nbsp;</i>On October 31, 2013, at approximately 1834 Central Daylight Time during review of industry operating experience, South Texas Project (STP) determined an unanalyzed condition exists related to the Control Room (CR) fire analysis. The original design of ammeter circuits which provide CR current indication for the non-Class 48 VDC battery and battery charger circuits and for the non-Class turbine lube oil emergency pump control circuit does not include overcurrent protection features to limit fault current. In the postulated event, a fire in the CR could cause a ground loop through unprotected ammeter wiring or control circuit wiring and potentially result in excessive current flow and heating to the point of causing a secondary fire outside the CR in the cable raceways. The postulated secondary fire could affect the availability of equipment needed to place the plant in a safe shutdown condition during a CR fire event. This scenario has not been analyzed in accordance with 10 CFR 50 Appendix R. Compensatory fire watch measures have been implemented and remain in place for the affected fire zones in the plant.<br /><br /> The cause was determined to be that the original design of the affected CR circuits did not adequately address fire protection program requirements. A design change is planned to correct the latent design deficiencies by providing circuit protection on affected CR circuits.
4992013001 | South Texas 2 | 01/04/2013 | 02/28/2013 | ML13072068 | <strong>Unit 2 Manual Reactor Trip due to Dropped Rods M8 and D8</strong><br /><i>Abstract:&nbsp;</i>At 07:05 on 1/4/2013, Unit 2, while at 100% power, commenced surveillances 0PSP03-RS-0004 and 0PSP03-RS-0001 to satisfy the monthly requirements of Technical Specification 4.1.3.1.2 and to demonstrate the shutdown and control rods are Operable by movement of at least 10 steps in any one direction. During testing, two rods on shutdown bank E (SBE) dropped to the bottom of the core and a manual reactor trip was required. The dropped rods on SBE occurred while inserting shutdown bank C (SBC) rods in 6 steps. After SBE rod M-8 dropped, rod motion was stopped. While validating the dropped rod, a second rod, D-8, in SBE dropped. At 09:41, once both dropped rods were validated by diverse indications of power, flux, and rod positions, a manual reactor trip was performed. Troubleshooting identified the problem as high resistance on Rod Holdout Mode Selector (RHMS) switch contacts in Rod Control Power Cabinet SCDE when the contacts should have been closed. This blocked the multiplexing signal to the SBE Stationary Regulation card resulting in dropped rods. This condition is considered reportable under 10 CFR 50.73(a)(2)(iv)(A), any event or condition that resulted in manual or automatic actuation of any of the systems listed in paragraph 10 CFR 50.73(a)(2)(iv)(B). There were no personnel injuries, no offsite radiological releases, and no damage to safety-related equipment associated with this condition. This condition did not have an adverse effect on the health and safety of the public.
4992013002 | South Texas 2 | 01/08/2013 | 06/03/2013 | ML13156A37 | <strong>Reactor Trip due to Main Transformer Lockout Relay Trip</strong><br /><i>Abstract:&nbsp;</i>On January 8, 2013, at 16:40 CST, with South Texas Project Unit 2 at 100% power, a fault in the 'C' phase of the Unit 2 2A Main Transformer (MT2A) occurred resulting in a Unit 2 automatic trip and partial loss of offsite power. Pressure from the fault ruptured the transformer tank and the oil ignited. The onsite fire brigade responded, and the fire suppression system worked as designed. The fire was extinguished at 16:56. There were no injuries and no radiological impacts to the public or station personnel.<br><br> An Unusual Event was declared at 16:55 CST for initiating condition HU-2, "Fire or explosion in protected area or switchyard which affects normal plant operations". Local, county, and state offices were notified as required, and the Unusual Event was terminated at 19:47 CST, after the partial loss of offsite power was restored.<br><br> Failure analysis concluded the most likely cause was an internal ground fault or an internal turn-to-turn fault inside the "C" phase high voltage windings due to untimely degradation of the paper insulation from the cumulative effects of passthrough faults, elevated temperatures, elevated moisture, and grid disturbances over a period of years. The damage to the transformer challenged a determination of the direct root cause of the fault. If warranted, the root cause report and LER will be revised after failure evaluation forensics are complete.<br><br> Corrective actions include replacement of MT2A with an on-hand spare, installation of wireless monitoring and notification features for the online dissolved gas monitors, approval for future replacement of all four main transformers with new units to support reliable operation through the end of the currently projected plant life, and implementation of a Large Equipment Asset Management process.
4992013003 | South Texas 2 | 01/07/2013 | 05/13/2013 | ML13141A28 | <strong>Operational Mode Change Prohibited by Limiting Condition for Operation 3.0.4 with Limiting Conditions for Operation Unknowingly Not Met for Inoperable Essential Cooling Water Pump</strong><br /><i>Abstract:&nbsp;</i>With Essential Cooling Water (ECW) Pump 2B unknowingly inoperable, the plant staff was unaware that the associated Limiting Conditions of Operation (LCO) were not met when Unit 2 reached greater than 5% rated thermal power and entered Mode 1 on 01/07/2013 at 0053, in violation of LCO 3.0.4. This event is considered reportable under 10 CFR 50.73(a)(2)(i)(B).<br><br> On 01/06/2013 at 2100, just prior to the mode change, a temperature excursion began on the ECW Pump 2B lower motor bearing, which peaked below the alarm setpoint before returning to normal by 01/07/2013 at 0125. This excursion was identified on 01/14/2013. Analysis of subsequent vibration data indicated a bearing defect with a step increase in vibration data. Without reasonable assurance that the pump would meet its mission time, ECW Pump 2B was declared inoperable on 01/15/2013 at 1200. Due to lack of any other abnormal temperature or vibration data available for the degraded condition, the pump is considered to have been inoperable since the start of the temperature excursion.<br><br> The bearing degradation was due to insufficient tolerance in the motor shaft endplay, as set during refurbishment. Corrective actions are planned to specify this design parameter for subsequent refurbishments, and to increase endplay adjustment shim thickness in the affected ECW pump motors to reduce bearing wear.
4992013004 | South Texas 2 | 12/19/2013 | 03/20/2014 | ML14118A03 | <strong>Manual Actuation of Main Steam Isolation Valves that was Not Part of a Preplanned Sequence During Testing or Reactor Operation</strong><br /><i>Abstract:&nbsp;</i>On December 19, 2013, while in Mode 3 preparing the Unit 2 secondary plant for startup, conditions occurred where it became necessary to break vacuum on the main condenser. The Operator closed the Main Steam Isolation Valves (MSIVs) using the Main Steam Isolation Actuation switch due to the urgency to prevent damage to the main turbine.<br /><br /> This action constitutes a valid manual actuation of multiple MSIVs and is therefore reportable under 10 CFR 50.73(a)(2)(iv)(A).<br /><br /> The risk significance of the event is considered to be very small. This event did not result in any offsite release of radioactivity or increase the offsite dose rates, and there were no personal injuries or damage to any safety-related equipment associated with this event.<br /><br /> The cause of the event was unspecific guidance in the off normal procedure for secondary plant stabilization. The failure of the bearing oil lift piping placed the Control Room Staff in a situation that required prompt action to prevent equipment damage, and the Staff made a decision to use the MSI Actuation switch as a result of the unspecific written guidance to ensure MSIVs and Main Steam Isolation Bypass valves (MSIBs) are closed.<br /><br /> The corrective action will be to revise the off normal procedure for secondary plant stabilization to provide specific direction for the switches to use for closing the MSIVs.
5282013001 | Palo Verde 1, Palo Verde 2, Palo Verde 3 | 03/08/2013 | 05/07/2013 | ML13133A00 | <strong>Unanalyzed Condition due to Spent Fuel Pool Criticality Analysis of Record Not Updated for Power Uprate</strong><br /><i>Abstract:&nbsp;</i>On March 8, 2013, PVNGS engineering personnel determined that certain impacts to the spent fuel pool (SFP) criticality analysis of record (AOR) had not been considered as part of the project to perform a power uprate to 3990 MW thermal in 2003. The power uprate impacted the reactivity of fuel discharged to the SFP but the SFP criticality AOR was not revised to account for the increased fuel reactivity. Therefore, this condition is being reported as an unanalyzed condition in accordance with 10 CFR 50.73(a)(2)(ii)(B).<br><br> The cause was procedures and processes lacked adequate rigor to identify impacts to the SFP criticality AOR. Additionally, the impacts of power uprate relative to the SFP criticality AOR were not well known or understood by personnel involved.<br><br> As an interim corrective action, an administrative control was implemented to apply a burnup penalty to low margin fuel assemblies to ensure Technical Specification (TS) reactivity requirements are met under all conditions. Planned corrective actions will revise design change procedures to consider reactivity impacts on the SFP and will revise the SFP criticality AOR using updated methodology and input parameters.<br><br> No similar events have been reported to the NRC in the prior three years.
5282013002 | Palo Verde 1, Palo Verde 2 | 04/08/2013 | 06/07/2013 | ML13165A32 | <strong>Inoperable Systems due to Defective Relays Reported under Part 21</strong><br /><i>Abstract:&nbsp;</i>This LER reports the failure of components caused by a defect in ARD66OUR control relays reported by Westinghouse, pursuant to 10 CFR 21, on April 8, 2013. The defect resulted in the failure of five normally energized control relays at PVNGS in two different systems in Unit 1 and two different systems in Unit 2. The relays were used in normally energized applications which are de-energized to position associated components to support the related safety function. The relays failed to change state when de-energized during testing.<br><br> The five failed relays were replaced. The cause was a change in the manufacturing process that occurred in May 2008. The defect was exhibited only on relays that failed in the manner described in the Westinghouse Part 21 report. An extensive testing program was completed to identify and replace ARD66OUR relays installed at PVNGS that exhibited the described failure mode. Westinghouse has modified the ARD66OUR relay plastic molding process to preclude this described failure mode. LER 05000529 / 2009-002-00 reported ARD66OUR relay failures that exhibited a similar failure mode.
5282013003 | Palo Verde 1, Palo Verde 2, Palo Verde 3 | 10/04/2013 | 12/03/2013 | ML13339A74 | <strong>Appendix R Unanalyzed Condition - Direct Current Ammeter Circuits without Overcurrent Protection</strong><br /><i>Abstract:&nbsp;</i>On October 04, 2013, at approximately 0946 Mountain Standard Time (MST), during review of industry operating experience, PVNGS engineering personnel determined an unanalyzed condition exists related to the Control Room (CR) fire analysis. The original design of ammeter circuits which provide CR current indication for the train B and D class 1E batteries and battery chargers does not include overcurrent protection features to limit fault current. In the postulated event, a fire in the CR could cause a ground loop through unprotected ammeter wiring and potentially result in excessive current flow and heating to the point of causing a secondary fire outside the CR in the cable raceways. The postulated secondary fire could affect the availability of equipment needed to place the plant in a safe shutdown condition during a CR fire event. This scenario has not been analyzed in accordance with 10 CFR 50 Appendix R, Section III.G. Compensatory fire watch measures have been implemented and remain in place for the affected fire zones in the plant.<br /><br /> The cause was determined to be that the original design of the DC ammeter circuits did not adequately address fire protection program requirements. A design change is planned to correct the latent design deficiencies by providing circuit protection on affected CR ammeter circuits.<br /><br /> No similar events have been reported to the NRC by PVNGS in the prior three years.
5282013004 | Palo Verde 1 | 11/06/2013 | 06/09/2014 | ML14163A52 | <strong>Condition Prohibited by Technical Specification 3.7.2 Due to an Inoperable Main Steam Isolation Valve (MSIV)</strong><br /><i>Abstract:&nbsp;</i>On April 10, 2014, a post-event review conducted in response to a proposed NRC non-cited violation concluded the actions to close and deactivate main steam isolation valve SGE-UV-170 (MSIV-170) to address an equipment malfunction on November 6, 2013, did not meet the operability requirements of Technical Specification (TS) Limiting Condition for Operation (LCO) 3.7.2. As a result, the requirement of LCO 3.7.2 Condition G to place the unit in Mode 2 within 6 hours was not completed. MSIV-170 was repaired and returned to service on November 9, 2013. <br /><br /> An investigation determined the cause of the condition prohibited by TSs was the operability determination (OD) was overly focused on the ability of the MSIV to perform its specified safety function and did not adequately consider the definition of operability and compliance with the TS. To prevent recurrence, PVNGS OD guidance will be revised to explicitly require evaluation of applicable LCOs to ensure the OD technical conclusions support compliance with the LCOs. <br /><br /> No similar events have been reported to the NRC by PVNGS in the prior three years.
5292013001 | Palo Verde 2 | 01/16/2013 | 10/25/2013 | ML13304A50 | <strong>Condition Prohibited by Technical Specifications due to Emergency Diesel Generator Low Output Voltage</strong><br /><i>Abstract:&nbsp;</i>On January 16, 2013, during the conduct of monthly surveillance testing, the PVNGS Unit 2 train B emergency diesel generator (2B EDG) did not reach the required generator output voltage at startup. As a result, the 2B EDG was declared inoperable and Unit 2 entered LCO 3.8.1, Condition B.<br /><br /> The direct cause was failure of an operational amplifier on the instantaneous prepositioning (IPP) board used to provide the voltage setpoint to the 2B EDG automatic voltage regulator (AVR) during operation in the emergency mode. The IPP board was replaced on January 17, 2013, and post-maintenance testing was successfully completed. The 2B EDG was declared operable on January 18, 2013, and LCO 3.8.1, Condition B was exited. The root cause of this event was an inadequate preventive maintenance strategy for relay VR2 which resulted in degraded relay contact resistance that allowed a voltage transient to be seen on the operational amplifier on the IPP board. To prevent recurrence, a new preventive maintenance strategy for EDG voltage regulator components will be established.<br /><br /> In the past three years, PVNGS has not reported a similar event for the six EDGs at Palo Verde.
5292013002 | Palo Verde 2 | 12/02/2013 | 01/31/2014 | ML14035A21 | <strong>Automatic Actuation of Unit 2 Reactor Protection System Resulting from Reactor Coolant Pump Motor Trip</strong><br /><i>Abstract:&nbsp;</i>On December 2, 2013, Unit 2 was operating in Mode 1 at 100 percent power. At approximately 1758 Mountain Standard Time a reactor trip was automatically actuated when reactor coolant pump (RCP) 1A speed dropped below 95 percent of rated speed which generated low departure from nucleate boiling ratio and high local power density trips on all four channels of the plant protection system. The reactor trip was determined to be uncomplicated and the reactor trip procedure was implemented to stabilize the plant in Mode 3. Operations personnel subsequently determined the RCP 1A motor circuit breaker tripped on excessive phase differential current. <br /><br /> The probable cause of the RCP 1A motor circuit breaker trip was a high impedance fault within the C phase of the motor stator coil. The faulted RCP 1A motor was replaced with an on-site spare RCP motor and Unit 2 was returned to power operation on December 14, 2013. The faulted motor has been sent to an off-site facility for disassembly and root cause analysis. <br /><br /> No previous similar events involving an automatic RPS actuation due to a RCP motor failure have been reported to the NRC by PVNGS in the prior three years.
5302013001 | Palo Verde 3 | 10/07/2013 | 12/06/2013 | ML13350A01 | <strong>Leakage on Reactor Vessel Bottom-Mounted Instrumentation Nozzle 3</strong><br /><i>Abstract:&nbsp;</i>On October 6, 2013, during a scheduled visual examination of the 61 bottom-mounted instrument (BMI) nozzles on the Unit 3 reactor vessel, white residue was identified around the annulus region of BMI nozzle 3. At 0219 on October 7, 2013, engineering personnel determined, based on past and present photographic evidence, that the white residue likely resulted from reactor coolant system (RCS) pressure boundary leakage. The pressure boundary leakage resulted in a condition prohibited by Technical Specification 3.4.14, reportable pursuant to 10 CFR 50.73(a)(2)(i)(B), and a degraded principal safety barrier, reportable pursuant to 10 CFR 50.73(a)(2)(ii)(A). Non-destructive examination (NDE) of BMI nozzle 3 identified axial cracking in a near-surface weld flaw in the J-groove weld that extended into the nozzle tube and ultimately resulted in the RCS leak path. An extent of condition evaluation found no indication of unacceptable flaws or leakage in the remaining 60 BMI nozzle assemblies in Unit 3. Additionally, no evidence was found that indicated leakage from BMI nozzle assemblies in Units 1 or 2. <br /><br /> The probable cause of the BMI nozzle 3 leakage was a near-surface weld flaw that came in contact with RCS water and allowed initiation of primary water stress corrosion cracking. The flaw was likely caused by a BMI nozzle Jgroove weld defect that occurred during reactor vessel fabrication and was undetected by penetrant testing. An American Society of Mechanical Engineers Code approved weld pad/half-nozzle repair was performed to establish a new BMI nozzle assembly weld configuration. Corrective actions include increasing the frequency of BMI visual examinations so that one is performed each refueling outage. <br /><br /> No similar events have been reported to the NRC by PVNGS in the prior three years.
5302013002 | Palo Verde 3 | 12/03/2013 | 02/03/2014 | ML14038A07 | <strong>Condition Prohibited by Technical Specifications During Dropped Control Element Assembly Recovery</strong><br /><i>Abstract:&nbsp;</i>On December 03, 2013, at approximately 0130, Unit 3 was in Mode 1 at 40 percent power recovering from a dropped Control Element Assembly (CEA) when the Required Action Completion Times of Technical Specification (TS) Limiting Condition for Operation (LCO) 3.2.1, Linear Heat Rate (LHR), and TS LCO 3.2.4, Departure from Nucleate Boiling Ratio (DNBR), were exceeded. Condition C of both LCO 3.2.1 and LCO 3.2.4 requires power to be <br /> The cause of exceeding the required action completion times was the operating crew inappropriately exited LCO 3.2.1 and LCO 3.2.4 prior to fully understanding and reconciling instrument and alarm discrepancies. <br /><br /> Planned corrective actions will revise procedure 40DP-90P02 "Conduct of Shift Operations" to add guidance and actions for Operations personnel prior to exiting a LCO. The revised guidance will require independent review of decisions to exit LCOs. A case study of this event will be developed and presented to licensed operators and shift technical advisors during Licensed Operator Continuing Training. Also, procedure 40A0-9ZZ11 "CEA Malfunctions" will be revised to incorporate lessons learned from this event. <br /><br /> No similar events have been reported to the NRC by PVNGS in the prior three years.