## Sheet1
LER Number | Plant Name | Event Date | Report Date | Accession # | Title
2192014001 | Oyster Creek | 07/11/2014 | 09/08/2014 | ML14252A84 | <strong>Manual Scram due to Lowering Vacuum</strong><br /><i>Abstract:&nbsp;</i>On July 11, 2014 at approximately 0312 EDT, during planned reactor power ascension with reactor power at approximately 56% of rated thermal power, main condenser vacuum began to degrade. In accordance with the abnormal operating procedure for degrading vacuum, Operators inserted a manual scram of the reactor at 0314 EDT.<br /><br /> Following the reactor scram, operations and maintenance personnel identified an approximate 2"x6" hole and an approximate 2”x3” hole on the last convolute of the downstream side of Y-1-26 ('B' Condenser Steam Inlet Expansion Joint). It was confirmed to be an active leak and subsequently the source of condenser vacuum degradation. As a corrective action to this event, the expansion joint was replaced.<br /><br /> All control rods fully inserted and plant response was as expected. This event is being reported pursuant to 10CFR50.73(a)(2)(iv)(A) due to an actuation of the Reactor Protection System (RPS).
2192014002 | Oyster Creek | 08/25/2014 | 10/08/2014 | ML14302A07 | <strong>Technical Specification Prohibited Condition Caused by Two Electromatic Relief Valves Inoperable for Greater than Allowed Outage Time</strong><br /><i>Abstract:&nbsp;</i>On June 20, 2014, during as-found testing of the Electromatic Relief Valve (EMRV) actuators removed from the plant in October 2012 during the 1R24 refueling outage, two ('B" and "D") of five EMRV actuators failed to operate. Subsequent inspection of these actuators found wear of the posts, springs and guides.<br /><br /> On August 25, 2014 the Root Cause Evaluation was completed and determined the most probable time of failure of the "B" and 'D" EMRVs was between July 27, 2012 and October 22, 2012. These dates are based on July 27th being the last known date that the "D" EMRV functioned and October 22 being the beginning of the refueling outage. Based on these dates, it is suspected that two of the five EMRVs would have been inoperable for longer than the Technical Specification Allowed Out of Service Time of 24 hours.<br /><br /> Therefore, this issue Is reportable under 10 CFR 50.73(a)(2)(i)(B) as an Operation or Condition which was Prohibited by the plant's Technical Specifications. Additionally, this report constitutes a Part 21 notification per 10 CFR 21.21(d)(3)(ii), previously reported via ENS 50495 on September 25, 2014.
2192014003 | Oyster Creek | 09/12/2014 | 12/01/2015 | ML15344A16 | <strong>Technical Specification Prohibited Condition Caused by Emergency Diesel Generator Inoperable for Greater than Allowed Outage Time</strong><br /><i>Abstract:&nbsp;</i>On July 28, 2014, Emergency Diesel Generator No. 2 (EDG-2) was being operated for its bi-weekly one-hour load test run, when alarms "EDG 2 ENGINE TEMP HI" and "EDG 2 DISABLED" were received. Operations manually shut down EDG-2 due to an apparent cooling problem with the diesel engine. During initial troubleshooting, the fan duct was opened to access the upper fan shaft and it was found that the cooling fan shaft had failed. Without the fan in service, radiator heat transfer performance was degraded, leading to high jacket water (coolant) temperatures and associated alarms. <br /><br /> On September 12, 2014, an Equipment Apparent Cause Evaluation (EACE) for the fan shaft failure was completed. The EACE determined that the remaining shaft life would have met the 24-hour mission time anytime during or just prior to the June 16, 2014 load test. Based on this conclusion, EDG-2 would not have been able to meet its mission time of 24 hours for 43 days, which is greater than the Technical Specifications (TS) Allowed Out of Service Time (AOT) of seven days. <br /><br /> Therefore, this issue is reportable under 10 CFR 50.73(a)(2)(i)(B) as an Operation or Condition which was Prohibited by the plant's Technical Specifications.
2192014004 | Oyster Creek | 09/18/2014 | 11/17/2014 | ML14332A09 | <strong>Local Leak Rate Test Results in Excess of Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On September 18, 2014, during refueling outage O1R25 with the unit in cold shutdown, plant personnel performed local leak rate testing (LLRT) of the Main Steam Isolation Valves (MSIVs). During the testing, it was identified that the "B" main steam line inboard isolation valve NS03B (V-1-8) exceeded the leakage rate limits allowed by the plant's Technical Specifications.<br /><br /> The MSIV (V-1-8) that exhibited excessive leakage was repaired and the as-left leakage rate was verified to be within Technical Specifications leakage limits.<br /><br /> This issue is reportable under 10 CFR 50.73(a)(2)(i)(B) as a condition which was prohibited by the plant's Technical Specifications.
2192014005 | Oyster Creek | 09/19/2014 | 08/11/2015 | ML15239A75 | <strong>Secondary Containment Declared inoperable</strong><br /><i>Abstract:&nbsp;</i>On September 19, 2014, during refueling outage O1R26 with the unit in cold shutdown, a technician discovered that a previously authorized and installed Temporary Configuration Change (TCC) had been removed from a penetration in the Outboard Main Steam Isolation Valve Room (Trunnion Room). The purpose of the TCC is to isolate the penetration from the Reactor Building (RB) to the Trunnion Room to allow the RB Trunnion Room door to be maintained open during refueling outages. Per Technical Specifications (TS) 3.5.B and 4.5.G, in order to maintain secondary containment integrity with the Trunnion Room door open, four penetrations connecting the Trunnion Room to the RB must be seated. The Trunnion Room door was open when the plug was found removed from a 6" equipment drain hub. The plug was immediately reinstalled. On September 20, 2014, the Post Maintenance Testing (PMT) for the TCC reinstallation was executed in order to declare secondary containment operable. This PMT revealed that the Standby Gas Treatment System (SBGTS) could not achieve the required minimum differential pressure of -0.25" water vacuum on the RB. The cause was determined to be an improperly latched personnel access hatch on the Outer Reactor Building Airlock Door. <br /><br /> ENS 50476 was submitted on September 20, 2014. This issue is reportable under 10 CFR 50.73(a)(2)(v)(C) as an event that could have prevented the fulfillment of the safety function of a system needed to control the release of radioactive material, and 10 CFR 50.73(a)(2)(i)(B) as a condition which was prohibited by the plant's Technical Specifications.
2192014006 | Oyster Creek | 10/12/2014 | 08/11/2015 | ML15251A20 | <strong>Reactor Scram due to Decreasing Reactor Water Level</strong><br /><i>Abstract:&nbsp;</i>On October 12, 2014, an automatic SCRAM occurred during the reactor startup evolution following the 1R25 refueling outage. The SCRAM occurred when a station electrician, in conjunction with a General Electric technician and a site engineer, secured power to the Main Generator Automatic Voltage Regulator (AVR) controllers while the Main Turbine warming evolution was in progress. The individuals were not authorized to perform this action nor did they have procedures in the field to operate the equipment. Their actions resulted in an automatic reactor SCRAM on low water level. <br /><br /> ENS 50524 was submitted on October 12, 2014, and updated on October 17, 2014. This issue is reportable under 10 CFR 50.73(a)(2)(iv)(A), because it involved an event or condition that resulted in manual or automatic actuation of any of the systems listed in paragraph (a)(2)(iv)(B).<br /><br /> The Root Cause Analysis was completed on January 30, 2015. The cause of this event was determined to be that Station Leadership has inconsistently reinforced Human Performance Error Reduction Tool Use and Procedure Use and Adherence. This resulted in the breakdown of multiple fundamental practices and standards that led to the event.
2202014001 | Nine Mile Point 1 | 02/12/2014 | 04/11/2014 | ML14118A03 | <strong>Reportable Conditions Not Reported During the Previous 3 Years Involving Average Power Range Monitors Inoperability</strong><br /><i>Abstract:&nbsp;</i>This LER is submitted to acknowledge that Nine Mile Point (NMP) missed providing LERs for past occurrences reportable in accordance with10 CFR 50.72(b)(3)(v)(A) and 10 CFR 50.73(a)(2)(v)(A) as conditions that could have prevented the fulfillment of the safety function of a structure or system needed to shutdown the reactor and maintain it in a safe shutdown condition. This condition was discovered on February 12, 2014. The reportable conditions occurred twice within the past three years when APRMs were declared inoperable as a result of reactor recirculation pump (RRP) trips. In each occurrence, the APRM flow-biased control rod block and scram function remained available, though, nonconservative. The cause of Operations personnel not recognizing the APRM conditions as reportable was due to ineffective training of Operations personnel. Corrective actions taken or planned include briefings and detailed training on reporting requirements and revisions to procedures that clarify event reporting requirements.
2202014002 | Nine Mile Point 1 | 05/08/2014 | 07/08/2014 | ML14205A27 | <strong>Unanalyzed Condition due to Unfused Motor Operated Valve Control Circuit</strong><br /><i>Abstract:&nbsp;</i>On May 8, 2014, at 1645, the results of an industry operating experience (OE) extent of condition review identified that an un-fused control circuit associated with the Unit 1 Reactor Water Cleanup Isolation Valve 12 could short circuit due to a fire in the circuit cable routing. This short circuit could cause the cable to selfheat and cause secondary fires along the associated cable route. The unanalyzed secondary fires could adversely affect safe shutdown equipment and potentially cause the loss of ability to safely shutdown as required by 10 CFR 50 Appendix R. The original plant wiring design and configuration for the containment isolation valve did not include separate overcurrent protection for motive power and control wiring. The only protection for control circuit wiring is by motive circuit fuses which are not sized appropriately to protect the control wiring. As a compensatory measure, Operations has initiated a fire inspection each shift to monitor the associated Fire Areas (1 and 10) until separate fuses are installed within the control circuitry of the motor operated valve (MOV). A similar event was reported in LER 2013-002.<br /><br /> This condition was entered into the Nine Mile Point (NMP) corrective action program as Condition Report (CR) 2014-004630.
2202014004 | Nine Mile Point 1 | 08/13/2014 | 10/10/2014 | ML14290A52 | <strong>Secondary Containment Inoperable Due to Simultaneous Opening of Airlock Doors</strong><br /><i>Abstract:&nbsp;</i>On August 13, 2014, at approximately 2318 hours, the secondary containment of the Nine Mile Point Nuclear Station Unit 1 (NMP1) Reactor Building was breached when station personnel opened both inner and outer airlock doors simultaneously while passing through. The integrity of the airlock was reestablished in approximately 5 seconds when one of the doors was closed and latched. The magnetic door lock system on the NMP1 airlock doors was bypassed defeating the system used to prevent simultaneous opening of both doors. Secondary containment differential pressure was unaffected by this event. The cause of the event is less than adequate physical barriers to prevent casual operation of the bypass pushbuttons. Corrective actions to be taken include installing closure devices on the magnetic door lock bypass pushbutton covers. NMP2 LER 2014-007 was provided for a similar event that occurred on April 2, 2014.
2202014005 | Nine Mile Point 1 | 10/16/2014 | 12/12/2014 | ML14353A21 | <strong>Secondary Containment Inoperable due to Simultaneous Opening of Airlock Doors</strong><br /><i>Abstract:&nbsp;</i>On October 16, 2014, at approximately 1042 hours, the secondary containment of the Nine Mile Point Nuclear Station Unit 1 (NMP1) Reactor Building was breached when station personnel opened both inner and outer airlock doors on elevation 261 simultaneously while traversing through the airlock. The integrity of the airlock was re-established within 5 seconds when one of the doors was closed and latched. Secondary containment differential pressure was unaffected by this event. The cause of the event is an inherent vendor design issue that resulted in a false expectation that the magnetic locks would prevent simultaneous opening of the airlocks. Corrective actions to be taken include installing cameras and monitors to prevent breaching of the secondary containment in addition to the existing magnetic locks. NMP1 LER 2014-004 was provided for a similar event that occurred on August 13, 2014.
2202014006 | Nine Mile Point 1 | 10/20/2014 | 12/12/2014 | ML14353A21 | <strong>Secondary Containment Inoperable Due to Simultaneous Opening of Airlock Doors</strong><br /><i>Abstract:&nbsp;</i>On October 20, 2014, at approximately 1353 hours, the secondary containment of the Nine Mile Point Nuclear Station Unit 1 (NMP1) Reactor Building was breached when station personnel opened both inner and outer airlock doors on elevation 261 simultaneously while traversing through the airlock. The integrity of the airlock was re-established within 5 seconds when one of the doors was closed and latched. Secondary containment differential pressure was unaffected by this event. The cause of the event is an inherent vendor design issue that resulted in a false expectation that the magnetic locks would prevent simultaneous opening of the airlocks. Corrective actions to be taken include installing cameras and monitors to prevent breaching of the secondary containment in addition to the existing magnetic locks. NMP1 LER 2014-004 was provided for a similar event that occurred on August 13, 2014 and NMP1 LER 2014-005 was provided for a similar event that occurred on October 16, 2014.
2372014001 | Dresden 2, Dresden 3 | 03/27/2014 | 05/27/2014 | ML14160A70 | <strong>Secondary Containment Inoperable Due to Two Interlock Doors Being Open Simultaneously</strong><br /><i>Abstract:&nbsp;</i>On March 27, 2014, two secondary containment interlock doors were opened simultaneously. At approximately the same time, an Electrical Maintenance Department (EMD) First Line Supervisor (FLS) approached the interlock from the emergency diesel generator side of the 2/3-5850-137 door and two Equipment Operators (EO) approached the interlock from the Reactor Building (RB) side of the 2/3-5850-59 door. When both work groups proceeded to enter the interlock, it was realized the doors were open simultaneously and they immediately secured both doors in the closed position. <br /><br /> An apparent cause was not identified, however, the most probable cause was determined to be a failure of the magnetic vane operated limit switch on the 2/3-5850-59 EDG door. This determination was based off of historical poor performance of the component. As a result, the station is completing a modification to the interlock doors and replacing the existing limit switches. <br /><br /> Based upon the short duration of the secondary containment doors being opened simultaneously and that the Secondary Containment differential pressure remained negative during the course of this event, this event is of low safety significance. The station has adjusted the limit switch and is in the process of implementing a design modification. <br /><br /> An Engineering Evaluation was performed (per NEI 99-02, Regulatory Assessment Performance Indicator Guideline) to show this event did not constitute a Safety System Functional Failure.
2372014002 | Dresden 2 | 04/12/2014 | 01/08/2015 | ML15035A06 | <strong>Unit 2 Reactor Scram due to Main Power Transformer Failure</strong><br /><i>Abstract:&nbsp;</i>On April 12, 2014 at 1012 CDT, the Main Power Transformer for Dresden Unit 2 faulted due to an internal flashover. Due to the trip of the transformer, an automatic reactor protection system actuation occurred. All control rods inserted to their full-in position, and following the reactor trip, all systems operated as expected.<br /><br /> The most probable cause of the transformer failure was determined to be a combination of insulation issues. As a result, the transformer was replaced. Improved manufacturer oversight is being developed and procedures are being revised to ensure critical inspections are implemented during manufacturing.<br /><br /> The safety significance of this event was determined to be minimal based upon the availability of the required systems to safely shut down the reactor.<br /><br /> This event is being reported in accordance with 10 CFR 50.73(a)(2)(iv)(A), any event or condition that resulted in manual or automatic actuation of any of the system listed in paragraph (a)(2)(iv)(B).
2372014003 | Dresden 2 | 05/03/2014 | 10/24/2014 | ML14325A59 | <strong>Unit 2 Reactor Scram During Automatic Voltage Regulator Channel Transfer</strong><br /><i>Abstract:&nbsp;</i>On May 03, 2014, Dresden Station was performing a channel swap of the Unit 2 Automatic Voltage Regulator (AVR). While attempting to perform the channel swap, the AVR unexpectedly switched to manual mode which resulted in exciter VARS rapidly decreasing. An automatic reactor protection system actuation, Turbine/Generator Trip, was received and all rods inserted to their full-in position. Following the reactor trip, all systems operated as expected.<br /><br /> The cause of this event was determined to be attributed to insufficient validation of vendor products following major equipment upgrades to ensure reliability of the newly installed equipment. Affected components were replaced, and the Automatic Voltage Regulator was successfully tested. Additionally, procedural guidance is being implemented to address risks associated with vendor, sub-vendor design, and technical products including risks associated with digital technology.<br /><br /> This event is being reported in accordance with 10 CFR 50.73(a)(2)(iv)(A), any event or condition that resulted in manual or automatic actuation of any of the system listed in paragraph (a)(2)(iv)(B).
2442014001 | Ginna | 01/20/2014 | 03/18/2014 | ML14079A52 | <strong>Total Particulate Concentration in B Emergency Diesel Generator Fuel Oil Storage Tank Exceeded Acceptance Criteria - Cause Attributed to Contamination from Using a Temporary Fuel Oil Storage Tank</strong><br /><i>Abstract:&nbsp;</i>On January 7, 2014, a fuel oil sample was collected from "B" Emergency Diesel Generator (EDG) fuel oil storage tank (TDG01B) per Technical Specification (TS) Surveillance Requirement (SR) 3.8.3.2, for routine testing. The sample was shipped to an off-site laboratory for analysis; the analytical results were received at Ginna on January 20, 2014. The report indicated that the total particulate concentration in TDG01B exceeded the acceptance criteria established by TS 5.5.12, "Diesel Fuel Oil Testing Program." Due to the 13 day lapse between sample collection and licensee receipt of analytical results, the Completion Time of seven (7) days for TS Limiting Condition for Operation (LCO) 3.8.3, "Diesel Fuel Oil," Condition B, "Restore fuel oil total particulates within limit," had been exceeded.<br /><br /> Upon identification of the unacceptable total particulate concentration, a work order was implemented to establish continuous filtration of TDG01B. Samples collected from the discharge of the filter indicated that the filtration was not achieving a satisfactory reduction in total particulate concentration; therefore, the filtration was secured. After further evaluation, the decision was made to replace the fuel oil in the tank.<br /><br /> The cause of the event was attributed to contamination from a temporary storage tank used in previous maintenance. To prevent re-occurrence of this event, guidance will be added to the procedure controlling work utilizing temporary storage containers or tanks to ensure the temporary tanks meet the same cleanliness criteria as the systems they are being used to service.
2442014002 | Ginna | 03/13/2014 | 05/08/2014 | ML14134A01 | <strong>Unanalyzed Condition due to Postulated Hot Short Fire Event Involving DC Control Circuits Affecting Multiple Fire Areas</strong><br /><i>Abstract:&nbsp;</i>On March 13, 2014 during an industry Operating Experience review, a postulated Appendix R fire scenario was identified that could potentially impact several fire areas and potentially affect safe shutdown equipment. The postulated scenario could allow fire spread via unprotected DC control circuit for non-safety related circulating water pump discharge motor operated valves (MOV). The affected wiring is routed through the screenhouse, "B" Emergency Diesel Generator room, turbine building, air handling room, relay room, and control room.<br /><br /> Compensatory actions taken include hourly fire tours in the potentially impacted areas.<br /><br /> Corrective action to install fuses to protect the circuits for the Circulating Water Pump Discharge MOVs was completed.
2442014003 | Ginna | 09/10/2014 | 11/16/2014 | ML14318A29 | <strong>"A" Emergency Diesel Generator Output Breaker Fails to Close During Routine Surveillance Testing, Resulting in a Condition Prohibited by Technical Specifications and a Potential Inability to Fulfill a Safety Function</strong><br /><i>Abstract:&nbsp;</i>On September 10, 2014, during performance of a routine, scheduled surveillance test (STP-O-12.1) on the "A" Emergency Diesel Generator (EDG), the output supply breaker to safeguards Bus 14 failed to close on demand. Non-intrusive troubleshooting revealed no obvious issues with the breaker, and the output supply breaker functioned as required during a second test. A spare breaker was installed and tested satisfactorily on September 11, 2014.<br /><br /> An inspection of the original breaker conducted with the assistance of an original equipment manufacturer (OEM) engineer determined the apparent cause of the failure to be misalignment and lack of end to end play of the tripper bar within the breaker operating mechanism. Corrective actions included installing a spare circuit breaker and performing STP-O-12.1 to verify satisfactory operation Testing procedures have been modified to include post-test inspections to ensure the tripper bar is properly aligned for operation. Maintenance procedures will be modified to verify proper end to end play alignment. This event is not considered to have had any significant effect on the health and safety of the public.
2472014001 | Indian Point 2, Indian Point 3 | 02/20/2014 | 04/07/2014 | ML14107A34 | <strong>Technical Specification (TS) Prohibited Condition due to Failure to Comply with TS 3.4.3 Reactor Coolant System Pressure-Temperature Limits During Vacuum Refill</strong><br /><i>Abstract:&nbsp;</i>On February 20, 2014, Entergy identified a failure to comply with Technical Specification (TS) 3.4.3 [Reactor Coolant System (RCS) Pressure and Temperature (P/T) Limits] after review of a Westinghouse PWR Owners Group (PWROG) correspondence (OG-14-66) dated February 19, 2014. The PWROG correspondence discussed a Non-cited Violation at Perry Nuclear Plant for failure to comply with their TS for RCS P/T limits when operating the plant with a vacuum in the reactor pressure vessel (RPV) during cold startups and cooldowns. A review of the Indian Point Units 2 and 3 TS 3.4.3 determined that TS 3.4.3 P/T limits for heatup and cooldown only provide for values greater than or equal to 0 psig. TS 3.4.3 requires that the RCS pressures and temperatures be maintained within limits at all times specified in TS Figures 3.4.3-1 and 3.4.3-2. The P/T Figures provide curves with a pressure starting at 0 psig. During past operation at both units, TS 3.4.3 P/T limits were not complied with when performing vacuum refill in Mode 5 as this process results in RCS pressures less than 0 psig. Cause of the event was a failure to recognize that a negative pressure was not allowed by the TS. Corrective actions for Unit 2 was a TS amendment that was processed and approved by the NRC to include the acceptability of the vacuum refill condition. Corrective actions for Unit 3 will be to submit a change to the TS to support this condition. The event had no effect on public health and safety.
2472014002 | Indian Point 2 | 02/24/2014 | 04/23/2014 | ML14127A06 | <strong>Technical Specification Prohibited Condition due to an Inoperable 23 Steam Generator (SG) Caused by a Through Wall Defect in 23 SG Drain Line Valve MS-68</strong><br /><i>Abstract:&nbsp;</i>On February 24, 2014, during initial Containment walkdowns after shutdown for a refueling outage, Operations identified a steam leak on 23 steam generator (SG) drain line valve MS-68. Valve MS-68 is a normally closed valve on a one inch drain pipe from the 23 SG shell side to the two inch SG Blowdown piping to the blowdown tank. The steam leak was due to a through wall defect in the valve body. The one inch SG drain pipe and valve MS-68 are safety related, ISI-ASME Code Class 2 High Energy (HE) and Seismic Class 1 components. Assessment of the condition determined the leak could not be isolated and Ultrasonic Testing (UT) could not be performed to determine the extent of the defect. The valve and associated piping are a pressure boundary for the SG and because there is no ASME Code method to evaluate the structural integrity of the through wall defect, Engineering concluded the valve was inoperable. Operations declared the 23 SG inoperable but the plant was in Mode 5 (Cold Shutdown) and one SG inoperable did not impact Technical Specification (TS) 3.4.7 [Reactor Coolant System (RCS) Loops-Mode 5, Loops Filled]. However, the condition had resulted in leaking prior to shutdown and therefore was applicable to TS 3.4.4 [Reactor Coolant System (RCS) Loops-Modes 1 and 2) which requires four operable RCS loops including four operable SGs. The cause of the steam leak was a pin hole in the body of valve MS-68. The pin hole was likely a defect in the original valve casting which over time propagated through the valve wall. Corrective action was removal and replacement of the valve. The event had no effect on public health and safety.
2472014003 | Indian Point 2 | 03/18/2014 | 05/19/2014 | ML14149A24 | <strong>Technical Specification (TS) Prohibited Condition Due to a Mode Change with an Inoperable 22 Auxiliary Feedwater Pump</strong><br /><i>Abstract:&nbsp;</i>On March 18, 2014, Entergy identified a failure to comply with Technical Specification (TS) 3.7.5 [Auxiliary Feedwater System (AFW)] after discovery that post maintenance testing (PMT) had not been performed after completion of work on the 22 Turbine Driven (TD) AFW pump steam supply valves MS-41 and MS-42. Failure to perform a PMT on valves MS-41 and MS-42 prevents demonstration that the valves are operable. Inoperable AFW pump steam supply valves causes the TD-AFW pump to be inoperable. TS 3.7.5 requires three trains of AFW to be operable in Modes 1, 2 and 3. Mode 3 was entered on March 16, 2014. TS 3.7.5 contains a note that Limiting Condition for Operation (LCO) 3.0.4.b is not applicable and this LCO was not met when the plant entered Mode 3 as the LCO of TS 3.7.5 and LCO 3.0.4.a was not met and LCO 3.0.4.b is precluded. Upon discovery of the condition, valves MS-41 and MS-42 and the 22 TD AFW were declared inoperable. Cause of the event was scheduling error. This resulted in the exclusion of the PMT from the outage schedule. Corrective actions included testing valves, and correcting the scheduling error. The event had no effect on public health and safety.
2492014001 | Dresden 3 | 11/06/2014 | 08/07/2015 | ML15223A43 | <strong>Electromatic Relief Valve Failed to Actuate During Surveillance Testing</strong><br /><i>Abstract:&nbsp;</i>On November 6, 2014, with the reactor in mode 5, an electromatic relief valve (ERV) actuator failed to open during the performance of scheduled surveillance testing. The surveillance involves an operator manually actuating the ERV from the main control room with operators staged in the field. The operators in the field reported an audible click when the manual actuation was initiated. However, when the demand signal was given, the actuator plunger did not move and the valve did not open. The Apparent Cause of failure was determined to be that actuator design is susceptible to vibration induced wear in conjunction with the vibration particularly on the 'B' Main Steam Line near the 3E ERV. <br /><br /> Corrective actions include replacement of ERV actuators with a hardened design, future inspections of supporting structures, and identifying the source of elevated vibrations. <br /><br /> This failure has been determined to be of very low safety significance.<br /><br /> This event is being reported under 10 CFR 50.73(a)(2)(i)(B) "Any operation or condition which was prohibited by the plant's Technical Specifications," and under 10 CFR 50.73(a)(2)(v)(D), "Any event or condition that could have prevented the fulfilment of the safety function of structures or systems that are needed to mitigate the consequence of an accident."
2502014001 | Turkey Point 3 | 01/03/2014 | 03/04/2014 | ML14087A12 | <strong>Missed Surveillance Test Resulted in a SG Pressure Instrument Channel to be Inoperable Longer than AOT</strong><br /><i>Abstract:&nbsp;</i>On January 3, 2014 with the Unit 3 reactor in Mode 1 at 100% power, the instrument channel associated with Main Steam Line Pressure Transmitter PT-3-495 was found outside procedural acceptance criteria due to PT drift. PT-3-495 was replaced, calibrated successfully, and returned to service on January 4, 2014. Subsequent review determined the instrument channel was inoperable from March 9, 2013 to January 3, 2014. During the period of inoperability, the allowed outage time of 6 hours was exceeded without taking the required action to place the channel in the tripped condition and the shutdown actions of Technical Specification (TS) 3.0.3 were not entered. This event is reportable in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by the TS. The root cause is attributed to a deviation from the normal process of using a dedicated work order (WO) to satisfy surveillance requirements. As result, Instrumentation and Control supervision failed to validate WO activities credited for satisfying TS requirements. As corrective action, the surveillance tracking program procedure will be revised to state that an independent verification is to be performed and documented prior to approval that a surveillance test has been completed when crediting non-dedicated WOs. An extent of condition review was also performed. Safety significance remained low during the period the instrument channel was inoperable because both redundant channels remained available.
2502014002 | Turkey Point 3 | 03/19/2014 | 05/15/2014 | ML14163A12 | <strong>Reactor Coolant System Pressure Boundary Leakage at Pressurizer Heater Sleeve Attachment Weld</strong><br /><i>Abstract:&nbsp;</i>On March 19, 2014 with the Unit 3 reactor in Mode 5 at 0% power (Cold Shutdown), examination revealed evidence of leakage in the annulus between the outer surface of the Pressurizer heater sleeve and the lower head bore at heater penetration 11. Unit 3 was in Mode 5 in preparation for refueling. Nondestructive examination confirmed that there was no flaw in the heater sleeve indicating that the in-vessel attachment weld was the probable source of leakage. Because of the inability to characterize the flaw in the attachment weld, the most likely root cause is attributed to an original fabrication welding defect in the heater sleeve partial penetration weld further impacted by stress corrosion cracking and/or thermal fatigue. Corrective action involved the installation of a half-nozzle ASME Code repair of heater sleeve 11, which relocated the reactor coolant system pressure boundary to the outside of the Pressurizer lower head at the heater sleeve penetration. Relief was authorized to leave the flaw in place for one operating cycle.
2502014003 | Turkey Point 3 | 04/23/2014 | 06/18/2014 | ML14192A01 | <strong>Manual Actuation of the Reactor Protection System due to Failure of Group Step Counter</strong><br /><i>Abstract:&nbsp;</i>On April 23, 2014 at approximately 1302 hours, Unit 3 entered Technical Specification (TS) 3.1.3.3 Action as a result of the Shutdown Bank B Group 1 step counter failing to increment. The reactor was subcritical in Mode 3 progressing to reactor startup. The reactor trip breakers were opened as required by the Action of TS 3.1.3.3. The TS requires that the reactor trip breakers be opened if the group step counter demand position indicator (group 1 and group 2) are not within ± 2 steps of each other. All rods fully inserted. The unit remained in Mode 3. This was a manual actuation of the Reactor Protection System. Therefore, an 8-hour report (EN# 50054) was made in accordance with 10 CFR 50.72(b)(3)(iv) to the NRC Operations Center. The cause of the event was a supervisory data logging card not fully seated in the circuit card rack because of insufficient instruction in a functional test procedure. The supervisory data logging card was reseated and the testing sequence continued successfully. A revision to the procedure will require a visual inspection and independent verification to verify proper engagement of the printed circuit cards.
2502014004 | Turkey Point 3, Turkey Point 4 | 07/20/2014 | 09/18/2014 | ML14280A48 | <strong>Ultimate Heat Sink Temperature Limit Exceeded Due to Environmental Conditions</strong><br /><i>Abstract:&nbsp;</i>On July 20, 26, 27, 28 and August 7, 2014, Turkey Point Units 3 and 4 entered and exited the Action for Technical Specification (TS) 3.7.4, Ultimate Heat Sink, once each day for periods of up to 8 hours because the 100 degree F limit for ultimate heat sink (UHS) temperature was exceeded. The 12 hour requirement to be in Hot Standby was not exceeded during these events and so there was no condition prohibited by the TS. On July 20, 2014, the NRC granted enforcement discretion (NOED No. 14-2-001) to allow the Turkey Point units to continue operation with UHS temperature up to 103 degrees F provided certain compensatory measures were implemented and termination criteria were met. License amendments were issued by the NRC on August 8, 2014, which increased the UHS temperature limit to 104 degrees F and terminated the NOED. Environmental conditions outside of management control negatively impacted UHS water quality (primarily an algae bloom) and the ability of the cooling canal system (CCS) to dissipate the heat rejected by plant operation. Corrective actions include biocide treatment of the CCS water, revision of the UHS temperature limit to 104 degrees F, and enhancement and integration of existing activities to improve the monitoring of CCS capability to accommodate normal and accident plant heat loads. There were no safety consequences to plant or public safety as a result of these events.
2502014005 | Turkey Point 3 | 08/11/2014 | 10/10/2014 | ML14303A47 | <strong>Manual Reactor Trip due to Loss of Instrument Air</strong><br /><i>Abstract:&nbsp;</i>On August 11, 2014 at approximately 1028 hours with Unit 3 at approximately 100% reactor power, a manual reactor trip was initiated in response to a loss of instrument air (IA). The Auxiliary Feedwater System automatically initiated as designed. The unit was subsequently stabilized in Mode 3 with IA restored. An automatic safety injection (SI) actuation occurred as a result of main steamline high differential pressure. High head safety injection (HHSI) pumps, residual heat removal (RHR) pumps, and emergency diesel generators (EDG) automatically started as designed due to the SI signal. Based on plant conditions, the HHSI and RHR pumps did not inject into the reactor coolant system. The running compressor was unloaded inadvertantly at approximately 1020 hours and the standby compressors started but did not load due to a latent design error in the start logic. Although the standby compressors were restarted and loaded by approximately 1029 hours, IA decreased below the pressure required for the reactor trip. The SI actuation was caused by inadequate control of primary plant parameters during a loss of IA to containment. Corrective actions include: Removing an unneeded permissive in the standby compressor control logic which prevented the compressor from loading, and revising the loss of IA procedure to provide additional guidance on control of pressurizer level and pressure when IA is lost.
2512014001 | Turkey Point 4, Turkey Point 3 | 04/25/2014 | 06/24/2014 | ML14192A01 | <strong>Incorrect Feedwater Flow Transmitter Calibration Caused RPS Channels to be Inoperable</strong><br /><i>Abstract:&nbsp;</i>On April 25, 2014, it was identified that three feedwater flow transmitters were incorrectly calibrated during the Unit 4 startup in April 2013. The transmitters' zero calibration point had been shifted to the high end of the calibration tolerance as provided in the setpoint methodology. The impact of the calibration was to shift the actuation point of the Steam/Feedwater flow mismatch reactor trip beyond that specified in Technical Specifications (TS). The condition existed longer than allowed by the TS with the required actions not taken. An extent of condition review identified a similar condition existed on one Unit 3 feedwater flow transmitter following that unit's startup in August 2012. The causes are that the Engineering Technical Response Memorandum (ETRM now ETR) form has a missing barrier to provide defense-in-depth to prevent inappropriate usage, and lack of technical rigor and knowledge regarding the design basis impact of the flow transmitter calibration change. Corrective actions include: 1) Revise fleet procedure and form for ETRs to specifically state restrictions for which ETRs cannot be used, and 2) provide training to appropriate Engineering personnel regarding proper scope and usage of ETRs, and scaling and channel uncertainties used to define the design and licensing basis for the reactor protection system and engineered safety feature actuation system instrumentation.
2512014002 | Turkey Point 4 | 05/25/2014 | 07/24/2014 | ML14206A85 | <strong>Automatic Actuation of the Reactor Protection System due to Low Main Condenser Vacuum</strong><br /><i>Abstract:&nbsp;</i>On May 25, 2014, with Unit 4 at approximately 20% reactor power during a shutdown to repair an unrelated equipment issue, an automatic reactor trip occurred due to low condenser vacuum. The transfer of steam supply to the gland sealing steam system from the Unit 4 main steam system to the Unit 3 auxiliary steam system while the unit was on-line caused the decrease in main condenser vacuum. Main condenser vacuum reached the turbine trip setpoint, which resulted in the automatic reactor trip. Trip response was uncomplicated.<br /><br /> The root cause was operations personnel did not adequately address the integrated system status as part of the decision making process used to realign the steam supply to the gland sealing steam system. Corrective actions include: 1) Revising procedural guidance to specify that steam supply to the gland sealing steam system cannot be transferred from the main steam system to the auxiliary steam system with a unit in Mode 1 or 2, and 2) Providing training to all licensed operators to demonstrate the integrated system response aspect of risk-based decision making.
2512014003 | Turkey Point 4 | 09/03/2014 | 11/10/2014 | ML14337A01 | <strong>Emergency Containment Cooler Safety Function Impacted During Breaker Replacement</strong><br /><i>Abstract:&nbsp;</i>On September 3, 2014, the 4C Emergency Containment Cooler (ECC) fan was removed from service for breaker cubicle replacement. When the control wires were disconnected for the cubicle replacement, the auto-start feature of the 4A ECC fan was also lost. As a result, both ECC fans in the B Train were inoperable for a period exceeding the one hour Technical Specification (TS) allowed outage time (AOT). In addition, the 4A ECC fan was inoperable for a period exceeding the 72 hour TS AOT because the control wires were not re-terminated due to a latent design error caused by ineffective design verification. The impact of performing the breaker replacement on the operability of both ECC fans was not recognized in the work planning process due to a lack of understanding of the design details. In addition, the work order (WO) implementing the breaker cubicle replacement did not contain the correct plant mode restrictions specified in the design package. Corrective actions include: 1) The procedure for performing design verification was revised to require that engineers performing verifications must be qualified, 2) A Responsible Engineer (RE) will be assigned to all Approved and Active major modifications such that each RE understands the design details sufficient to provide implementation support, and 3) Revise the WO planning procedure to ensure that WOs do not alter/change design requirements and are consistent with specified plant restrictions in the design. Safety significance is minimal as margins in the safety analysis support ECC function.
2542014001 | Quad Cities 1, Quad Cities 2 | 03/04/2014 | 05/05/2014 | ML14135A28 | <strong>Secondary Containment Differential Pressure Momentarily Lost due to Fuel Pool Radiation Monitor Spike</strong><br /><i>Abstract:&nbsp;</i>On March 4, 2014, at 1917 hours, a Fuel Pool Channel 1B High Radiation alarm occurred. The 1B fuel pool radiation monitor spiked high at 50 mRem/hr, trended downward, and returned to its previous steady-state value of 14 mRem/hr. The high spike caused the Unit 1 and Unit 2 Reactor Building (RB) ventilation and Control Room (CR) ventilation to isolate as designed. The Standby Gas Treatment System (SBGTS) was already in operation for a scheduled surveillance as of 1900 hours on March 4, 2014.<br /><br /> The Unit 1 and Unit 2 RB ventilation system isolation caused the secondary containment differential pressure to be momentarily lost (pressure went positive), and secondary containment was declared inoperable. The RB ventilation system was then shut down for scheduled maintenance, the CR ventilation system was returned to its normal configuration, and troubleshooting was initiated.<br /><br /> Since both Units 1 and 2 share a common RB, the loss of differential pressure (RB pressure went positive) for approximately three (3) minutes impacted both Units 1 and 2 secondary containments.<br /><br /> The cause of the secondary containment loss of differential pressure event was due to a failed fuel pool radiation monitor detector that caused the RB ventilation system to isolate. The detector failure was caused by a manufacturing defect that caused double pulsing on the GM-Tube.<br /><br /> Corrective actions included replacing the failed radiation monitor detector, and sending the failed detector to the vendor for failure analysis.<br /><br /> The safety significance of this event was minimal. Given the impact on the secondary containment, this report is submitted (for Units 1 and 2) in accordance with the requirements of 10 CFR 50.73 (a)(2)(v)(C), which requires the reporting of any event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to control the release of radioactive material.
2542014002 | Quad Cities 1, Quad Cities 2 | 04/01/2014 | 06/02/2014 | ML14163A09 | <strong>Reactor Building Interlock Doors Opened Simultaneously Cause Loss of Secondary Containment</strong><br /><i>Abstract:&nbsp;</i>On April 1, 2014, at 1357 hours, an Instrument Maintenance Technician notified the Main Control Room that both doors in the secondary containment interlock on the 595 foot elevation between the Reactor Building (RB) and the Unit 2 Reactor Feed Pump room (located inside the turbine building (TB)) were opened simultaneously. The failure of this interlock caused a loss of secondary containment per Technical Specification (TS) 3.6.4.1, Condition A. The doors were immediately reclosed, and the secondary containment boundary was immediately reestablished. Operators verified the RB (secondary containment) differential pressure was maintained operable at greater than 0.10 inch of vacuum water gauge. <br /><br /> Secondary containment remained available and functional during the event since the secondary containment interlock was immediately restored by closing the doors and since the RB differential pressure was maintained during the event. No RB low differential pressure alarms were received during this event. The reactor building is a common volume to both Units 1 and 2, and an interlock failure can impact the secondary containment for both units. <br /><br /> The cause of the interlock failure was due to a malfunctioning interlock door hydraulic actuator and time delay relays had allowed the second door to open before the first door was secured. <br /><br /> Corrective actions included replacing the failed actuator and adjusting the limit switch. A set point change will be implemented to resolve relay time delay issues. <br /><br /> The safety significance of this event was minimal. Given the impact on the secondary containment, this report is submitted (for Units 1 and 2) in accordance with the requirements of 10 CFR 50.73 (a)(2)(v)(C), which requires the reporting of any event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to control the release of radioactive material.
2542014003 | Quad Cities 1, Quad Cities 2 | 05/22/2014 | 07/17/2014 | ML14212A49 | <strong>HPCI Interlock Doors Opened Simultaneously Cause Loss of Secondary Containment</strong><br /><i>Abstract:&nbsp;</i>On May 22, 2014, at 2150 hours, a mechanic notified the Main Control Room that both doors [DR] in the secondary containment [NG] interlock [IEL] to the High Pressure Coolant Injection (HPCI) room from the Turbine Building (TB) [NM] were opened simultaneously. The failure of this interlock caused a loss of secondary containment per Technical Specification (TS) 3.6.4.1, Condition A. The doors were immediately reclosed, and the secondary containment boundary was reestablished. Operators verified the Reactor Building (RB) (secondary containment) differential pressure was maintained operable at greater than 0.10 inch of vacuum water gauge.<br /><br /> Secondary containment remained available and functional during the event since the secondary containment interlock was immediately restored by closing the doors and since the RB differential pressure was maintained during the event. No RB low differential pressure alarms were received during this event. The RB is a common volume to both Units 1 and 2. An interlock failure can impact the secondary containment for both units.<br /><br /> The cause of the interlock failure was due to a bent locking bolt resulting in misalignment of the interlock plungers on the TB-side door. The mechanical interlock device could be defeated inadvertently in this condition.<br /><br /> Corrective actions included replacing the bent locking bolt and realigning the TB-side doors.<br /><br /> The safety significance of this event was minimal. Given the impact on the secondary containment, this report is submitted (for Units 1 and 2) in accordance with the requirements of 10 CFR 50.73 (a)(2)(v)(C), which requires the reporting of any event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to control the release of radioactive material.
2542014004 | Quad Cities 1, Quad Cities 2 | 11/18/2014 | 01/16/2015 | ML15029A49 | <strong>Reactor Building Interlock Doors Opened Simultaneously Cause Loss of Secondary Containment</strong><br /><i>Abstract:&nbsp;</i>On November 18, 2014, at 0900 hours, Chemistry personnel notified the control room that both the Unit 1 reactor building (RB) and the Unit 2 turbine building (TB) doors for the 647 foot elevation secondary containment interlock were opened simultaneously. The failure of this interlock caused a loss of secondary containment per Technical Specification (TS) 3.6.4.1, Condition A. The doors were immediately closed and secondary containment pressure remained negative throughout the event. The Field Supervisor was dispatched to investigate the interlock issue and found that the issue was intermittent. Operators staged signage and ropes to administratively control the interlock closed until repairs were performed.<br /><br /> Secondary containment remained available during the event because the secondary containment interlock was immediately restored by closing the doors, and the RB differential pressure was maintained throughout the event. No RB low differential pressure alarms were received during the event. The RB is a common volume to both Units 1 and 2, and an interlock failure can impact the secondary containment for both units.<br /><br /> The cause of the interlock failure was the door magnets on the Unit 2 TB door did not fully engage to hold the door closed due to inadequate design of the interlocks.<br /><br /> Corrective actions included adjustment of the lower magnet on the TB door to ensure good connection between the door and the frame. A modification to the 647 foot elevation interlock doors that addresses single point vulnerabilities will be implemented, and the preventative maintenance frequency will be shortened from 12 months to 6 months.<br /><br /> The safety significance of this event was minimal. Given the impact on the secondary containment, this report is submitted (for Units 1 and 2) in accordance with the requirements of 10 CFR 50.73 (a)(2)(v)(C), which requires the reporting of any event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to control the release of radioactive material.
2542014005 | Quad Cities 1, Quad Cities 2 | 12/15/2014 | 02/13/2015 | ML15058A03 | <strong>Main Control Room Door Unable to Close Causes Loss of Control Room Envelope Boundary</strong><br /><i>Abstract:&nbsp;</i>On December 15, 2014 at 0730 hours, the south Main Control Room (MCR) door was unable to be fully closed due to a failure of the closer mechanism. Technical Specification (TS) 3.7.4, Condition C, was entered due to the inoperable Control Room Envelope (CRE). A security guard was stationed to provide controlled access to the MCR.<br /><br /> The CRE function was restored shortly after the event when the door closer arm linkage was disconnected, the door was confirmed closed, and successfully smoke tested.<br /><br /> The cause of the MCR door closer mechanism failure was a manufacturing defect of the pinion gear.<br /><br /> Corrective actions included replacement of the door closer mechanism, and a preventative maintenance task to replace the closer mechanism will be established.<br /><br /> The safety significance of this event was minimal. Given the impact on the MCR envelope, this report is submitted (for Units 1 and 2) in accordance with the requirements of 10 CFR 50.73 (a)(2)(v)(D), which requires the reporting of any event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident.
2552014002 | Palisades | 01/29/2014 | 03/27/2014 | ML14086A62 | <strong>Degraded Condition due to Crack Indications in Control Rod Drive Mechanism Housing Assemblies</strong><br /><i>Abstract:&nbsp;</i>On January 24, 2014, during an internal examination of the upper housing assembly for control rod drive mechanism No.23 (CRDM-23), an axial crack indication was identified adjacent to an interior surface, nonstructural, onlay weld (weld No.5). The examination of CRDM-23 upper housing assembly was performed as a corrective action from a 2012 event. On January 29, 2014, it was determined the crack indications in the upper housing assembly of CRDM-23 exceeded the acceptance criteria specified in the inspection plan. Subsequent examination of all 45 CRDM upper housing assemblies identified unacceptable crack indications on 17 assemblies. All crack indications were located in the proximity of the interior surface onlay weld No.5.<br /><br /> Crack indications in the upper housing assemblies of the CRDMs were caused by transgranular stress corrosion cracking (TGSCC). An accumulation of tensile stress, a susceptible material, and an environment that supports cracking are required for TGSCC to occur. Failure mode analyses are currently in-progress. It is suspected that manufacturing irregularities in surface onlay weld No.5 produced sufficient tensile stresses within the 316L stainless steel upper housing assemblies to initiate TGSCC.<br /><br /> The upper housing assemblies for 44 of the 45 total CRDM were removed and replaced with upper housing assemblies of modified design. Previously, in August 2012, the upper housing assembly of CRDM-24 was replaced with the same modified design. No crack indications were identified in the upper housing assembly of CRDM-24.
2552014003 | Palisades | 02/05/2014 | 03/27/2014 | ML14086A62 | <strong>Weld Defect in Pressurizer Nozzle to Nozzle Safe End Flange</strong><br /><i>Abstract:&nbsp;</i>On February 5, 2014, with the unit in Mode 6 for refueling outage 23 (1R23), during in-service inspection (ISI) examinations, an ultrasonic examination (UT) performed on a dissimilar metal weld (DMW) between the pressurizer nozzle and safe end flange for a pressurizer safety relief valve, revealed two axial indications in the root area of the weld. The two indications did not meet applicable acceptance criteria under ASME Section XI, IWB-3514, "Standards for Examination Category B-F, Pressure Retaining Dissimilar Metal Welds in Vessel Nozzles, and Examination Category B-J, Pressure Retaining Welds in Piping."<br /><br /> The weld material encompassing the indications was removed. A weld repair was performed per ASME Section XI, IWA-4000, "Repair/Replacement Activities," Code Case N-638-4, "Similar and Dissimilar Welding Using Ambient Temperature Machine GTAW Temper Bead Technique," and relief request, "RR 4-19 Proposed Alternative to the Requirements of ASME Code Case N-638-4," which was submitted to, and approved by, the NRC. The repair was completed on March 08, 2014, and a post-weld radiograph was satisfactorily completed on March 09, 2014.<br /><br /> The event posed no threat to public health and safety.<br /><br /> This event is reportable in accordance with 10 CFR 50.73(a)(2)(ii)(A) as a degraded or unanalyzed condition.
2592014002 | Browns Ferry 1, Browns Ferry 2, Browns Ferry 3 | 03/31/2014 | 05/30/2014 | ML14155A12 | <strong>Diesel Generator Inoperable due to Fuel Oil Leak</strong><br /><i>Abstract:&nbsp;</i>On March 31, 2014, based on the report obtained from the Tennessee Valley Authority (TVA) Central Laboratory, a revision was made to a past operability evaluation that determined Diesel Generator A was inoperable from March 5, 2013 at 0505 central standard time (CST) until November 23, 2013 at 2004 CST, which was longer than allowed by Technical Specifications. The inoperability was a result of a fuel oil leak originating from a threaded pipe nipple.<br /><br /> On November 23, 2013, common Diesel Generator (DG) A was operated for performance of its routine 24-hour surveillance test. The DG A was fully loaded at 1210 CST, and at 1430 CST, a fuel oil leak of approximately 100 drops per minute was discovered on the discharge line of the engine-driven fuel oil pump. The DG was secured and an inspection of the discharge line identified a circumferential thru-wall crack on the underside of the pipe nipple threaded into the pump discharge check valve. The leaking pipe nipple was removed and replaced. A section of the failed pipe nipple was sent to the TVA Central Laboratories Services for failure analysis who issued a report that identified the direct cause of the failure as low-stress/high-cycle fatigue.<br /><br /> The root causes identified were that the existing configuration of the engine-driven fuel oil pump discharge piping on DG A does not provide sufficient margin to allow for minor variations in maintenance and that workers improperly reassembled the pipe union on DG A fuel oil piping while performing the 12-year inspection.
2592014003 | Browns Ferry 1 | 08/26/2014 | 10/24/2014 | ML14302A16 | <strong>Turbine Generator Neutral Overvoltage Causes a Reactor Scram</strong><br /><i>Abstract:&nbsp;</i>On August 26, 2014, at 1730 Central Daylight Time, Browns Ferry Nuclear Plant (BFN), Unit 1, experienced a turbine trip resulting in an automatic reactor scram. The cause of the turbine trip was a control valve fast closure signal that was generated by a turbine trip on generator neutral over voltage signal from the 1A Generator Neutral Overvoltage relay.<br /><br /> The root cause of the event was the failure of an internal fuse to Generator Circuit Breaker Potential Transformer to clear a fault due to improper fuse size. This was the result of insufficient technical rigor during vendor design and in the Tennessee Valley Authority's review of the vendor design.<br /><br /> The corrective action to prevent recurrence is to develop and implement a design change for all three BFN Units to replace the fuses contained within the Main Generator Circuit Breaker Potential Transformers with a fuse that will coordinate with the Generator Neutral Overvoltage Relay and clear prior to the actuation point of the Generator Neutral Overvoltage Relay during any postulated failure of the Potential Transformers.
2592014004 | Browns Ferry 1 | 10/04/2014 | 12/03/2014 | ML14342A08 | <strong>Main Steam Isolation Valves Leaking in Excess of Technical Specification Requirements</strong><br /><i>Abstract:&nbsp;</i>On October 4, 2014, at approximately 2000 hours Central Daylight Time (CDT), during performance of surveillance procedures for Primary Containment Local Leak Rate Testing of the Main Steam Lines, both the 1B Outboard (OUTBD) Main Steam Isolation Valve (MSIV) and the 1D OUTBD MSIV failed to meet the Technical Specifications (TS) Surveillance Requirement (SR) 3.6.1.3.10 leak rate limit of 100 standard cubic feet per hour (scfh). Both MSIVs were considered to be inoperable for a period of time greater than allowed by TS.<br /><br /> Since both MSIVs failed to meet the leak rate limit, Browns Ferry Nuclear Plant, Unit 1, operated longer than allowed by TS Limiting Condition for Operation (LCO) 3.6.1.3 and the TS LCO 3.0.4 was not met for each applicable Mode change since the last recorded as-found MSIV leak rate test on October 21, 2012, when the leak rates were below the TS leak rate limit.<br /><br /> The causes of the event were inadequate packing for the 1B OUTBD MSIV and non-uniform scale buildup for the 1D OUTBD MSIV.<br /><br /> The corrective actions for these causes are to repack the 1B OUTBD MSIV using an improved packing configuration and to repair the 1D OUTBD MSIV and add the non-uniform scale buildup condition to the valve database for trending.<br /><br /> Based on an analysis of the conditions discovered, it was concluded that this event did not result in any significant safety consequences.
2592014005 | Browns Ferry 1 | 10/29/2014 | 12/23/2014 | ML15007A38 | <strong>Automatic Depressurization System Valve Inoperable for Longer Than Allowed by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On October 29, 2014, during performance of the Browns Ferry Nuclear Plant (BFN) Unit 1 Main Steam Relief Valve (MSRV) Manual Cycle Test, MSRV 1-19 failed to open. Investigation of the failure revealed a misconfiguration of the control air lines to both the MSRV 1-19 and MSRV 1-18 which occurred during installation of the flex hoses in 2006. MSRV 1-19 has an Automatic Depressurization System (ADS) function which was defeated by the air line misconfiguration. The ADS function for MSRV 1-19 has been inoperable since May 2007. This condition would have prevented MSRV 1-19 from performing its specified ADS safety function for longer than allowed by Technical Specifications.<br /><br /> The cause of this event was a latent organizational and programmatic gap associated with the BFN Unit 1 Restart Organization. Specifically, the management and organizational infrastructure in place during the BFN Unit 1 restart was inadequate to preclude numerous human performance errors during the 2005-2007 time period, including the multiple human performance errors associated with this event.<br /><br /> The corrective action is to revise the MSRV pilot valve installation procedures for all three units to include a step to validate the ADS-MSRVs are connected to the appropriate ADS accumulator.
2592014006 | Browns Ferry 1 | 11/25/2014 | 01/26/2015 | ML15028A19 | <strong>Main Steam Relief Valves' Lift Settings Outside Technical Specifications Required Setpoint</strong><br /><i>Abstract:&nbsp;</i>On November 25, 2014, the Tennessee Valley Authority determined, two of thirteen Browns Ferry Nuclear Plant (BFN), Unit 1, Main Steam Relief Valves (MSRVs) mechanically actuated at pressures outside the allowed +/- three percent tolerance of their Technical Specification (TS) setpoint. The BFN, Unit 1, TS Limiting Condition for Operation 3.4.3 requires the safety function of twelve MSRVs to be Operable in reactor Modes 1, 2, and 3. Since two of the thirteen MSRVs actuated outside their TS setpoint allowance by greater than +/- three percent, it is probable that BFN, Unit 1, operated with only eleven Operable MSRVs for longer than allowed by the TS.<br /><br /> An analysis of the event determined that there was no impact on the MSRVs to perform their specified safety function.<br /><br /> The cause for the MRSVs failing above three percent of their setpoint was corrosion bonding of the pilot valve discs to the valve seats because the valve disc surface finish does not make allowance for corrosion bonding. Corrective actions to reduce the probability of similar events occurring in the future are to determine what the required MSRV pilot valve disc finish is for optimal platinum adhesion and to revise the valve procedure to add steps to verify pilot disc finish is equal to or better than this value before the disc is coated in platinum.
2602014001 | Browns Ferry 2, Browns Ferry 1 | 03/27/2014 | 12/23/2014 | ML14364A02 | <strong>Electric Board Room Air Conditioning System Inoperable for Longer than Allowed by the Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On March 27, 2014, it was determined that the Browns Ferry Nuclear Plant (BFN) Required Actions of Technical Requirements Manual (TRM) 3.7.6, Electric Board Room Air Conditioning (AC) System, Condition B, would allow both BFN, Unit 2, Electric Board Room (EBR) AC subsystems to be inoperable for up to 7 days before declaring the Technical Specifications (TS) supported equipment in the EBRs inoperable. This allowance is contrary with the TS definition of "Operable-Operability" with respect to support systems. On two separate occasions in the past three years BFN, Unit 2, EBR AC System and its TS supported systems, were inoperable longer than allowed by TS. After further review of the condition, the causal analysis was revised and it was determined that BFN, Units 1 and 2, did not experience a Safety System Functional Failure (SSFF). This event is being reported in accordance with Title 10 of the Code of Federal Regulations (10 CFR) 50.73(a)(2)(i)(B).<br /><br /> The root cause determined that BFN personnel failed to fully understand the difference between the Technical Requirements Manual (TRM) and Technical Specifications (TS) with respect to operability. When the TS and TRM were implemented, BFN personnel failed to realize the intent of the TRM and believed it was at the same level of the TS.<br /><br /> The corrective actions to prevent recurrence include revising the TRM to clearly delineate the intent and use with respect to operability and revising the procedure for Technical Specifications, Licenses and Amendments to clearly delineate the role of the TRM and TS.
2602014003 | Browns Ferry 2 | 05/21/2014 | 07/21/2014 | ML14205A43 | <strong>Both Trains of Standby Liquid Control Inoperable</strong><br /><i>Abstract:&nbsp;</i>On May 21, 2014, at 1721 Central Daylight Time, Browns Ferry Nuclear Plant (BFN), Unit 2, declared both trains of Standby Liquid Control (SLC) inoperable due to suspected in-leakage to the BFN, Unit 2, SLC tank. Chemistry personnel were dispatched to check the tank level locally after the Control Room received a high level alarm and reported that tank level was high and rising. Based on this report, the SLC system was rendered inoperable and unavailable by closing the SLC tank isolation valve common to both pumps to prevent overflowing the tank. It was subsequently determined that the sensing line had become clogged causing erroneous level indication and the local report of level was incorrect. Sensing lines for the tank level instrumentation were cleared and Operability was restored by returning the isolation valve to the open position and verifying tank level was normal.<br /><br /> The cause of the event was the inadequate use of human performance tools by chemistry personnel which led to the incorrect reporting of SLC tank level when an unexpected condition was encountered.<br /><br /> The corrective actions to reduce recurrence are to revise the surveillance for checking SLC solution level to include a caution note stating that an accurate tank level stick reading cannot be obtained when excessive bubbling is observed in the tank and to increase the frequency of mechanical cleaning of the SLC level indication sensing line. In addition, the responsible Chemistry technician was coached on the appropriate use of human performance tools.
2612014001 | Robinson 2 | 01/09/2014 | 08/05/2014 | ML14225A77 | <strong>Reactor Trip due to a Two-out-of-Three Logic Signal from Steam Generator Water Level Protection Train B Logic Matrix</strong><br /><i>Abstract:&nbsp;</i>At 2234 hours EST on 1/9/2014, with the Unit in Mode 1 at 100% power, H. B. Robinson Steam Electric Plant, Unit 2 experienced an automatic reactor trip/turbine trip during the performance of Steam Generator (SG) Water Level Protection Channel testing. The 'B' reactor trip breaker opened as a result of its 2/3 SG Lo-Lo Level input logic being satisfied. This occurred when one channel contact was "open" due to foreign material lodged between the contact faces and the second channel contact was opened during channel testing. The opening of the 'B' reactor trip breaker resulted in a turbine trip followed by a reactor trip. Auxiliary Feedwater automatically started as expected. There were no other equipment performance issues.<br /><br /> The cause of this event was degradation of passive components (wire labels) in the Reactor Protection System (RPS) relay rack. Degraded wire labels were the source of the foreign material which became lodged in an RPS relay contact creating an undetected halftrip condition.<br /><br /> The foreign material was removed from the RPS relay contact. Both trains of RPS were tested to verify proper functioning of each RPS relay, and both trains of RPS relay racks were inspected to confirm no foreign material was present which could affect proper operation of the RPS relays.
2612014002 | Robinson 2 | 06/26/2014 | 01/26/2015 | ML15036A02 | <strong>Technical Specification Violation due to Incorrect Procedural Guidance</strong><br /><i>Abstract:&nbsp;</i>On 11/26/2014 the Robinson Nuclear Regulatory Commission Resident notified plant staff that the practice of crediting the plant computer (Emergency Response Facility Information System or ERFIS) in lieu of Rod Position Indication (RPI), and not entering the required actions of Technical Specification (TS) 3.1.7 had been reviewed and concluded that this practice was not allowed per the TS.<br /><br /> One occurrence was found where the required actions for TS 3.1.7 were not entered due to crediting ERFIS. On 6/26/2014, Operators identified a discrepancy between RPI indicator and ERFIS indication for a single control rod. Licensed Operators determined that entry into LCO 3.1.7 was not required and ERFIS was documented as acceptable for RPI system operability. All ERFIS RPI indications remained normal and within limits.<br /><br /> Troubleshooting of the RPI on 06/30/2015 revealed that the signal conditioner to the RPI display had failed and the ERFIS display for the control rod in question was accurate, showing that the control rod was within limits; therefore, there were no safety impacts from this event.<br /><br /> Actions were to suspend this practice and issue Standing Instruction 14-023. Operations Surveillance Test procedures were revised to remove language that supported operator actions to credit ERFIS data. The condition was entered into the site's corrective action program.
2632014001 | Monticello | 01/17/2014 | 03/14/2014 | ML14073A59 | <strong>Primary System Leakage Found in Recirculation Pump Upper Seal Heat Exchanger</strong><br /><i>Abstract:&nbsp;</i>On January 17, 2014, leakage into the Reactor Building Closed Cooling Water (RBCCW) System was determined to be Reactor Coolant Pressure Boundary (RCPB) leakage as identified by the Monticello Nuclear Generating Plant (MNGP) Technical Specifications (TS). Based on this, the TS limiting condition for operation was not met and a plant shutdown was required. The plant shutdown commenced at 2029 on January 17, 2014. There was no radioactive release from the plant. The plant was shut down without incident to repair the source of the inleakage. <br /><br /> The apparent cause for the RCPB leak was the lack of an established maintenance strategy in place to periodically check the condition of the heat exchanger or replace it. A crack formed in the #12 Recirculation Pump Upper Seal Heat Exchanger coil due to intergranular stress corrosion cracking. <br /><br /> The leaking # 12 Recirculation Pump Upper Seal Heat Exchanger was removed and the system was modified to operate without this heat exchanger by utilizing the excess capacity of the #12 Recirculation Pump Lower Seal Heat Exchanger.
2632014002 | Monticello | 02/07/2014 | 07/13/2016 | ML16196A22 | <strong>Torus to Drywell Vacuum Breaker Did not Indicate Closed During Testing</strong><br /><i>Abstract:&nbsp;</i>On February 7, 2014, while performing the monthly torus to drywell vacuum breaker check procedure, vacuum breaker valve AO-2382A did not indicate closed as expected. The valve was cycled several times per an alarm response procedure for an open torus to drywell vacuum breaker until it indicated closed.<br /><br /> A causal evaluation has determined the cause of the observed indication for vacuum breaker valve AO-2382A after cycling to be interference between the vacuum breaker test lever and vacuum breaker test actuator stem. This interference was introduced during the 2013 refueling outage when the lever arm was removed for seal replacements. The procedural guidance was not detailed enough to ensure the critical clearances were maintained during removal and replacement of the test lever. The condition was resolved during the 2015 outage by establishing proper clearances between the test lever and actuator stem for all torus to drywell vacuum breakers. In some cases (5 of 8 torus to drywell vacuum breakers) a portion of the test actuator stem was removed. In addition, a revision to the torus to drywell vacuum breaker seal replacement procedure was made to ensure proper clearance between the test lever and test actuator stem would be maintained following maintenance activities.
2632014003 | Monticello | 02/11/2014 | 07/13/2016 | ML16196A22 | <strong>Torus to Drywell Vacuum Breaker Dual Indication During Testing</strong><br /><i>Abstract:&nbsp;</i>On February 11, 2014 while performing the monthly torus to drywell vacuum breaker check procedure, vacuum breaker valve AO-2382A indicated closed as expected in the control room after cycling but did not indicate closed locally in the reactor building. The valve was cycled several times per an alarm response procedure for an open torus to drywell vacuum breaker until it indicated closed. <br /><br /> A causal evaluation has determined the cause of the observed intermittent dual indication for vacuum breaker valve AO-2382A after cycling to be interference between the vacuum breaker test lever and vacuum breaker test actuator stem. This interference was introduced during the 2013 refueling outage when the lever arm was removed for seal replacements. The procedural guidance was not detailed enough to ensure the critical clearances were maintained during removal and replacement of the test lever. The condition was resolved during the 2015 outage by establishing proper clearances between the test lever and actuator stem for all torus to drywell vacuum breakers. In some cases (5 of 8 torus to drywell vacuum breakers) a portion of the test actuator stem was removed. In addition, a revision to the torus to drywell vacuum breaker seal replacement procedure was made to ensure proper clearance between the test lever and test actuator stem would be maintained following maintenance activities.
2632014004 | Monticello | 02/10/2014 | 04/11/2014 | ML14104B43 | <strong>Time to Energize Loads Greater than Surveillance Requirement</strong><br /><i>Abstract:&nbsp;</i>On February 10, 2014, Monticello personnel identified that the Emergency Diesel Generators (EDGs) would not energize permanently connected loads until 10.2 or 10.34 seconds for Division I and Division II, respectively, which exceeded the 10 second limitation of Monticello Technical Specification (TS) Surveillance Requirement (SR) 3.8.1.12. As a result, both EDGs were declared inoperable.<br /><br /> The apparent cause of this event is that the description of the EDG TS SR was inadvertently changed during transition from custom TS 4.9.B.3 to improved TS SR 3.8.1.12 due to improper verification and validation practices of the Improved TS preparation team in 2004-2006.<br /><br /> The set-points for the applicable relays have been revised. The time delay set-point change provides a setting to support EDG performance meeting the 10 second acceptance criterion of SR 3.8.1.12. Additionally, the surveillance procedure will be revised as necessary to implement correct testing for SR 3.8.1.12.
2632014005 | Monticello | 03/20/2014 | 05/19/2014 | ML14139A18 | <strong>Appendix R Fire Door Failed to Latch</strong><br /><i>Abstract:&nbsp;</i>On March 20, 2014, during performance of the semi-annual fire door inspection, an Appendix R fire door did not latch as required and divisional separation could not be assured in the event of a fire. A continuous fire watch was established within the required timeframe once the deficiency was discovered.<br /><br /> The cause of door-410B failure to close and latch during performance of the surveillance was determined to be insufficient closing force.<br /><br /> Immediate corrective actions were to repair door-410B by adjusting the door closer and lubrication of the door latch. The door was then satisfactorily tested and declared functional. Long term corrective actions include door closer force adjustments on a periodic basis.
2632014006 | Monticello | 03/28/2014 | 05/23/2014 | ML14143A16 | <strong>Secondary Containment Doors Opened Simultaneously</strong><br /><i>Abstract:&nbsp;</i>On March 28, 2014, two secondary containment doors in the main access airlock were opened at the same time. With both doors open, Technical Specification Surveillance Requirement 3.6.4.1.3 was not met and secondary containment was declared inoperable. Interviews with individuals involved indicate the doors were open for approximately two seconds.<br /><br /> The cause was determined to be plant employees do not have secondary containment airlock training, and the airlock interlock did not have posted operating instructions.<br /><br /> Corrective actions include affixing permanent labels next to the interlock push button which provide instructions on how to appropriately open the doors. As an additional measure, plans are in place to replace the doors with doors that have windows. The need for training on proper airlock operation will also be evaluated for inclusion in general access training.
2632014007 | Monticello | 04/17/2014 | 06/12/2014 | ML14163A58 | <strong>Non-compliance with Technical Specification 3.4.9 - Reactor Coolant System Pressure and Temperature Limits</strong><br /><i>Abstract:&nbsp;</i>On April 17, 2014, plant personnel discovered a previously unrecognized failure to take appropriate actions of Technical Specification (TS) Limiting Condition for Operation 3.4.9. This failure occurred on seven prior occasions when the Reactor Pressure Vessel (RPV) pressure dropped below 0 psig. <br /><br /> The cause of the failure to take the appropriate TS actions was that station personnel did not recognize a vacuum was drawn on the RPV and the implications for compliance with Pressure-Temperature curves. <br /><br /> The Pressure Temperature Limits Report curves will be updated to recognize that the RPV may be operated at a vacuum.
2632014008 | Monticello | 05/15/2014 | 07/14/2014 | ML14195A27 | <strong>Opening Identified in Fire Barrier</strong><br /><i>Abstract:&nbsp;</i>On May 15, 2014, an unsealed conduit penetration was identified between two fire zones, Division I and Division II of safe shutdown equipment in the Emergency Filtration (EFT) Building, which does not meet the two hour fire barrier rating of the wall required per the Fire Hazards Analysis.<br /><br /> The cause of the unsealed penetration is unknown and is considered a legacy issue as this conduit was routed prior to 1991.<br /><br /> The EFT fire protection barrier will be restored to functional status and the penetration will be periodically inspected. The Fire Barrier Wall, Damper and Floor Inspection procedure will be revised to add use of additional tools (e.g., cameras or boroscope) to perform inspections on portions of fire barriers that are not easily accessed.
2632014009 | Monticello | 08/05/2014 | 09/30/2014 | ML14273A54 | <strong>Both Emergency Filtration Trains Inoperable</strong><br /><i>Abstract:&nbsp;</i>On August 5, 2014, the 'A' emergency filtration train (EFT) was out of service for charcoal filter replacement work; during that time 'B' EFT was placed in service to supply fresh filtered air to the Control Room. After the 'B' EFT had run for 12 minutes, a low flow alarm occurred and the 'B' EFT fan tripped. This resulted in both trains of emergency filtration being inoperable. Technical Specification Limiting Condition for Operation (LCO) 3.7.4 was not met and as a result, LCO 3.0.3 was entered at 16:01 hours which required the plant to be in Mode 4 within 37 hours.<br /><br /> The 'B' EFT fan tripped because the damper actuator failed due to poor quality of vendor refurbishment. The 'B' EFT trip caused the plant to enter LCO 3.0.3 due to the legacy operating procedure that permitted Operators to start the 'B' EFT while 'A' EFT was inoperable for maintenance.<br /><br /> The failed actuator was subsequently replaced and post maintenance testing was satisfactorily completed. The EFT procedures will also be revised to restrict operation of the standby train while in protected status.
2632014011 | Monticello | 12/28/2014 | 02/26/2015 | ML15057A53 | <strong>Two Emergency Diesels Inoperable due to Human Error</strong><br /><i>Abstract:&nbsp;</i>On December 28, 2014, during performance of the surveillance test for the 12 Emergency Diesel Generator (EDG) the Non-Licensed Operator inappropriately adjusted the local 11 EDG governor setting. The correct action was to adjust 12 EDG governor setting. As a result, both EDGs were declared inoperable.<br /><br /> The root cause of this event is that insufficient controls were in place to prevent the operator from manipulating the wrong component when latent issues existed.<br /><br /> The administratively inoperable 12 EDG was declared operable and operators completed actions to return 11 EDG to operable status following procedures and system walk down. The procedure for controlling protected equipment will be enhanced and human performance tool usage expectations were upgraded regarding the operation of Technical Specification related equipment to help prevent recurrence.
2652014001 | Quad Cities 2 | 03/31/2014 | 05/30/2014 | ML14163A00 | <strong>Control Rod Drive Hydraulic Control Unit Scram Inlet Isolation Valve Pressure Boundary Leak</strong><br /><i>Abstract:&nbsp;</i>On March 31, 2014, at 1302 hours, an Inservice Inspection Program VT-2 examination of the Unit 2 Control Rod Drive (CRD) Hydraulic Control Unit (HCU) ASME Class 2 piping and components was being performed. An apparent through-wall valve body leak of approximately two drops per minute was discovered on the 2-0305-101-18-27 CRD HCU Scram Insert Isolation Valve. This valve is subjected to full reactor pressure during normal service and during this inspection. This valve is the isolation valve to the reactor vessel CRD drive housing, and since it is the first isolation boundary off of the reactor vessel, it therefore cannot be isolated from the reactor coolant system to allow repairs. The valve was declared inoperable, Technical Specifications LCO 3.4.4 Condition C was entered, and the Unit was shutdown and depressurized to effect repairs. <br /><br /> On April 1, 2014, the 2-0305-101-18-27 valve was removed from the system and shipped for analysis. It was determined that the through wall leak that developed was the direct result of an inherent manufacturing defect that eventually propagated to the valve surface following years of pressure and temperature cycles that the system normally experiences. <br /><br /> Corrective actions included replacing the failed isolation valve and performing additional CRD system inspections. A root cause analysis was performed and no additional contributing factors were identified. <br /><br /> The safety significance of this event was minimal since the leakage rate was very small and full scram capability was maintained by the control rod. Due to the impact on the reactor coolant pressure boundary, this report is submitted in accordance with the requirements of 10 CFR 50.73(a)(2)(ii)(A), which requires the reporting of any event or condition that results in the condition of the nuclear power plant, including its principal safety barriers, being seriously degraded. Since a plant shutdown was completed as required by the plant Technical Specifications, this report is also submitted in accordance with the requirements of 10 CFR 50.73(a)(2)(i)(A), which requires the reporting of the completion of any nuclear plant shutdown required by the plant's Technical Specifications.
2652014002 | Quad Cities 2 | 04/02/2014 | 06/20/2014 | ML14195A00 | <strong>Cable Tray Fire Caused by Non-Conforming Cable Routing</strong><br /><i>Abstract:&nbsp;</i>On April 2, 2014, at 1228 hours, a Fire Alarm System (FAS) alarm was received for the Unit 2 D heater bay area. Although entry into the room at the time identified only a steam leak, subsequently various spurious alarms and electrical system anomalies occurred.<br /><br /> At 1303 hours, Unit 2 was manually scrammed, the turbine was tripped, and the main steam isolation valves (MSIVs) were closed to ensure the steam leak was isolated. A fire was identified to have occurred in the D heater bay (an area of the plant containing the high pressure (final stage) D feedwater heaters, and several Unit 2 cable trays and risers). The fire was extinguished by the automatic wet pipe sprinkler fire suppression system.<br /><br /> At 1340 hours, due to the manual de-energizing of safety-related motor control center (MCC) 29-1 in the reactor building in response to notification that smoke had been observed, an ALERT level Emergency Action Level classification was declared as HA3 (fire in a vital area affecting safety system equipment). The emergency was terminated at 2132 hours.<br /><br /> The cause of the event was an existing cable flaw that was caused by cable routing that exceeded the required minimum static bend radius.<br /><br /> Corrective actions included repairing impacted cables, replacing the failed steam seal expansion joint, operating procedure revisions, and additional inspections/tests.<br /><br /> The safety significance of this event was minimal. Given the impact on multiple systems, this report is submitted in accordance with 10 CFR 50.73 (a)(2)(iv)(A) for manual or automatic actuation of any of the systems listed in paragraph (a)(2)(iv)(B); in accordance with 10 CFR 50.73 (a)(2)(v)(D) for an event that could have prevented the fulfillment of the safety function of systems needed to mitigate the consequences of an accident; and in accordance with 10 CFR 50.73(a)(2)(i)(A), for the completion of a nuclear plant shutdown required by the plant's Technical Specifications.
2652014003 | Quad Cities 2 | 05/06/2014 | 07/15/2014 | ML14212A03 | <strong>RPS Pressure Switch for Condenser Vacuum - Low Inoperable and Exceeded Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On May 16, 2014, with Unit 2 at full power, a main condenser flow reversal was performed. During the flow reversal, anomalous indications were noted for the 2C condenser [COND] backpressure response. As a result of the slow response, RPS pressure switch [PS] 2-0503-B was declared inoperable. This pressure switch is one of the inputs into the Reactor Protection System (RPS) [JD] for the Turbine Condenser Vacuum-Low function. The isolation valve [RTV] for this pressure switch was found partially closed. The valve was opened and normal indication was restored.<br /><br /> During the review of this event, it was identified that the RPS pressure switch was inoperable since May 6, 2014. Unit 2 did not meet the required number of channels per TS 3.3.1.1, Function 10, Turbine Condenser Vacuum-Low, when transitioning to MODE 1 at 2252 on May 6, 2014, as required by TS 3.0.4, and did not take the actions required in the allowed outage time.<br /><br /> The safety significance of this event was minimal. Sufficient redundant condenser backpressure instrumentation was operable to maintain scram capability and the RPS safety function. This event is reportable as an operation or condition prohibited by plant Technical Specifications per 10 CFR 50.73(a)(2)(i)(B).
2652014004 | Quad Cities 2 | 11/04/2014 | 12/30/2014 | ML15008A02 | <strong>Unit 2 HPCI Inlet Drain Pot Level Switch Failure</strong><br /><i>Abstract:&nbsp;</i>On November 4, 2014, the Unit 2 High Pressure Coolant Injection (HPCI) system was isolated to perform planned maintenance and surveillance activities. During performance of the HPCI Drain Pot Level Switch, Valve and Alarm Functional Verification, the Unit 2 HPCI Inlet Drain Pot Level Switch failed to reposition as designed. Failure of the level switch could allow an undetected buildup of water in the steam supply lines, which could result in the failure of the HPCI turbine. It was determined that this condition would have resulted in declaring the Unit 2 HPCI inoperable and a notification to the NRC was made. (ENS 50593)<br /><br /> The Unit 2 HPCI Inlet Drain Pot Level Switch is used to detect a failure of the normal pathway of the HPCI steam line drains and opens an alternate pathway for condensate removal. Since this alarm was nonfunctional, the steam trap bypass valve was manually opened prior to the restoration of HPCI on November 5, 2014. Temporary procedures have been implemented to verify periodically that the HPCI inlet drain pot is clear of condensate and the steam trap bypass valve remains open. These actions will provide reasonable assurance that the HPCI steam supply line will be free from condensate to support the operability of HPCI.
2692014001 | Oconee 1, Oconee 2, Oconee 3 | 03/28/2014 | 05/27/2014 | ML14149A47 | <strong>Unanalyzed condition associated with the 13.8kV emergency power cables located in the underground trench.</strong><br /><i>Abstract:&nbsp;</i>For the 13.8kV Keowee Hydroelectric Station (KHS) power cables contained in the underground trench to both transformer CT-4 and to the Protected Service Water (PSW) system, single failure analysis considered a three-phase bolted fault at the end connections and a phase-to-ground fault as bounding conditions. This single failure analysis was questioned in a recent NRC inspection as not being bounding. Duke Energy evaluated the issue and concludes the cables to be operable but nonconforming with the current licensing basis due to a lack of documentation. Additional cable analysis and/or testing is needed. The results of planned power cable analysis and/or testing will provide the necessary information needed to update the licensing basis documentation. This condition is conservatively being reported in accordance with 10 CFR 50.73(a)(2)(ii)(B) as an event or condition that resulted in the nuclear power plant being in an unanalyzed condition that significantly degraded plant safety. <br /><br /> The preliminary apparent cause of this event is a missed opportunity to update the licensing basis in 2002 when the underground trench and cables were modified, and again in 2013, when the PSW system 13.8kV power cables and control cables were placed in service. Duke will complete the causal evaluation and as necessary, supplemented the report following the conclusion of that evaluation. Duke Energy used a risk-informed approach to determine the risk significance associated with the condition. The analysis results concluded that the postulated single failure of the Keowee emergency power supply represents an insignificant impact to plant risk.
2692014002 | Oconee 1, Oconee 2, Oconee 3 | 11/25/2014 | 01/26/2015 | ML15028A19 | <strong>Deficiency in Loss of Coolant Accident Analysis Adversely Affected Predicted Peak Cladding Temperature</strong><br /><i>Abstract:&nbsp;</i>On November 25, 2014, Duke Energy Carolinas, LLC (Duke Energy) reviewed AREVA 10 CFR 50.46 Notification Letter FAB 14-00631, which indicated a deficiency had been discovered in the uranium thermal conductivity models used in the Oconee Nuclear Station (ONS) Loss of Coolant Accident (LOCA) analysis of record. When the model deficiency was corrected, the ONS Large Break LOCA Peak Cladding Temperature (PCT) exceeded 2200 degrees F. The Oconee licensing basis PCT is evaluated for compliance with the criterion in 10 CFR 50.46(b)(1) and must not exceed a PCT of 2200 degrees F. This issue was reported to the NRC as an 8-hour non-emergency notification on November 25, 2014 (NRC Event Notification EN 50640). On December 17, 2014, Duke Energy submitted a Special Report as required by 10 CFR 50.46 (ML14353A214).<br /><br /> Once notified, Duke Energy implemented administrative restrictions to ensure that the Oconee Units would not violate the reduced linear heat rate (LHR) limits specified by AREVA.<br /><br /> There are no new regulatory commitments contained within this Licensee Event Report.
2712014001 | Vermont Yankee | 09/29/2014 | 11/21/2014 | ML14330A24 | <strong>Inoperable Emergency Diesel Generator due to Hydraulic Lock from Internal Jacket Coolant Water Leak</strong><br /><i>Abstract:&nbsp;</i>On September 29, 2014, with reactor power operation at 96 percent power, the 'A' train Emergency Diesel Generator (EDG) did not complete the starting sequence during a scheduled Technical Specification monthly surveillance. The direct cause of the event was a hydraulic lock condition between opposing pistons on compression stroke in the #6 cylinder which prevented the EDG from turning. This condition resulted from an internal Jacket Coolant Water leak through a copper gasket that provides a sealing surface inside the cylinder. The copper gasket had been in service since installation during a cylinder liner replacement in 1992. There were no indications of a leak prior to its discovery, therefore the exact time when a hydraulic lock condition developed is unknown. The 'A' EDG was potentially inoperable since the completion of the last successful surveillance that demonstrated its capability to meet its safety function on August 25, 2014. Based on the ability of the 'A' EDG to be recovered within a few hours, the availability of the redundant 'B' train EDG, and the availability of normal and alternate offsite and onsite power sources capable of supplying power to engineered safety feature loads during and following design basis accidents, this event did not pose a threat to public health and safety.
2722014001 | Salem 1, Salem 2 | 01/07/2014 | 03/10/2014 | ML14069A24 | <strong>High Energy Line Break Door Blocked Open During Maintenance Activity</strong><br /><i>Abstract:&nbsp;</i>On January 7, 2014, Salem determined that control of the Turbine Driven Auxiliary Feedwater (TDAFW) pump enclosure High Energy Line Break (HELB) barrier door had been inadequate for work which was performed in the room on October 3, 2013. The cause of this event is attributed to an organizational failure to ensure that guidance provided in plant HELB program procedures contained sufficient justification for compensatory actions used for barrier impairments. <br /><br /> This event is being reported pursuant to 10 CFR 50. 73(a)(2)(ii)(B) as "The nuclear power plant being in an unanalyzed condition that significantly degraded plant safety"; 10 CFR 50. 73(a)(2)(v) as "Any event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to: (B) Remove residual heat, and (D) Mitigate the consequences of an accident"; and 10 CFR 50.73(a)(2)(vii) as "Any event where a single cause or condition caused at least one independent train or channel to become inoperable in multiple systems or two independent trains or channels to become inoperable in a single system designed to: (B) Remove residual heat, and (D) Mitigate the consequences of an accident."
2722014002 | Salem 1 | 04/08/2014 | 06/04/2014 | ML14155A28 | <strong>Manual Reactor Trip due to Loss of the 11 Steam Generator Feedwater Pump</strong><br /><i>Abstract:&nbsp;</i>On April 8, 2014 at 2112, Salem Unit 1 control room operators received an alarm indicating failure of the 12 Essential Controls Inverter. At 2113, operators observed indications of a trip of the 11 Steam Generator Feedwater Pump (SGFP). Operators manually initiated a Main Turbine automatic runback by manually tripping the 11 SGFP in accordance with procedures. At 2114, operators manually tripped the reactor due to a low level in the 13 Steam Generator (SG). All control rods fully inserted on the trip. All three Auxiliary Feedwater (AFW) pumps started as expected in response to low SG levels and decay heat was removed by the steam dumps to the main condenser. Operators entered the emergency procedures for the plant trip and stabilized the plant in Mode 3 (HOT STANDBY).<br /><br /> The cause of this event was due to a loss of power to the 11 SGFP speed probes. A ground on the electrical bus providing power to the speed probes was repaired.<br /><br /> This report is made in accordance with 10 CFR 50.73(a)(2)(iv)(A), "any event or condition that resulted in manual or automatic actuation of any of the systems listed in paragraph (a)(2)(iv)(B)" for a manual reactor trip and automatic actuation of the AFW system.
2722014003 | Salem 1 | 04/13/2014 | 06/04/2014 | ML14155A27 | <strong>Reactor Trip due to Actuation of Generator Protection</strong><br /><i>Abstract:&nbsp;</i>On April 13, 2014 at 2113, Salem Unit 1 experienced an automatic reactor trip. The direct cause of the reactor trip was a generator lockout resulting from a main generator transformer overall differential relay trip. All control rods fully inserted on the trip. All three Auxiliary Feedwater (AFW) pumps started as expected in response to low steam generator levels and decay heat was removed by the steam dumps to the main condenser. Operators entered the emergency procedures for the plant trip and stabilized the plant in Mode 3 (HOT STANDBY).<br /><br /> The Main Generator Overall Differential Relay tripped due to a failed wiring termination on the C Phase Neutral Generator Current Transformer. The failed wiring termination was repaired.<br /><br /> This report is made in accordance with 10 CFR 50.73 (a)(2)(iv)(A), "...any event or condition that resulted in manual or automatic actuation of any of the systems listed in paragraph (a)(2Xiv)(B)..." due to an automatic reactor trip and actuation of the AFW system.
2722014004 | Salem 1 | 05/07/2014 | 07/03/2014 | ML14184B29 | <strong>Reactor Trip due to Actuation of Generator Protection</strong><br /><i>Abstract:&nbsp;</i>On May 7, 2014 at 0456, Salem Unit 1 experienced an automatic reactor trip. The direct cause of the reactor trip was a generator lockout resulting from a main generator differential relay trip. All control rods fully inserted on the trip. All three Auxiliary Feedwater (AFW) pumps started as expected in response to low steam generator levels and decay heat was removed by the steam dumps to the main condenser. Operators entered the emergency procedures for the plant trip and stabilized the plant in Mode 3 (HOT STANDBY).<br /><br /> The Main Generator Differential Relay tripped due to a failed wiring termination on the A Phase Neutral Generator Current Transformer (CT). The failed wiring termination was repaired.<br /><br /> This report is made in accordance with 10 CFR 50.73 (a)(2)(iv)(A), " ... any event or condition that resulted in manual or automatic actuation of any of the systems listed in paragraph (a)(2)(iv)(B) ... " due to an automatic reactor trip and actuation of the AFW system.
2722014005 | Salem 1 | 08/27/2014 | 10/21/2014 | ML14295A04 | <strong>Loss of a Safety Function Resulting from Safety Injection Pump Breaker Failure</strong><br /><i>Abstract:&nbsp;</i>On August 27, 2014, the 11 Safety Injection (SI) pump was being tagged out for planned maintenance. At 0243, the 11 SI pump was declared inoperable when its 4 kilovolt (kV) supply breaker was racked out. At 0248, the 12 SI pump failed to start on demand when operators were attempting to fill the 14 SI Accumulator. The unit entered Technical Specification (TS) 3.0.3 for inoperability of two SI pumps. At 0301, the 11 SI pump was realigned, tested and returned to service and the unit exited TS 3.0.3. The apparent cause of the 12 SI pump failure to start was due to a failure of the spring release solenoid in the pump's breaker.<br /><br /> This report is made in accordance with 10 CFR 50.73 (a)(2)(v)(D), "Any event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed. to: ...(D) Mitigate the consequences of an accident" for inoperability of both SI Pumps.
2722014006 | Salem 1 | 10/19/2014 | 04/08/2015 | ML15098A35 | <strong>Manual Reactor Trip due to Main Power Transformer Low Oil Level</strong><br /><i>Abstract:&nbsp;</i>On October 19, 2014, at 2051, while performing a unit shutdown in preparation for its twenty-third refueling outage, Salem unit 1 control room operators initiated a manual reactor trip at approximately 20 percent reactor power. The manual reactor trip was inserted due to concerns with the 1B Main Power Transformer, which had been in service with identified oil leakage. All control rods fully inserted on the trip. The auxiliary feedwater system actuated as designed in response to low steam generator levels. Decay heat removal was via the steam dumps to the main condenser. The plant was stabilized in Hot Standby.<br /><br /> Operators failed to recognize parameters on 1B Main Power Transformer which would have required them to enter an Adverse Condition Monitoring Plan. Entry into the plan would have required them to perform a fast load reduction and remove the main turbine from service at 40 percent power. Salem Generating Station will fully integrate procedure use and adherence principles and behaviors throughout Operations.<br /><br /> This report is made in accordance with 10 CFR 50.73 (a)(2)(iv)(A), "Any event or condition that resulted in manual or automatic actuation of any of the systems listed in paragraph (a)(2)(iv)(B) ... "for a manual reactor trip and for automatic actuation of the auxiliary feedwater system.
2752014001 | Diablo Canyon 1, Diablo Canyon 2 | 01/28/2014 | 03/31/2014 | ML14090A45 | <strong>Technical Specification 3.4.3, Reactor Coolant System Pressure Limit Violation During Vacuum Refill due to Human Error</strong><br /><i>Abstract:&nbsp;</i>On January 28, 2014, Pacific Gas and Electric (PG&E) recognized Regulatory Operating Experience at another station to be applicable to Diablo Canyon Power Plant (DCPP). An NRC inspection report describes a failure to comply with reactor coolant system (RCS) Pressure and Temperature (P/T) Limits when RCS pressure drops below 0 pounds per square inch gauge (PSIG). At the time of discovery, DCPP's Pressure Temperature Limit Report (PTLR) only described pressures above 0 PSIG. However, since 2001, DCPP's analyses and procedures allow drawing a vacuum during RCS refill following refueling. Therefore, PG&E is conservatively reporting RCS pressure below 0 PSIG as a violation of Technical Specification 3.4.3 "RCS Pressure and Temperature (PIT) Limits."<br /><br /> The apparent cause of not maintaining RCS pressure within the limits described in the PTLR was legacy design error. PG&E interpreted the PTLR to only apply to upper pressure limits, and therefore did not consider it in conflict with the adoption of the vacuum refill analysis and procedure. Corrective actions included revising the PTLR to specify 0 pounds per square inch absolute as the lower limit. Therefore, the explicit PTLR compliance error during vacuum refill did not adversely affect the health and safety of the public or station personnel.
2752014003 | Diablo Canyon 1, Diablo Canyon 2 | 03/06/2014 | 02/02/2015 | ML15033A48 | <strong>Unanalyzed Condition Affecting Unit 1 and 2 Emergency Diesel Generators, Tornado Missiles</strong><br /><i>Abstract:&nbsp;</i>On March 6, 2014, at 09:06 PST, with Diablo Canyon Power Plant (DCPP) Unit 1 in Mode 5 and Unit 2 in Mode 1 at 100 percent power, DCPP concluded the Unit 1 and Unit 2 emergency diesel generators (EDGs) radiator ventilation exhaust plenums were not sufficiently analyzed for tornado missiles. Additionally, DCPP identified that the EDGs engine exhaust pipes were not protected from tornado missiles. DCPP staff performed an operability assessment and concluded the EDGs remained operable. On March 6, 2014, at 16:33 PST, DCPP made an 8-hour, nonemergency report to the NRC (Event Notification 49879) per 10 CFR 50.72(b)(3)(ii)(B), "Unanalyzed Condition." During review of extent of condition this issue was determined to affect the ventilation systems associated with Unit 1 and Unit 2 480 V AC switchgear and battery/inverter equipment. Event Notification 49879 was updated on September 9, 2014, at 19:45 PDT.<br /><br /> The cause was due to a misunderstanding of the DCPP tornado missile protection licensing basis. DCPP incorrectly extended the NRC approval of limited tornado protection exceptions to the EDG ventilation system redesign and modification. Corrective actions included retraining and requalifying all employees who perform 10 CFR 50.59 screens and evaluations including commissioning a Licensing Basis Verification Project to ensure the Current Licensing Basis is clear and to correct deficient 10 CFR 50.59 evaluations. DCPP is evaluating tornado missile risk using a probabilistic technique and will be pursuing a change to the tornado missile licensing basis via license amendment request.
2752014004 | Diablo Canyon 1, Diablo Canyon 2 | 10/31/2014 | 03/30/2015 | ML15089A59 | <strong>Actuation of Six Emergency Diesel Generators due to Loss of Offsite Power</strong><br /><i>Abstract:&nbsp;</i>On October 31, 2014, at 17:40 PDT, during a medium to heavy rain, Pacific Gas and Electric Company (PG&E) lost its 230 kV offsite power source at the Diablo Canyon Power Plant when an insulator in the 230 kV switchyard flashed over. This resulted in the valid start of all Unit 1 and 2 emergency diesel generators (EDGs), three per unit. All EDGs successfully started, but did not load since all associated electrical buses remained energized by auxiliary power. All systems operated as designed with no problems observed. The 230 kV offsite power source is the only offsite power system designed to be immediately available following an accident. However, the safety-related onsite EDGs would have provided power to mitigate the consequences of an accident while the 230 kV system was unavailable. On October 31, 2014, at 23:07 PDT, PG&E made an 8-hour nonemergency report to the NRC. The 230 kV offsite power was declared operable on November 1, 2014, at 02:29 PDT.<br /><br /> PG&E completed a root cause evaluation and determined that inadequate organizational oversight and alignment resulted in ineffective and untimely execution of planned corrective actions intended to prevent excessive buildup of environmental contaminants on the 230 kV insulators.<br /><br /> This event did not adversely affect the health or safety of the public.
2772014001 | Peach Bottom 2, Peach Bottom 3 | 05/21/2014 | 07/17/2014 | ML14202A34 | <strong>Unanalyzed Condition due to Broken Wires in Breakers Used for Appendix R Post-Fire Safe Shutdown</strong><br /><i>Abstract:&nbsp;</i>On May 21, 2014 at approximately 1100 hours, based on inspections being performed as part of an extent-of-condition review, it was determined that an unanalyzed condition existed that potentially impacted the ability to mitigate an Appendix R fire postulated to occur in the control room and cable spreading room. Broken wires leading to the alternate fuse for the 125vdc control power supply had been previously identified in the breaker enclosures for three 4 kV safety-related breakers. In the event of an Appendix R fire in the control room and cable spreading room, with a fire-induced short circuit that results in a blown primary control power fuse, the broken wires would result in the loss of control power to the affected breakers. This would impact the ability to close the breaker locally after the control room has been evacuated. Instead of using the handswitch on the front of the breaker enclosure to close the breaker, the operator would have to open the enclosure door and push the manual close button on the breaker.<br /><br /> Based on the plant's fire protection defense-in-depth features and the ability of the operator to perform a simple alternate action to close the breaker, this event would not impact the ability to reach and maintain a safe shutdown condition in the event of an actual fire.
2772014002 | Peach Bottom 2, Peach Bottom 3 | 08/23/2014 | 10/17/2014 | ML14297A08 | <strong>Emergency Service Water Pinhole Leak Results in Condition Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On August 23, 2014, a pin-hole leak was identified in a 6" diameter pipe elbow in the Emergency Service Water (ESW) system. The piping is classified as safety-related, ASME Code Class 3, moderate energy piping. Engineering evaluated the piping flaw and determined that it did not meet NRC approved ASME code case requirements for acceptance of flaws in Class 3 moderate energy piping. As a result, both subsystems of the ESW System were declared inoperable at 1300 hours on Saturday, August 23, 2014, for both Units 2 and 3. Technical Specification (TS) 3.7.2, Condition B, requires the unit to be in Mode 3 within 12 hours due to two inoperable ESW subsystems.<br /><br /> Ultrasonic examination of the pipe was performed to determine the size and nature of the flaw. The flaw was caused by internal pitting likely caused by corrosion and flow effects of river water in the elbow. A risk assessment was performed and it was determined that the condition met the requirements for requesting a Notice of Enforcement Discretion (NOED) from the NRC. A verbal request was made to the NRC to extend the required completion time for TS 3.7.2, Condition B by 48 hours, to allow for additional time to obtain an emergent ASME code relief request. The NRC granted the NOED at 1922 hours on August 23, 2014.
2772014003 | Peach Bottom 2 | 10/29/2014 | 12/05/2014 | ML14342B00 | <strong>Containment Leakage Limit Exceeded due to Through-Seat Leakage of Feed Water Check Valves</strong><br /><i>Abstract:&nbsp;</i>On 10/29/14 at approximately 1100 hours, Engineering personnel determined that the N-9A primary containment penetration pathway had leakage that exceeded the maximum allowable primary containment leakage rate (La) value required by Technical Specification (TS) 5.5.12, Primary Containment Leakage Rate Testing Program. This determination was based on as-found leakage through the seats of two redundant feed water check valves (CHK-2-06-28A and CHK-2-06-96A) that are Primary Containment Isolation Valves (PCIVs). The cause of the deficiency in both swing check valves was due to operational wear on the check valve pivot shaft and associated bushings. Both check valves were repaired during the Refueling Outage and as-left leak testing proved appropriate leak-tightness of the check valves in the closed position. Additional corrective actions are being assessed as part of a causal analysis being performed in accordance with the station's corrective action program. There were no actual safety consequences associated with this event.
2802014001 | Surry 1, Surry 2 | 03/29/2014 | 05/27/2014 | ML14154A08 | <strong>Closed Service Water Valve Results in Exceeding Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>At 11:40 on March 29, 2014, with both Unit 1 and Unit 2 operating at 100% power, the Unit 1D service water header was declared inoperable as a result of indications received during testing. The direct cause of the indications was due to a mostly closed service water header isolation valve for the Unit 1D service water header. In October 2013, following valve replacement, the valve handwheel was reoriented causing the valve to become mostly closed while indicating open. Therefore, the Unit 1D service water header was inoperable from October 21, 2013 until March 29, 2014 and Technical Specification limiting conditions of operation were exceeded twice during timeframes when one of two other operable service water headers was tagged out for maintenance. Also, as a result of the restricted flow condition, a service water pump that supplies cooling to a charging pump was also determined to be inoperable beyond its Technical Specification limiting conditions of operation. Therefore, this report is being submitted, pursuant to 10 CFR 50.73(a)(2)(i)(B), for operations prohibited by Technical Specifications. Based on the risk assessment of this event, the risk impact was determined to be very small and, as a result, the health and safety of the public were not affected.
2812014001 | Surry 2 | 04/30/2014 | 06/23/2014 | ML14182A08 | <strong>Pressurizer Safety Valves Fail As-Found Setpoint Testing</strong><br /><i>Abstract:&nbsp;</i>On April 30, 2014, with Unit 2 in cold shut down for a refueling outage, the Unit 2A pressurizer safety valve failed its as-found test due to the lift setting being lower than the setpoint tolerance allowed by Technical Specifications.<br /><br /> On May 6, 2014, the Unit 2C pressurizer safety valve also failed its as-found test due to the lift setting being lower than the setpoint tolerance allowed by Technical Specifications.<br /><br /> The as-found pressurizer safety valve lift settings were evaluated and it was determined the valves were capable of performing their safety function with the low as-found lift settings. Therefore, the health and safety of the public were not affected.<br /><br /> This report is being submitted, pursuant to 10 CFR 50.73(a)(2)(i)(B), for operation prohibited by Technical Specifications.
2812014002 | Surry 2 | 10/13/2014 | 12/09/2014 | ML14350A21 | <strong>Reactor Trip due to Loose Termination on Reactor Trip Relay</strong><br /><i>Abstract:&nbsp;</i>On October 13, 2014 at 07:58, with Units 1 and 2 at 100% power, Unit 2 experienced a reactor trip due to a spurious opening of the Unit 2 "B" reactor trip breaker due to a loose screw on a reactor protection trip relay for the reactor trip breaker.<br /><br /> All three auxiliary feedwater pumps automatically started on low-low steam generator water level providing flow to the steam generators. The rapid increase in steam generator pressure on the relief valve setpoints resulted in the lifting of all three steam generator power operated relief valves. Unit 2 was placed in hot shutdown and the health and safety of the public were not affected. The loose screw on the reactor protection trip breaker relay was tightened and the breaker was closed successfully. Remaining connections on the Unit 2 relay control circuitry were checked for tightness. Unit 1 reactor trip breaker relay control circuitry will be checked for tightness at the next available opportunity. Torque requirements for terminal screws will be incorporated into the Surry Electrical Installation Specification and applicable procedures will be revised to include the torque requirements.<br /><br /> This report is being submitted pursuant to 10CFR50.73(a)(2)(iv)(A) as an event that resulted in the automatic actuation of the Reactor Protection System and the Auxiliary Feedwater System.
2822014001 | Prairie Island 1 | 04/30/2014 | 06/27/2014 | ML14178B27 | <strong>D1/D2 EDG's Inoperable due to Outside Air Temperature Greater than 97 Degrees Fahrenheit</strong><br /><i>Abstract:&nbsp;</i>During a review of a draft D1/D2 Emergency Diesel Generator (EDG) Room Electrical Component and Relay Cabinet Temperature Calculation a list was generated to determine all electrical components in the D1/D2 rooms. The D1/D2 Room Electrical Component and Relay Cabinet Temperature Calculation used Engineering Changes (EC) 19815 and 19915 as inputs for what devices should be evaluated. It was discovered that EC19815 and EC19915 did not address all components in the D1/D2 rooms. The purpose of EC19815 and EC19915 was to determine the maximum ambient temperature data for electrical components and use that information in Operability Recommendation (OPR) 01327157. OPR 01327157 uses the engineering evaluations to justify the assessed capability of the equipment in the D1/D2 rooms up to 130 degrees F. Investigation began into the temperature rating of the equipment that was not in EC19815 and EC19915. Preliminarily it has been determined that four (4) components have a rating of 120 degrees F.<br /><br /> Based on an engineering analysis, D1/D2 would have been inoperable for 415 minutes on June 7, 2011, 36 minutes on July 2, 2012, 212 minutes July 4, 2012, 272 minutes July 6, 2012, and 43 minutes on May 14, 2013. The root cause evaluation is currently in progress and the long-term corrective actions have not been identified.
2822014002 | Prairie Island 1 | 06/03/2014 | 01/30/2015 | ML15030A36 | <strong>Emergency Diesel Generators Declared Inoperable due to Not Meeting High Energy Line Break Requirements</strong><br /><i>Abstract:&nbsp;</i>D1 and D2 Emergency Diesel Generators (EDG) were declared inoperable at 1902 CDT on June 3, 2014, due to the station identifying that the Turbine Building High Energy Line Break (HELB) heat-up analysis temperature of 253 degrees Fahrenheit exceeded the maximum temperature limit of 200 degrees Fahrenheit for both diesel generators supply and exhaust fan blade positioners.<br /><br /> Technical Specification (TS) Limiting Condition for Operation (LCO) 3.8.1 Condition B was entered for both EDG's and LCO 3.8.1 Condition E was entered for two EDGs inoperable on the same unit. The EDGs could start and run if required at the time of entry.<br /><br /> This condition is reportable per 10 CFR 50.73(a)(2)(v)(D), any event or condition that could have prevented the fulfillment of a safety function of structures or systems that are needed to: mitigate the consequences of an accident.<br /><br /> The Q-List Project personnel did not recognize the potential Condition Adverse to Quality that was created if newly upgraded Safety Related components were not evaluated for Environmental Qualification (EQ) program applicability in a timely manner.
2822014003 | Prairie Island 1 | 06/23/2014 | 08/20/2014 | ML14232A32 | <strong>Emergency Diesel Generator Auto Start due to Degraded Bus Voltage Signal</strong><br /><i>Abstract:&nbsp;</i>At 1107 on June 23, 2014, Safeguards Bus 15 received a degraded voltage signal that resulted in the bus load shed and the automatic start of the D1 Emergency Diesel Generator (EDG). Bus 15 reenergized to normal voltage after the source breaker from D1 (EDG) automatically closed. This event is reportable under 10 CFR 50.73(a)(2)(iv)(A); Any event or condition that results in valid actuation of emergency AC electrical power systems, EDG. The initiating condition was a failure of the Load Tap Changer (LTC) on the 10-Bank transformer which affected voltage to the normal offsite power supply to the 1R transformer and Safeguards Bus 15. The Causal Evaluation determined that the failure in the Load Tap Changer (LTC) for control for Prairie Island Nuclear Generating Plant (PINGP) transformer bank (TR 10) was caused by the failure of the 84Y coil from a General Electric (GE) CR120A relay that was installed in 1967. There are no periodic inspections or replacement activities (preventive maintenance) to prevent the relay failure. Relay cycling was validated during fall 2013 LTC control circuit upgrade. TR 10 is Transmission and Distribution (T&D) owned equipment installed in the PINGP switchyard. Corrective action has been initiated to evaluate T&D Preventive Maintenance (PM) strategy associated with switchyard components that were credited for offsite power in accordance with SOER 99-1 and develop PM strategy. Corrective action has been initiated to evaluate a potential design change for T&D owned LTC control circuit to eliminate the single component vulnerability.
2822014004 | Prairie Island 1, Prairie Island 2 | 08/08/2014 | 03/31/2015 | ML15090A65 | <strong>Unanalyzed Condition due to Lack of Appropriate Fuse Protection - Supplement</strong><br /><i>Abstract:&nbsp;</i>On August 8, 2014, the Appendix R program engineer identified a licensee reportable legacy issue. As a result of external industry operating experience, a drawing review was performed and it was determined that the control circuits for the DC Emergency Oil Pumps for both Unit 1 and Unit 2 are not fused properly. Therefore, an overload within the control circuit could result in a fire that could propagate to multiple fire areas affecting safe shutdown equipment that could be compromised, which affects the 10 CFR 50 Appendix R safe shutdown analysis. Based on this information, the determination was made that this condition meets the reporting criteria for 10 CFR 50.73(a)(2)(ii)(B), any event or condition that results in the nuclear power plant being in an unanalyzed condition that significantly degrades plant safety.<br /><br /> The causal evaluation determined that the plant designer did not fuse the DC Emergency Oil Pump circuit separate from the power cables because they were concerned that inadvertent fuse failure would fail the DC Emergency Oil Pump and damage the turbine bearings. Inconsistency in manufacturing of fuses at the time of design could lead to some fuses failing open even if the conditions should not have caused the fuse to fail open.<br /><br /> Corrective Actions have been initiated to modify the DC Emergency Oil Pump control circuit over-current protection to protect the control circuit from over-current conditions and perform an evaluation of the Service Building DC system to determine if there are other instances where protection was sacrificed for reliability.
2852014001 | Fort Calhoun | 01/08/2014 | 03/07/2014 | ML14069A34 | <strong>Reactor Shutdown due to Sluice Gate Failure</strong><br /><i>Abstract:&nbsp;</i>At approximately 2230 Central Standard Time (CST), on January 8, 2014, CW-14C, Traveling Screen Sluice Gate, motor operator shaft was found damaged (bent) by Operations personnel. At 2330 CST a large block of ice buildup was observed on top of the sluice gate caused by a pinhole leak in the backwash piping located directly above the CW-14C gate. At 0250 CST, January 9, 2014, Operations unsuccessfully attempted manual closing of CW-14C. At 0315 CST the station entered TS 2.0.1(1) due to all raw water (RW) pumps being declared inoperable. At 0518 CST the station commenced a reactor shutdown. At 0900 CST the station completed the reactor shutdown.<br /><br /> The root cause was determined to be that CW-14C MOV torque setting was at a value that allowed the stem to be bent. <br /><br /> CW-14C was lowered and then verified closed by divers. The flooding strategy for the Intake Structure was met at 0350 CST on January 10, 2014. RW Pumps AC-10A, AC-10B, AC-10C and AC-10D were declared operable and TS 2.0.1(1) was exited.
2852014002 | Fort Calhoun | 01/12/2014 | 03/12/2014 | ML14071A27 | <strong>Reactor Manual Trip due to Control Rod Misalignment</strong><br /><i>Abstract:&nbsp;</i>After reaching criticality on January 12, 2014, the control room attempted to reduce power ascension rate while at zero percent power by inserting Group 4 CEAs. All Group 4 CEAs inserted with the exception of control rod RC-10-41, which failed to move. Group 4 was inserted further until a 10 inches deviation existed between RC-10-41 and the remaining Group 4 CEAs. Power continued to slowly rise and the Control Room conservatively decided to manually trip the reactor with the existing deviation. On January 12, 2014, at 0323 the reactor was manually tripped due to reactor power rising with RC-10- 41 deviation. Control room entered EOP-00, Standard Post Trip Actions, and exited AOP-2. All CEAs inserted into the reactor as expected following the trip. <br /><br /> Troubleshooting determined that the rectifier for RC-10-41 had failed. <br /><br /> The failed CEDM rectifier and associated fuses for RC-10-41 were replaced. <br /><br /> Additional review of the rectifier failure is being performed and any significant findings will be addressed in a supplement to this LER if needed.
2852014003 | Fort Calhoun | 03/17/2014 | 05/14/2014 | ML14135A40 | <strong>Reactor Trip due to Stator Water Cooling Leak During Maintenance</strong><br /><i>Abstract:&nbsp;</i>On March 17, 2014, at 12:02 Central Daylight Time (CDT), a turbine trip and subsequent reactor trip occurred while operating at nominal 100 percent power. Maintenance was in progress on the main generator stator cooling system when system inventory was lost resulting in an automatic turbine trip due to low system pressure. Immediate response by operations personnel included implementing procedure emergency operating procedure (EOP) -00, Standard Post Trip Actions, and subsequent entry into procedure EOP-01, Reactor Trip Recovery. Based on plant system response this is considered an uncomplicated trip.<br /><br /> The station determined that the root cause of the plant trip was that operational risk was not effectively identified or mitigated by individuals throughout the organization.<br /><br /> The leak was isolated shortly after the trip by fully removing the probe and closing the isolation valve. Fort Calhoun Station will be implementing the Exelon risk management procedure, WC-AA-104, Integrated Risk Management. This procedure provides direction consistent with industry best practices, and requires individual review of each category of risk identification and mitigation.
2852014004 | Fort Calhoun | 04/24/2014 | 10/03/2014 | ML14276A59 | <strong>Unqualified Limit Switches Render Safety Equipment Inoperable</strong><br /><i>Abstract:&nbsp;</i>On April 24, 2014, during a review of previous conditions affecting equipment qualification it was identified that the environmental qualification of Namco EA180 series limit switches were not being properly maintained per vendor requirements. This condition was not verbally reported at the time of discovery as the condition was identified and resolved while the plant was in an extended shutdown. <br /><br /> A cause evaluation was completed and determined that technical requirements from the vendor manual for maintaining environmental qualification of the Namco EA180 series limit switches were not captured in the applicable plant procedure. <br /><br /> The applicable plant procedure has been revised to include vendor information for maintaining environmental qualification of the limit switches. The limit switch top cover gasket and screw assemblies for all environmentally qualified Namco EA180 series limit switches were replaced and torqued in accordance with vendor requirements.
2852014005 | Fort Calhoun | 06/27/2014 | 08/25/2014 | ML14238A71 | <strong>Technical Specification Violation of Containment Integrity</strong><br /><i>Abstract:&nbsp;</i>On Friday, June 27, 2014, during performance of a valve exercise test it was discovered that test swagelock plug was missing between the containment penetration and the associated outboard isolation valve. Technicians discovered the test swagelock plug resting on a nearby junction box and not in place on the containment penetration. The technicians immediately notified the Auxiliary Building Operator who was assisting with the surveillance test. Operations shift supervision were notified and operations declared containment inoperable per Technical Specification and entered a 1 hour limiting condition for operation (LCO) to restore containment integrity. The shift manager directed the technicians to reinstall the test swagelock plug on the containment penetration. At that point, operations declared containment operable and exited the associated Technical Specification LCO.<br /><br /> Maintenance personnel exhibited weak Human Performance tool Independent Verification usage. Station personnel completed the Containment Integrity checklists prior to all containment isolation boundary maintenance and/or LLRTs being completed.<br /><br /> Containment integrity was restored.
2852014006 | Fort Calhoun | 09/16/2014 | 11/12/2014 | ML14316A45 | <strong>Inoperability of Radiation Monitors due to an Error in Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>During an NRC inspection on September 16, 2014, it was discovered that the calibration procedure for Radiation Monitor (RM) - 091A/B uses a source that is above 1 Roentgen per hour (R/hr). This does not meet the technical specification requirement for calibration at least one decade below 1 R/hr. 1 R/hr is the lower limit of detection of the high range detector for the RM-091 instruments. Calibration at least one decade below 1 R/hr is not possible.<br /><br /> The most likely cause of the event is that a typographical error was introduced into license amendment request (LAR) during review process in 1993 and was not corrected prior to submittal to NRC.<br /><br /> A LAR (LIC-14-0122) was submitted to the NRC to correct the technical specification error.
2852014007 | Fort Calhoun | 12/17/2014 | 02/13/2015 | ML15050A24 | <strong>Plant Trip due to Moisture Intrusion into a Transformer Control Cabinet</strong><br /><i>Abstract:&nbsp;</i>On December 17, 2014, at 1014 Central Standard Time (CST), the Fort Calhoun Station (FCS) reactor tripped due to a loss of load signal from the main turbine. The loss of load signal actuates the reactor protective system (RPS) which tripped the plant. The trip of the turbine was caused by a spurious actuation of a relay on the station unit auxiliary transformer that normally provides power to 4160 VAC bus 1A2.<br /><br /> The root cause was that FCS had not ensured that an identified single point vulnerability for T1A-2 transformer was eliminated or had an adequate mitigating strategy.<br /><br /> The control cabinet sealing was improved to reduce moisture from the interior of the cabinet. The relay that caused the trip was removed from the trip circuit. The station will modify the control circuits to eliminate the single point vulnerability in the transformer control cabinets.
2862014001 | Indian Point 3 | 01/06/2014 | 03/04/2014 | ML14077A06 | <strong>Automatic Reactor Trip as a Result of Steam Flow/Feedwater Flow Missmatch with Low 33 Steam Generator (SG) Water Level due to the Failure of the 33 SG Feedwater Flow Controller</strong><br /><i>Abstract:&nbsp;</i>On January 6, 2014, the 33 Steam Generator (SG) steam flow (SF) Feedwater flow (FF) mismatch and SG level control deviation alarms annuniciated. Operators noticed the selected feedwater (FW) flow (FF) channel at zero and swapped to the alternate channel and noted both FW flow channels at zero. With the 33 SG level at approximately 10% and lowering, operators started actions to initiate a manual reactor trip (RT) when an automatic RT occurred on a SF/FF mismatch coincident with low 33 SG level. All control rods fully inserted and all required safety systems functioned properly with the exception of the intermediate range excore neutron flux detector N-35 which was undercompensated. The plant was stabilized in hot standby with decay heat being removed by the main condenser {SG}. The Auxiliary Feedwater System automatically started as expected due to SG low level from shrink effect. The Emergency Diesel Generators did not start as offsite power remained available and stable. Investigations determined the decreasing SG levels were due to reduced main FW flow as a result of a closed 33 Feedwater Regulating Valve (FRV). The closure of the 33 FRV-437 was due to no output from flow controller FC-437. The apparent cause was station personnel failed to apply lateral thinking and teamwork and question what other options were available besides procuring an identical controller. Corrective actions included replacing FC-437 and FC-417. A project to improve procurement and ease replacement of NUS modules will be developed. The event had no effect on public health and safety.
2862014002 | Indian Point 3 | 07/16/2012 | 03/10/2014 | ML14097A00 | <strong>Technical Specification (TS) Prohibited Condition due to an Inoperable Essential Service Water (SW) Header as a Result of a Socket Weld Leak in Code Class 3 SW Piping</strong><br /><i>Abstract:&nbsp;</i>On July 16, 2012, during operator rounds, a Service Water (SW) leak was discovered on a socket weld elbow of a three quarter inch diameter sample pipe connected to the 31 Component Cooling Water (CCW) Heat Exchanger (Hx) SW discharge pipe upstream of sample valve SWN-49-1. The leak was too small to quantify. The leak is on a component classified as ASME Section XI Code Class 3. The weld leak was evaluated and determined not applicable to acceptance under Code Case N-513-3. The condition was determined to have no impact on SW cooling safety function. The affected SW header was declared inoperable and Technical Specification (TS) 3.7.9 (SW System) entered until the applicable CCW loop for the 31 CCW Hx was isolated. TS 3.7.8 (CCW System) was entered for one CCW loop inoperable. At the time this condition was identified the condition was not recognized as being reportable. The apparent cause was crevice corrosion due to exposure of unlined carbon steel to brackish SW (chloride) environment in low flow or stagnant vent/drain piping. The corrective action was a complete replacement of the affected piping assembly during the TS allowed outage time (AOT). The event had no significant effect on public health and safety.
2862014003 | Indian Point 3 | 02/06/2014 | 04/07/2014 | ML14107A10 | <strong>Automatic Actuation of the Turbine Driven Auxiliary Feedwater Pump following Testing of the 31 Emergency Diesel Generator due to Non-SI Blackout Logic Defeated Reset</strong><br /><i>Abstract:&nbsp;</i>On February 6, 2014, the 32 Turbine Driven Auxiliary Feedwater Pump (AFWP) unexpectedly automatically actuated and started coincident with opening the 31 Emergency Diesel Generator (EDG) output breaker during performance of monthly functional test 3PT-M79A (31 EDG Functional Test). When the 31 EDG breaker was opened, the Non-Safety Injection (SI) Blackout Logic Defeated relay reset itself without operator actions. Normally the Non-Safety Injection (SI) Blackout Logic Defeated circuitry prevents automatic starting of equipment until manually reset. Operators verified the 32 AFWP was not required and restored the 32 AFWP to standby. The cause of the auto AFWP start was the Non-SI Blackout Logic Defeated reset pushbutton was stuck in the depressed position (open contacts). The failure was a degraded switch that created an open circuit in the Non-SI Blackout Logic Defeated reset circuit preventing relay 3-5/2A from properly sealing in and defeating the Non-SI Blackout relays (3-2/2A and 3-2/3A) functions when the 31 EDG output breaker was manually opened. Corrective action was replacement of the pushbutton. The event had no effect on public health and safety.
2862014004 | Indian Point 3 | 08/13/2014 | 08/01/2016 | ML16224B01 | <strong>Automatic Reactor Trip as a Result of Meeting the Trip Logic for Over Temperature Delta Temperature During Reactor Protection System Pressurizer Pressure Calibration</strong><br /><i>Abstract:&nbsp;</i>On August 13, 2014, Instrumentation and Control (I&C) technicians started performance of an 8-hour scheduled surveillance 3-PC-OL04A (Pressurizer Pressure Loop P-455 Channel Calibration) with Loop I in test and tripped. The test was approved by I&C and operations to be stopped for a break with the bistables still tripped, Channel I in test. During the break, an automatic reactor trip (RT) occurred as a result of meeting the trip logic for Overtemperature Delta Temperature (OTDT). All control rods fully inserted and all required safety systems functioned properly. The plant was stabilized in hot standby with decay heat being removed by the main condenser. The Auxiliary Feedwater System automatically started as expected due to SG shrink effect. No work was being performed at the time of the RT and no actual OTDT existed. The direct cause of the RT was a spurious signal spiking on channel 3 of the OTDT circuitry with another channel tripped for testing. The two possible root causes were 1) a random failure of the OTDT static gain unit (Foxboro Integrator/Converter module QM-431D), 2) loose wiring connection on distribution block DB-4 (output of static gain unit QM-431) due to workmanship issue. Corrective actions included replacement of static gain module QM-431D and associated PR N-43 isolation amplifies NM306 and NM307, and static gain modules QM-421D, and QM-411D, replacement of three OPDT trip bistables (TC-421 A/B, TC-431 A/B, TC-441 A/B), replacement of setpoint module TM-432B (other setpoint modules had been previously replaced), and replacement of Loop 3 T(avg) E/I converter TM-432R. Procedure IP-SMM-WM-140 revised to include expectation on minimizing break times when a channel is tripped. The event had no effect on public health and safety.
2892014001 | Three Mile Island 1 | 04/25/2014 | 06/24/2014 | ML14176A96 | <strong>Unfused DC Motor Control Circuits</strong><br /><i>Abstract:&nbsp;</i>On 04/25/14 while Three Mile Island Unit 1 (TMI-1) was operating at 100% power, a concern was identified by Engineering as a result of their review of an industry operating event (ENS 49490). It was identified that unprotected DC control circuits for non safety-related DC motors routed from the turbine building to other separate fire areas could potentially overheat from a postulated fire in the Cable Spreading Room/Relay Room which could affect control cables routed in the same cable trays and potentially affect equipment credited to achieve and maintain fire safe shutdown. The condition was initially reported in ENS 50059 and again in ENS 50108 as a result of the extent of condition review. The apparent cause of the event is failure to identify that full-voltage 250VDC control circuit fuses should have been installed. Corrective actions were completed to install fuses in the identified and affected control circuits.<br /><br /> The submittal of this LER constitutes reporting to the NRC in accordance with 10 CFR 50.73(a)(2)(ii)(B).
2892014002 | Three Mile Island 1 | 07/13/2014 | 09/11/2014 | ML14254A40 | <strong>Through-Wall Leak on High Pressure Injection (HPI) "A" Train Root Valve MU-V-1034 Socket Weld</strong><br /><i>Abstract:&nbsp;</i>On July 13, 2014 at 17:31 Three Mile Island, Unit 1 exceeded a 72 hour limiting condition for operation (LCO), after being granted a period of enforcement discretion, due to a through-wall leak found on the "A" train of the High Pressure Injection (HPI) system piping at the 1/2" socket weld coupling to root valve MU-V-1034. The flaw resulted in declaring the "A" train of HPI inoperable. This event was reportable under 10 CFR 50.73(a)(2)(i)(B) as an operation or condition which was prohibited by the plant's technical specifications. A Notification of Enforcement Discretion (NOED) was granted by the NRC at 17:19 on July 13, 2014. The apparent cause leading to the NOED request was inadequate procedure guidance for applying freeze seals which resulted in delays in achieving isolation of the leak in order to establish proper conditions to perform the repair. The through-wall leak most probable cause was determined to be from stress corrosion cracking driven by fatigue. The corrective action was to grind out the weld and repair (reweld). This event had no adverse effect upon the health and safety of the public.
2932014001 | Pilgrim | 05/06/2014 | 07/07/2014 | ML14196A04 | <strong>Condition Prohibited By Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On May 6, 2014, with Pilgrim Nuclear Power Station (PNPS) in the RUN Mode operating at 100 percent power, the NRC Resident Inspector raised a concern about the PNPS method of complying with PNPS Technical Specification (TS) Limiting Condition for Operation (LCO) 3.7.A.2.b when a Primary Containment Isolation Valve is inoperable. TS LCO 3.7.A.2.b.requires that at least one containment isolation valve in each line having an inoperable valve shall be deactivated in the isolated condition. Deactivation means to electrically or pneumatically disarm, or otherwise secure the valve. PNPS interpretation and practice had been that a "Danger" tag on the control switch meets this requirement for a fail-closed valve with no automatic valve opening signal. At the time, Primary Containment Isolation Valves AO-5042A and AO-5044A were inoperable in the isolated position but were not deactivated.<br /><br /> The apparent cause of this event is failure to properly revise procedures and practices when LCO TS 3.7.A.2.b was revised in 1988 to permit periodic opening of the deactivated valve in the line under administrative controls.<br /><br /> This event was not risk significant and had no adverse impact on the health and safety of the public.
2962014001 | Browns Ferry 3 | 03/18/2014 | 05/19/2014 | ML14143A36 | <strong>Automatic Reactor Scram due to a Turbine Trip on High Moisture Separator Level</strong><br /><i>Abstract:&nbsp;</i>On March 18, 2014, the Browns Ferry Nuclear Plant (BFN) Unit 3 reactor automatically scrammed due to a turbine trip from a high main turbine moisture separator level. Initial indications show the level controller for 3B2 Moisture Separator failed to maintain level in automatic. Additionally, local manual control attempts failed to restore moisture separator level. Following the turbine trip Main Steam Isolation Valves remained open with main turbine bypass valves controlling reactor pressure.<br /><br /> At approximately 2232, Central Daylight Time (CDT) the 3B2 Moisture Separator Level High Alarm was received and an operator was dispatched to investigate. In accordance with the alarm response procedure the 3B2 Moisture Separator Water Level Controller was placed in manual. Attempts to control the Moisture Separator Reservoir 3B2 High Level Dump Valve manually were ineffective. At approximately 2252 CDT, the Unit 3 reactor automatically scrammed due to a turbine trip from a high moisture separator level.<br /><br /> The root cause was a failure to prevent the introduction of foreign material during the manufacturing process of the Moisture Separator Level Controller. The manufacturing defect was a legacy issue dating back to 1971 when the controller body was originally machined. The corrective actions to prevent recurrence requires the removal, cleaning of air passages, replacement of control relays, for similar controllers and upgrading the calibration procedure to include cleaning guidance.
2962014002 | Browns Ferry 3 | 05/06/2014 | 07/07/2014 | ML14189A41 | <strong>Automatic Reactor Scram due to an Anticipated Transient without Scram/Alternate Rod Insertion Signal Generated During Functional Test</strong><br /><i>Abstract:&nbsp;</i>On May 6, 2014, at approximately 0830 Central Daylight Time (CDT), the Browns Ferry Nuclear Plant (BFN) Unit 3 reactor automatically scrammed as a result of an Anticipated Transient Without Scram/Alternate Rod Insertion (ATWS/ARI) signal generated during functional testing of reactor water level instrumentation. The scram air header was depressurized through the ATWS/ARI valves causing all rods to insert into the core. The ATWS/ARI signal also simultaneously opened the Recirculation Pump Trip (RPT) breakers, tripping both Recirculation pumps. The loss of both pumps along with reduced core flow caused a reactor water level transient that lowered level below the Reactor Protection System (RPS) trip setpoint (+2 inches), resulting in a full reactor scram signal. Prior to this event, reactor power was 2.1 percent as all control rods were inserted by the ATWS/ARI initiation ten seconds earlier. Following receipt of the ATWS/ARI signal, all plant systems performed as required.<br /><br /> The root cause of the event was that the ATWS low reactor water level Automatic Trip Unit (ATU) cards initiated a voltage transient that actuated the ATWS high reactor pressure trip due to a design anomaly.<br /><br /> The corrective action to prevent recurrence includes installing time delay relays in association with the Unit 3 reactor pressure ATWS circuit.
2962014003 | Browns Ferry 3 | 06/02/2014 | 07/31/2014 | ML14217A34 | <strong>Primary Containment Isolation Valve Inoperable for Longer Than Allowed by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On June 2, 2014, during performance of the Reactor High Pressure Calibration surveillance, the Residual Heat Removal (RHR) Shutdown Cooling (SDC) Inboard Suction Valve Isolation relay failed to energize preventing automatic closure of the RHR SDC Inboard Suction Valve. On three occasions, the inability of this valve to close automatically upon receipt of the Primary Containment Isolation System signal resulted in a violation of the Browns Ferry Nuclear Plant, Unit 3, Technical Specifications. The Shutdown Cooling Mode of the Residual Heat Removal System was unaffected by this condition.<br /><br /> The cause of the event was relay wires had been lifted and incorrectly landed due to a human performance error at an indeterminate time between a successful post maintenance test (PMT) on March 07, 2014, and the time the condition was corrected by re-landing the wires according to plant drawings on June 6, 2014.<br /><br /> The corrective action to reduce likelihood of recurrence is to develop and deliver a case study to the Maintenance, Modifications, and Operations departments based on the details of this event.
2982014001 | Cooper Station | 01/06/2014 | 03/06/2014 | ML14070A36 | <strong>Secondary Containment Declared Inoperable due to Rise in Differential Pressure</strong><br /><i>Abstract:&nbsp;</i>On January 6, 2014, the differential pressure (DP) in the reactor building rose above the requirement of -0.25 inches of water column DP, causing entry into Limiting Condition of Operation (LCO) 3.6.4.1, Condition A. Secondary containment was declared inoperable at 02:45. <br /><br /> The DP transient occurred when a non-licensed plant operator (NLO) was hanging tags in support of maintenance work. During the process of hanging tags, the NLO inadvertently opened the wrong drain valve. When the wrong drain valve was open, the reactor recirculation motor generator (RRMG) exhaust fan discharge damper that was operating closed. The NLO felt the change in DP and closed the drain valve, which opened the RRMG exhaust fan discharge damper, restoring ventilation. DP was restored, secondary containment was declared operable at 03:02, and the LCO was exited. During this event, DP remained negative at all times. <br /><br /> The root cause is the organization was not fully aware of the effects of the cross-over leakage between the reactor building envelope and the RRMG exhaust system. To prevent recurrence of this event, procedures will be revised to ensure adequate precautions are taken to avoid exceeding the -0.25 inches of water column DP requirement, information about the effects of cross-over leakage will be incorporated into the appropriate training materials, and a procedure to directly measure air leakage will be developed
2982014002 | Cooper Station | 10/07/2013 | 04/11/2014 | ML14105A01 | <strong>Jacket Water Leak into Emergency Diesel Generator Engine Results in Condition Prohibited by Technical Specifications and Loss of Safety Function</strong><br /><i>Abstract:&nbsp;</i>On October 7, 2013, Diesel Generator (DG) 1 was declared inoperable for the performance of the monthly operability test. During the test, indications of water intrusion into the DG1 lubricating oil system were observed. DG1 remained inoperable during troubleshooting activities. Upon further investigation, a crack in the liner wall was visible near the top of the 1-Left cylinder liner. The liner was removed and sent to Lucius Pitkin, Incorporated, for examination. A new liner was installed and DG1 was declared operable on October 12, 2013.<br /><br /> The root cause of the event was that the subpar mechanical properties of the liner caused the cylinder liner to crack which then allowed jacket water to leak into the engine lubrication oil.<br /><br /> To prevent recurrence of this condition, the test method(s) shall be specified to ensure that liners currently in inventory have sufficient material tensile strength to conform to the given requirements. A report that details the test methods used and the results of testing shall be reviewed prior to any liner from inventory being installed in either DG1 or DG2.
2982014003 | Cooper Station | 02/25/2014 | 06/26/2014 | ML14182A09 | <strong>Valve Linkage Pin Out of Position Causes Condition Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On February 25, 2014, during planned Reactor Core Isolation Cooling (RCIC) system maintenance activities, a linkage pin in the RCIC trip and throttle valve, RCIC-MOV-MO14, was found out of position and not properly retained. The pin is part of the linkage assembly that ensures a successful valve reset following normal RCIC turbine trip situations. With the linkage pin in the as-found condition, it may have become disengaged during future RCIC system operation and prevented RCIC-MOV-MO14 to automatically reset, thus causing a system failure. Investigation found the set screws loose with no thread locker applied.<br /><br /> The cause of the linkage pin being out of position is inadequate work instructions during the valve overhaul in September 2010. The inadequate work instructions led to the set screws being out of position, which eventually let the linkage pin move out of position.<br /><br /> Immediate corrective action was taken to properly reinstall the pin and operation of RCIC-MOV-MO14 was tested satisfactorily on February 25, 2014. An additional corrective action was completed to revise the associated maintenance plan for RCIC-MOV-MO14 to include guidance for installation of the linkage pin and set screws
2982014004 | Cooper Station | 10/03/2014 | 11/24/2014 | ML14335A60 | <strong>Implementation of Enforcement Guidance Memorandum 11-003, Revision 2, Causes Conditions Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>During Refueling Outage 28 (RE-28), Cooper Nuclear Station implemented the guidance of Enforcement Guidance Memorandum (EGM) 11-003, Revision 2, "Dispositioning Boiling Water Reactor Licensee Noncompliance with Technical Specification Containment Requirements During Operations with a Potential for Draining the Reactor Vessel," dated December 13, 2013. Consistent with EGM 11-003, Revision 2, secondary containment operability was not maintained during Operations with a Potential for Draining the Reactor Vessel activities, and Required Action C.2 of Technical Specification 3.6.4.1 was not completed.<br /><br /> EGM 11-003, Revision 2, was implemented seven times during RE-28. These conditions are being reported as conditions prohibited by Technical Specifications.<br /><br /> Implementation of EGM 11-003, Revision 2, during RE-28 was a planned activity. As such, there were no root cause evaluations of the events. Consistent with the guidance provided in EGM 11-003, Revision 2, Nebraska Public Power District will submit a license amendment request to adopt a Technical Specifications Task Force (TSTF) traveler associated with generic resolution of this issue within 12 months after the issuance of the Notice of Availability of the TSTF traveler.
2982014005 | Cooper Station | 10/13/2014 | 12/10/2014 | ML14350A21 | <strong>Lube Oil Leak Results in a Potential Condition Prohibited by Technical Specifications and a Potential Loss of Safety Function</strong><br /><i>Abstract:&nbsp;</i>On October 13, 2014, Cooper Nuclear Station (CNS) observed an oil leak on the southeast corner of the Diesel Generator 2 engine during the performance of the monthly operability test. Upon further investigation, the right bank camshaft thrust bearing cover bolting was found completely loose or missing.<br /><br /> The event is currently under investigation. CNS will provide a supplement to this Licensee Event Report.
3062014001 | Prairie Island 2 | 12/31/2013 | 06/20/2014 | ML14174B24 | <strong>Unanalyzed Condition due to Removal of Multiple Steam Generator Lateral Support Shims and Bumpers</strong><br /><i>Abstract:&nbsp;</i>On December 31, 2013, while Unit 2 was in Mode 3 (Hot Standby), the Hot Gap clearance checks and adjustments were being performed following the Steam Generator (SG) Replacement Project. During the performance of the Hot Gap checks, it was discovered that multiple Upper Lateral Support (ULS) shims were removed from both 21 and 22 SG. This resulted in both Reactor Coolant System (RCS) loops being declared inoperable and entering Technical Specification (Tech Specs) 3.4.5 Condition D for the RCS loops while in Mode 3. This placed both RCS loops in an unanalyzed condition for seismic and pipe rupture analysis and required an 8 hours report to the NRC via Event Notification (49685) under 10 CFR 50.72(b)(3)(ii)(B). Additionally, based on further analysis, it was determined that with both RCS loops inoperable, the condition required the notification to be updated to include 10 CFR 50.72(b)(3)(v)(B), a loss of safety function.<br /><br /> Actions were taken to reinstall all of the ULS shims, which restored the proper configuration to meet operability requirements for seismic and pipe rupture acceptance criteria. The installation was completed on December 31, 2013, at 1728 CST, at which time Tech Specs 3.4.5 Condition D was exited.<br /><br /> The Root Cause to this event was the Steam Generator Replacement Project (SGRP) failure to document on the design drawings their assumption that the Unit 2 ULS shim packs would be measured and adjusted one shim pack at a time while making adjustments in Mode 3.
3062014002 | Prairie Island 2 | 05/19/2014 | 07/15/2014 | ML14197A19 | <strong>23 Fan Coil Unit Lower Northeast Face Corner Gasket Leaking</strong><br /><i>Abstract:&nbsp;</i>At approximately 1236 CDT on May 19, 2014, a Cooling Water (CL) Leak was identified on the lower face on the northeast corner on 23 Containment Fan Coil Unit (FCU) flange. The FCU is considered part of the Containment boundary. The leak caused a breach to this boundary, which could result in radioactivity traveling from Containment into the CL system, and resulting in off-site dose to the public. Unit 2 Containment was declared inoperable for a loss of Containment integrity, which required entry into Technical Specifications (TS) LCO 3.6.1 Condition A, Containment inoperable, in MODES 1, 2, 3, and 4. Immediate actions were taken to isolate the FCU and it was isolated within 1 hour from the initial conformation of the leak and TS 3.6.1 Condition A was exited. This restored Containment to an operable status. A second leak was found on the southwest CL supply inlet flange. A Work Request was initiated to repair the leak, and 23 Containment FCU was restored to an operable condition. This condition is reportable under 10 CFR 50.73(a)(2)(v)(C), Event or Condition that Could Have Prevented Fulfillment of a Safety Function to control the release of radioactive material. The Root Cause evaluation determined that the maintenance procedures and work plans for installation of Containment FCU Head Face Flange gaskets and inlet/outlet piping spacers/gaskets do not meet station planning standards for critical component maintenance and repair to prevent leakage through all ranges of operation. Planned corrective actions are to revise the Containment FCU Maintenance and Inspection procedures to specify a 45ft-lbs torque value for the Containment FCU Head Face Flanges vice providing an allowable range and to direct workers to take measurements of inlet/outlet flange spacers during installation to ensure spacers are centered in the flange.
3112014002 | Salem 2 | 01/31/2014 | 03/31/2014 | ML14090A27 | <strong>Manual Reactor Trip due to a Partially Dropped Rod</strong><br /><i>Abstract:&nbsp;</i>On January 31, 2014 at 0805, Salem Unit 2 experienced a partially dropped rod, identified as Control Bank D, Group B, Rod 1D2, while performing monthly rod surveillance testing. Rod 1D2 indicated 166 steps with the remainder of Control Bank D, Group B rods at 220 steps withdrawn. Operators entered Technical Specification (TS) 3.1.3.1, Action c. for the misaligned control rod, requiring a reduction in thermal power to less than 75 percent Rated Thermal Power (RTP) within one hour. A load reduction using boration and turbine load adjustments was commenced at 0812.<br /><br /> At 0904, at approximately 70 percent RTP, the plant entered the Action for TS 3.1.1.1, Shutdown Margin (SDM), which requires a continuous boration rate of equal to or greater than 33 gpm until the required SDM is restored. At approximately 20% RTP, the reactor was manually tripped due to a lack of available turbine load to continue to maintain Tave on program. All control rods inserted on the reactor trip. Corrective actions will be based on the cause of the rod 1D2 cable failure and possible enhancements to the SDM calculation procedure.<br /><br /> This report is being made in accordance with 10 CFR 50.73(a)(2)(iv)(A) as an "...event or condition that resulted in manual or automatic actuation of any of the systems listed in paragraph (a)(2)(iv)(B)..."
3112014003 | Salem 2 | 02/16/2014 | 04/11/2014 | ML14101A28 | <strong>Enforcement Discretion Received for Exceeding Allowable Outage Time for Inoperable Offsite Power Source</strong><br /><i>Abstract:&nbsp;</i>On February 13, 2014, at 1356 hours, the Salem Unit 2, 24 Station Power Transformer (SPT) was declared inoperable due to elevated transformer combustible gas levels indicating an active internal thermal fault. Salem requested enforcement discretion from the Nuclear Regulatory Commission (NRC) for 6 days because the time required to replace and return the 24 SPT to operable status would have exceeded TS 3.8.1.1, Action a.3, allowable outage time of 72 hours for inoperability of a single independent power source.<br /><br /> The NRC granted enforcement discretion on February 15, 2014, for 6 additional days. Successful completion and return to service of the 24 SPT occurred on February 18, 2014 at 0315 hours and the Notice of Enforcement Discretion (NOED) was terminated.<br /><br /> This report is being made in accordance with 10 CFR 50.73(a)(2)(i)(B), "Any operation which was prohibited by the plant's Technical Specifications..."
3132014001 | Arkansas 1, Arkansas 2 | 03/05/2014 | 05/05/2014 | ML14125A48 | <strong>Inadequate External Flood Protection for Safety-Related Equipment Located Below the Design Basis Flood Elevation</strong><br /><i>Abstract:&nbsp;</i>During Fukushima flooding walk downs to ensure the availability of flood protection barriers, a condition wasidentified which had the potential to adversely impact the ability to address external flooding conditions.Several individual pathways between both unit's Turbine Building and Auxiliary Building were identified thatcould bypass flood barriers. The identified pathways were for the most part scheduled and unscheduled,partially filled conduits. Configuration changes have been developed and implemented whereby theseindividual pathways were sealed or other isolation capabilities added. Examples of inadequate internal floodprotection were also identified. In addition, the bottom of a small segment of bus work associated with theflood-protected offsite power source path was found to be below the design basis flood maximum height.<br /><br /> The root causes include the lack of configuration control and a lack of robust design of external flood protectionbarriers. Additionally, inadequate walk downs, a breakdown in the Operating Experience process, and a lackof understanding of the risk significance of flood barriers also contributed to this condition.<br /><br /> Mitigating strategies have been implemented for the identified conditions. Actions to correct theprogrammatic aspects of this condition and the inadequate flood protection barriers are in progress.
3132014002 | Arkansas 1 | 11/25/2014 | 12/22/2014 | ML14357A09 | <strong>Special Report - Significant Change in Peak Cladding Temperature</strong><br /><i>Abstract:&nbsp;</i>This report is submitted pursuant to the 30 day Special Report requirement of 10 CFR 50.46(a)(3)(ii). The guidance provided in NURGEG 1022, Revision 3, allows the reporting under 10 CFR 50.73 and 10 CFR 50.46 to be combined. <br /><br /> On November 25, 2014, AREVA NP Inc. notified Entergy Operations, Inc. of a deficiency in the Arkansas Nuclear One, Unit 1 (ANO-1) Emergency Core Cooling System evaluation model. When the deficiency is accounted for, the Large Break Loss-of-Coolant Accident Peak Clad Temperature was estimated to exceed 2200°F and the absolute value of the deficiency is greater than the requirement of 10 CFR 50.46(a)(3)(ii). Exceeding 2200°F resulted in ANO-1 making an 8-hour NRC notification on November 25, 2014. See Event Notification EN 50641. The purpose of this report is to provide the information required by 10 CFR 50.46(a)(3)(ii).
3152014001 | Cook 1, Cook 2 | 02/20/2014 | 04/11/2014 | ML14106A60 | <strong>Non-Compliance with LCO 3.4.3 During Reactor Coolant System Vacuum Fill</strong><br /><i>Abstract:&nbsp;</i>On February 20, 2014, following a review of a Pressurized Water Reactor Owners Group notification of a recent Non Cited Violation at another nuclear power plant, Donald C. Cook Nuclear Plant (CNP) staff determined that CNP was in a similar circumstance of having been in an Operation or Condition Prohibited by Technical Specifications (TS).<br /><br /> At the end of each refueling outage, CNP draws a vacuum on the Reactor Coolant System (RCS) in order to refill the system. The RCS temperature and pressure (T/P) Limiting Condition for Operation (LCO), LCO 3.4.3, references two associated T/P operational limit figures, both of which terminate at a lowest pressure of 0 pounds per square inch gauge (psig). Therefore, operation at a vacuum is reportable in accordance with 10 CFR 50.73(a)(2)(i)(B), Operation or Condition Prohibited by TS.<br /><br /> The apparent cause is that the 10 CFR 50.59 screening for the original RCS vacuum fill procedures did not consider LCO 3.4.3 and its associated figures. The procedures have been put on administrative hold to preclude drawing a vacuum on the RCS until the LCO is revised to accommodate operation at a vacuum.
3152014002 | Cook 1, Cook 2 | 08/20/2014 | 10/20/2014 | ML14294A74 | <strong>Non-Compliance with LCO 3.8.1 During Surveillance Preparations</strong><br /><i>Abstract:&nbsp;</i>On August 20, 2014, the Donald C. Cook Nuclear Plant (CNP) Units 1 and 2 were operating at 100 percent power. At 2234 the Unit 1 and 2 AB Emergency Diesel Generator (AB EDG) Fuel Oil Storage Tank (FOST) Level Low alarm was received. FOST level was reported to be 8'7" and TS 3.8.3 Condition A was entered in Unit 1 and Unit 2. Further investigation discovered a Foreign Material Exclusion (FME) cover (nylon bag style FME cover) was installed on the AB FOST vent.<br /><br /> The FME cover had been installed under a work order on August 20, 2014, at 1400 in preparation for leakage testing to be conducted on the FOST. Fuel oil transfer pumps were operated to transfer fuel oil from the AB FOST to both units AB EDG Day Tanks, subsequently drawing a vacuum in the air volume of the tank. The vacuum caused level indication to decrease and actuate the Low Level alarm. During the investigation, a walk-down of the AB FOST revealed the FME cover blocking the vent and was removed. Subsequently at 0411 on August 21, 2014, the FOST Level Low alarm cleared and level in the tank returned to 10.0'. At this point TS 3.8.3 Condition A was exited.<br /><br /> Subsequent investigation determined that during the period of inoperability of the FOST, both Unit 1 and Unit 2 AB EDGs were also inoperable and a violation of T.S. 3.8.1 requirements occurred due to the configuration of a required support system. Therefore, this event is reportable in accordance with 10 CFR (a)(2)(i)(B).
3152014003 | Cook 1, Cook 2 | 11/01/2014 | 12/23/2014 | ML14364A02 | <strong>Manual Reactor Trip due to Lake Debris Intrusion Causing Degraded Forebay Conditions</strong><br /><i>Abstract:&nbsp;</i>On November 1, 2014, at approximately 0249, Donald C. Cook Plant Unit 1 (U1) and Unit 2 (U2) reactors were manually tripped from 100 percent and 55 percent power, respectively, when high winds and high waves on Lake Michigan resulted in a heavy influx of dune grass and debris into the forebay which resulted in degraded forebay conditions, lowering forebay level, and damaged trash racks. Following the U1 trip, the U1 Turbine Driven Auxiliary Feed Pump (TDAFP) tripped unexpectedly three minutes following the automatic start. Following the U2 trip, the U2 Main Generator trip was performed manually when the automatic trip failed.<br /><br /> Corrective actions taken include cleaning and repair of damaged forebay trash racks and travelling water screens. Corrective maintenance also corrected the causes of the U1 TDAFP trip and the U2 Main Generator trip function. Planned corrective actions include revising plant procedures to provide a comprehensive approach to adverse lake conditions.<br /><br /> The manual Reactor Protection System actuation and the automatic Auxiliary Feedwater System actuation were reported in accordance with 10 CFR 50.72(b)(2)(iv)(B) and 10 CFR 50.72(b)(3)(iv)(A) (Event Notification 50587). The valid actuations are reportable as a Licensee Event Report (LER) in accordance with 10 CFR 50.73(a)(2)(iv)(A). The storm and lake conditions necessitating the reactor trips is reportable as an LER in accordance with 10 CFR 50.73(a)(2)(iii).
3172014001 | Calvert Cliffs 1 | 01/21/2014 | 03/20/2014 | ML14080A30 | <strong>Reactor Trip due to Turbine Control System Reboot</strong><br /><i>Abstract:&nbsp;</i>On January 21, 2014, at 9:25 p.m., Unit 1 experienced an automatic reactor trip from 100 percent power. The reactor trip occurred when 13 kV Service Bus 21 deenergized due to a ground fault on feeder breaker 252-2104. The loss of the service bus caused a loss of power to safety-related 4 kV Bus 14, which caused an automatic start of the 1B Emergency Diesel Generator to power 4 kV Bus 14. When the 1B Emergency Diesel Generator repowered 4 kV Bus 14, the resultant voltage spike caused the main turbine controls to reboot. This deenergized the electrical trip device solenoids, depressurized the emergency trip supply header, and initiated turbine control valve closure. During this time, the turbine controls could not communicate a trip signal to the Reactor Protective System and the Unit 1 reactor subsequently tripped on high reactor coolant system pressure.<br /><br /> The root cause was determined to be an electrical design vulnerability not anticipated in the original design, where a voltage spike can result in turbine controls rebooting. No actions were required to return systems to pre-event normal status. There have been no recent similar events.
3172014002 | Calvert Cliffs 1 | 02/07/2014 | 04/03/2014 | ML14097A07 | <strong>Condition Prohibited by Technical Specifications due to Auxiliary Feedwater Train Inoperable due to Human Performance Error</strong><br /><i>Abstract:&nbsp;</i>The event was mis-positioning of the Auxiliary Feedwater (AFW) mud leg drain isolation valve (1-MS-225) and the mud leg steam trap bypass valve (1-MS-228) on 2/7/2014. During operator rounds these valves were cycled but were not returned to their closed position. During the performance of a scheduled surveillance test (STP-O-9-1), steam entered the AFW room through the open valves. The affected AFW pumps were determined to be inoperable with steam entering the room. The apparent cause of the event was that the Turbine Building Operators failed to apply human performance tools (procedure use and adherence, and placekeeping) to maintain proper configuration control. Corrective actions were handled through the performance management system and are complete. The AFW train was determined to have been inoperable for 12 hours, 50 minutes. Technical Specification (TS) 3.7.3.C requires 1 hour Actions with both AFW pumps inoperable. Since the 1 hour Actions were not performed within 1 hour, TS 3.7.3.E should have been entered. It requires that the Unit be placed in Mode 3 in 6 hours, and Mode 4 in 12 hours from entry into the Condition. Unit 1 was not placed in Mode 3 within 7 hours from the time the steam-driven AFW pumps were made inoperable. Therefore, the condition existed for a time longer than allowed by TSs. No similar Licensee Event Reports were found.
3172014003 | Calvert Cliffs 1 | 02/28/2014 | 04/24/2014 | ML14119A43 | <strong>Pressurizer Safety Valves As-Found Settings (Low) Outside Technical Specification Limits due to Inadequate Lift Spring Performance</strong><br /><i>Abstract:&nbsp;</i>During scheduled testing at the offsite testing facility, the as-found lift settings for the pressurizer safety valves (PSVs) previously installed in Unit 1 at the 1RV200 and 1RV201 locations were measured outside the Technical Specification allowable values (both valves lifted low). The valves had been installed during the 2012 Unit 1 refueling outage and were removed during the 2014 Unit 1 refueling outage for scheduled testing and maintenance. Spare valves were installed during the 2014 refueling outage. The failed valves were disassembled and inspected at the offsite facility. The apparent cause of the PSV failures is that the internal lift spring assemblies of a specific manufacturer lot failed to hold PSV set pressure. This apparent cause will be verified as the removed internal lift spring assemblies for each valve is further reviewed, examined, and tested to support this apparent cause. No other installed PSVs contain internal lift spring assemblies from this specific manufacturer's lot.
3172014005 | Calvert Cliffs 1 | 03/14/2014 | 05/12/2014 | ML14139A41 | <strong>Condition Prohibited by Technical Specifications due to Auxiliary Feedwater Actuation System Channel Inoperable due to Human Performance Error</strong><br /><i>Abstract:&nbsp;</i>On March 14, 2014, with Unit 1 in Mode 3, Control Room operators observed that Auxiliary Feedwater Actuation System (AFAS) Sensor Channel ZF High Level Bistable for No. 12 Steam Generator (SG) was tripped and would not reset. The cause was due to No. 12 SG Wide Range Level Transmitter 1LT1124C being isolated due to its manual isolation valve (1HVFW-1804) being mis-positioned in the closed position. This rendered AFAS Sensor Channel ZF inoperable. Investigation determined that 1HVFW-1804 was left closed following calibration of 1LT1124C on March 4, 2014. The apparent cause was that Technicians failed to apply human performance tools to maintain proper configuration control. Corrective actions were handled through the performance management system and are complete. This condition existed within a mode of applicability for approximately 34 hours. Technical Specification (TS) Condition 3.3.4.A requires a 1 hour Action. Since the 1 hour Action was not performed within 1 hour TS Condition 3.3.4.E should have been entered. It requires the Unit to be placed in Mode 4 within 12 hours from entry into the Condition. The tripped unit was not in bypass in 1 hour nor was Unit 1 placed in Mode 4 in 12 hours from the time the AFAS channel was made inoperable. Therefore, the condition existed for a time longer than allowed by TS. LER 317-2014-002 has a similar root cause.
3172014006 | Calvert Cliffs 1 | 05/01/2014 | 06/26/2014 | ML14182A66 | <strong>Reactor Trip due to Reactor Protective System Matrix Relay Testing Pushbutton Failure</strong><br /><i>Abstract:&nbsp;</i>On May 1, 2014 at 1016, Unit 1 experienced an automatic reactor trip from 100 percent power. Surveillance Test Procedure M-212E-1, Reactor Protective System Matrix Functional Test was being performed during the time of the trip. Two reactor trip circuit breakers opened as expected for the in-progress testing and approximately four minutes later, the remaining six reactor trip circuit breakers opened, resulting in a reactor trip. Operator actions were appropriate and in accordance with procedures. Plant response to the trip was uncomplicated. This event is being reported pursuant to 10 CFR 50.73(a)(2)(iv)(A) due to Reactor Protective System actuation. The root cause was determined to be that the contacts on the matrix relay trip test pushbuttons had silver sulfide contamination causing erratic contact resistance. Corrective actions will replace the remaining matrix relay trip test pushbuttons, assign locations codes, and develop a maintenance strategy to these components. No similar licensee event reports were identified.
3172014007 | Calvert Cliffs 1 | 07/24/2014 | 09/19/2014 | ML14265A41 | <strong>Reactor Coolant System Pressure Boundary Leakage in Reactor Coolant Pump Differential Pressure Transmitter Tubing</strong><br /><i>Abstract:&nbsp;</i>On July 24, 2014, a Unit 1 reactor coolant pressure boundary leak was identified on the high pressure sensing line tubing for the 11A Reactor Coolant Pump differential pressure transmitter. Technical Specification 3.4.13, Action B was entered requiring that the Unit be placed in Mode 3 within 6 hours and Mode 5 within 36 hours. As a result, operators commenced a plant shutdown at 2321 on July 24, 2014. The leak was isolated by shutting root isolation valves 1HVRC-141 and 1HVRC-142 and the condition was exited at 0250 on July 25, 2014.<br /><br /> The most probable root cause for the tubing leak is a missing support that allowed the tubing to fret on a piece of retired-in-place packing leak off line. Corrective actions include repairing the tubing and replacing the missing support no later than the 2016 Unit 1 refueling outage.
3182014001 | Calvert Cliffs 2 | 01/21/2014 | 03/20/2014 | ML14080A30 | <strong>Reactor Trip due to Inadequate Protection Against Weather Related Water Intrusion</strong><br /><i>Abstract:&nbsp;</i>On January 21, 2014, at 9:25 p.m., Unit 2 experienced an automatic reactor trip from 99.5 percent power. The reactor trip occurred when 13 kV Service Bus 21 deenergized due to a ground fault on feeder breaker 252-2104. The loss of the service bus caused a loss of power to non-safety-related 4 kV buses, which caused a loss of circulating water pumps and main condenser vacuum, requiring the use of auxiliary feedwater and atmospheric dump valves to maintain Reactor Coolant System temperature. Power was also lost to safety-related 4 kV Bus 24, which caused an automatic start of the 2B Emergency Diesel Generator to power 4 kV Bus 24.<br /><br /> The loss of power to non-safety-related 13 kV Service Bus 21 was caused by water intrusion when an air filter assembly located at the back of breaker 252-2104 cubicle became dislodged during a snow storm, allowing snow to enter the cubicle, melt, and cause a ground fault. This event is being reported pursuant to 10 CFR 50.73(a)(2)(iv)(A) due to Reactor Protective System actuation and the automatic start of the 2B Emergency Diesel Generator. Corrective actions include repairs to 13 kV Service Bus 21 and installation of a new filter housing. Previous events related to safety-related structures have been documented in Licensee Event Reports 317/2010-001 and 317/2011-003.
3182014002 | Calvert Cliffs 2 | 06/09/2014 | 08/07/2014 | ML14220A36 | <strong>Diesel Generator Technical Specification Surveillance Requirement Missed due to Human Performance Error</strong><br /><i>Abstract:&nbsp;</i>On June 9, 2014 at 1735, a 2A diesel generator field flash monitoring relay alarm was received in the Control Room. Investigation revealed no local alarms and no conditions consistent with an alarm condition existed. The Control Room alarm manual was referenced but critical information was missed. Following investigation by the Operations crew, a determination was made that the issue did not impact diesel generator operability based on proper indications and satisfactory status of standby systems for the diesel generator. Troubleshooting on June 11, 2014 determined that a field flash fuse clip was loose, rendering the diesel generator inoperable. Initial Technical Specification Condition 3.8.1.B which requires one hour Actions, and subsequent Technical Specification Condition 3.8.1.J to be in Mode 3 in six hours was missed due to the late identification of the diesel generator inoperability. The apparent cause of this event is human performance error. Corrective actions include operator training focused on understanding the causes of the degraded condition and validation of indications for potential inoperability and updating specific guidance for diesel generator alarms.
3212014001 | Hatch 1, Hatch 2 | 03/14/2014 | 06/05/2014 | ML14156A10 | <strong>Unfused DC Ammeter Circuits Result in an Unanalyzed Condition</strong><br /><i>Abstract:&nbsp;</i>On March 14, 2014 at 11:50 AM, with Units 1 and 2 operating at 100 percent rated thermal power (RTP), a review of industry operating experience concerning postulated fire induced circuit failures of unfused DC ammeter circuits determined the described condition was applicable to Edwin I. Hatch Units 1 and 2 reactor protection system (RPS) battery/battery charger ammeter circuits. This review determined that a postulated fire could result in concurrent shorts of an unfused DC ammeter cable and a DC cable of opposite polarity. Due to a lack of overcurrent protection on the ammeter cables, the resultant excessive current flow and overheating of the ammeter cable could result in in a secondary fire in another fire area that could adversely affect fire safe shutdown capability and create an unanalyzed condition with respect to 10 CFR 50 Appendix R analysis requirements for this postulated condition.<br /><br /> The current configuration has apparently existed since construction. The original design standards did not account for this situation and did not call for overcurrent protection on these circuits.<br /><br /> Compensatory actions taken were to establish required fire watches with subsequent actions taken to deenergize the affected circuits which removed the described vulnerability until design changes are implemented to correct the deficiency.
3212014002 | Hatch 1 | 05/01/2014 | 06/27/2014 | ML14178B35 | <strong>HPCI Steam Leak Results in Water in the Turbine Making HPCI Inoperable</strong><br /><i>Abstract:&nbsp;</i>On 5/1/2014 at 3:40 PM, with Unit 1 operating at 100 percent rated thermal power (RTP), condensation was found leaking out of the governor end gland seal and the coupling end of the High Pressure Coolant Injection (HPCI) turbine. By taking a temperature reading of the turbine casing, the elevated temperature of the turbine casing at the location monitored indicated that the steam supply isolation valve was leaking by to the HPCI Turbine Exhaust.<br /><br /> Due to a blown fuse, the exhaust drain pot drain valve no longer opened automatically on a high exhaust drain pot level signal. As a result the steam condensate from a leaking steam supply valve eventually filled the exhaust drain pot, the turbine exhaust line, and the turbine itself. With the presence of the blown fuse there was no HPCI Turbine Exhaust Drain Pot Level High annunciation received by the main control room (MCR).<br /><br /> Investigation showed that the blown fuse controlled power to the exhaust drain pot level control switches and alarms. Actions were taken to drain the system and restore power and annunciation by replacement of the affected fuse, and HPCI was returned to an operable status. Additional monitoring of the fused circuit and operation of the drain from the drain pot was established until the plant is in a condition to repair the leaking steam supply valve.
3212014003 | Hatch 1 | 05/07/2014 | 07/07/2014 | ML14188C02 | <strong>Safety Relief Valves As Found Settings Resulted in Not Meeting Tech Spec Surveillance Criteria</strong><br /><i>Abstract:&nbsp;</i>On May 7, 2014, at approximately 0837, Unit 1 was at 99.9 percent rated thermal power (RTP) when the "as-found" testing results of the 2-stage main steam safety relief valves (SRVs) were received which indicated that five of eleven SRVs had experienced setpoint drift during the previous operating cycle which resulted in their failing to meet the Technical Specification (TS) opening setpoints of 1150 psig +/- 3 percent as required by TS surveillance requirement 3.4.3.1.<br /><br /> The root cause of the SRV setpoint drift is attributed to corrosion-induced bonding between the pilot disc and seating surfaces. This conclusion is based on previous root cause analyses and the repetitive nature of this condition at Hatch and within the BWR industry. The 2-stage SRVs with platinum coated pilot seats were removed from Unit 1 during the 2014 refueling outage and replaced with 3-stage SRVs with a modified pilot. 3-stage SRVs typically do not exhibit set point drift, additionally the modified pilot reduces instances of vibration induced spurious openings and leak-by.<br /><br /> A 3-stage SRV with a similar modified pilot was installed on Unit 2 during the 2013 outage. Current plans are to replace the remaining ten valves at Unit 2 with the same modified pilot valves during the next outage in 2015.
3212014005 | Hatch 1 | 07/03/2014 | 08/29/2014 | ML14241A39 | <strong>Degraded Diesel Room Fan Flow Switch and Incorrect Thermal Overload Setting Result in Condition Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On 07/03/2014 at 0856 EDT, the 1A Emergency Diesel Generator (EDG) Room Exhaust Fans 'A' and 'B' were found in a tripped condition during the 1A EDG monthly surveillance. The 1A EDG was declared inoperable and the required actions were taken in accordance with the Technical Specifications. The thermal overloads for the motor control center (MCC) cubicles feeding the fans had tripped due to incorrectly sized thermal overload heaters. New thermal overload heaters were installed June 6, 2014 in order to correct a previous modification that installed incorrectly sized thermal overload heaters. The thermal overload heaters that were installed in June 2014 were found to have been sized too conservatively, leading to trip settings that were close to the normal operating current for the fans. The differential pressure flow switch for the 'A' fan was also found to be malfunctioning, causing both the 'A' and `B' fans to cycle on and off on a frequent basis. This frequent starting of the exhaust fans resulted in the thermal overloads being exposed to many motor start cycles, thereby increasing the operating current of the motor. The incorrectly sized thermal overload heaters in conjunction with the frequent fan starts led to the thermal overloads having trip settings that were too close to the normal operating current for the fans, resulting in premature trips of the thermal overloads. The flow switch and thermal overload heaters were replaced and the fans were returned to service restoring the 1A EDG to operable status.<br /><br /> The thermal overloads for the pan assemblies associated with the 1A EDG ventilation exhaust fans and the 'A' flow switch were replaced and the fans were returned to service.
3232014001 | Diablo Canyon 2 | 02/02/2014 | 07/02/2014 | ML14183B25 | <strong>Lightning Arrester Failure Resulting in Reactor Trip</strong><br /><i>Abstract:&nbsp;</i>On February 2, 2014, at 1129 PST, a failure of the Diablo Canyon Power Plant, Unit 2, Phase B, 500 kV lightning arrester resulted in a direct short to ground and actuated the 500 kV tie-line current differential relay. The actuation of the 500 kV tie-line current differential relay opened the Unit 2 generator output breakers to isolate the generator, which then actuated a turbine trip. Since Unit 2 was operating above the 50 percent power permissive, the reactor protection system initiated a Unit 2 reactor trip. Plant equipment responded as designed.<br /><br /> The cause was indeterminate due to the component damage. The corrective actions, including installing lightning arresters with increased capability to withstand, periodic cleaning of the arresters, and enhanced condition monitoring, address all probably causes.<br /><br /> There were no personnel injuries, no offsite radiological releases, and no damage to safety-related equipment associated with this condition. This condition did not have an adverse effect on the health and safety of the public.
3232014002 | Diablo Canyon 2 | 08/14/2014 | 05/07/2015 | ML15127A63 | <strong>Unit 2 Plant Shutdown Required by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On August 13, 2014, while performing scheduled maintenance on Unit 2 Emergency Diesel Generator (EDG) 2-2, Diablo Canyon Power Plant (DCPP) identified a failed Inlet-to-Fuel-Header capscrew on Engine Cylinder 1L. As part of subsequent inspections to determine whether a similar condition existed on any of the other Unit 1 or Unit 2 EDGs, a degraded capscrew was identified on EDG 2-3 Cylinder 8L. No capscrew issues were identified on the Unit 1 EDGs or on Unit 2 EDG 2-1. EDG 2-3 was declared inoperable at 1631 on August 14, 2014, resulting in two of three EDGs being inoperable at the same time, which requires ensuring at least two EDGs are operable within 2 hours, or be in Mode 3 within the following 6 hours.<br /><br /> Although the capscrew on EDG 2-3 was successfully replaced within 2 hours, during fuel system fill and vent following corrective maintenance, a fuel oil leak from the belt driven fuel oil booster pump occurred. Because repairs of EDG 2-3 could not be completed within the time permitted by Technical Specification 3.8.1 for two EDGs inoperable, a Unit 2 plant shutdown commenced. On August 14, 2014, at 2351 hours, Unit 2 entered Mode 3.<br /><br /> The cause of the failed capscrew on EDG 2-2, and the degraded capscrew on EDG 2-3, was determined to be high cycle fatigue. The cause of the fuel oil booster pump leak was determined to be a manufacturing defect combined with high seal annulus pressure during fuel oil system priming. Corrective actions include replacement of all capscrews with an improved material design, and incorporation of updated vendor guidance and updated fuel system priming instructions into station procedures.<br /><br /> This event did not adversely affect the health or safety of the public.
3242014001 | Brunswick 2 | 03/06/2014 | 05/02/2014 | ML14135A04 | <strong>Secondary Containment Loss of Safety Function due to Airlock Door Interlock Design</strong><br /><i>Abstract:&nbsp;</i>At 1605 Eastern Standard Time (EST) on March 6, 2014, Operations determined that both the inner and outer secondary containment airlock doors, on the 50 foot elevation of the reactor building, had been simultaneously opened for approximately one to two minutes on March 5, 2014. This event occurred while an employee was exiting secondary containment. The inner door failed to latch and opened as the employee was opening the outer door. Upon recognition of the condition, the employee took action to secure both doors.<br /><br /> This condition is being reported in accordance with 10 CFR 50.73(a)(2)(v)(C), as an event or condition that could have prevented fulfillment of a safety function needed to control the release of radioactive material. With both doors open, Surveillance Requirement 3.6.4.1.2 of Technical Specification 3.6.4.1, Secondary Containment, was not met, rendering secondary containment inoperable.<br /><br /> The root cause of this event is that the design of the secondary containment airlock c:oor interlocks is not robust enough to prevent inoperability of secondary containment. The corrective action to prevent recurence is to implement a design change to install a new interlock for the secondary containment airlock doors.
3242014002 | Brunswick 2 | 04/20/2014 | 06/19/2014 | ML14188B45 | <strong>Secondary Containment Loss of Safety Function due to Opening in Reactor Building Roof Drain Piping</strong><br /><i>Abstract:&nbsp;</i>On April 20, 2014, during operator rounds, the Reactor Building Auxiliary Operator (AO) identified pooled water on the floor on the 80-foot elevation of the Unit 2 Reactor Building. Upon further investigation, a through-wall leak in the Unit 2 Reactor Building 8-inch roof drain pipe was identified. The leak was determined to exceed the allowable leakage margin of the Secondary Containment pressure boundary, which resulted in Secondary Containment being considered inoperable per Technical Specifications (TSs). As such, this condition is being reported in accordance with 10 CFR 50.73(a)(2)(v)(C) as an event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to control the release of radioactive material. This event is also being reported in accordance with 10 CFR 50.73(a)(2)(i)(B) as operation prohibited by the plant's Technical Specifications since the as-found condition of the drain pipe clearly existed for longer than the Completion Times provided in TS 3.6.4.1, Secondary Containment.<br /><br /> The root cause of this event is that the Reactor Building roof drain pipe's equipment reliability classification was not appropriate. Corrective actions include changing the equipment reliability classification of the Reactor Building roof drain piping to Important and revising the inspection methodology of the Reactor Building roof drain piping to require assessment of the internal condition of the piping.
3252014001 | Brunswick 1 | 03/07/2014 | 05/01/2014 | ML14135A04 | <strong>Implementation of Enforcement Guidance Memorandum (EGM) 11-003, Revision 2</strong><br /><i>Abstract:&nbsp;</i>On March 7, 2014, Unit 1 implemented the guidance of EGM 11-003, Revision 2, "Enforcement Guidance Memorandum on Dispositioning Boiling Water Reactor Licensee Noncompliance with Technical Specification Containment Requirements During Operations with a Potential for Draining the Reactor Vessel," dated December 13, 2013. Consistent with EGM 11-003, Revision 2, secondary containment operability was not maintained during Operations with a Potential for Draining the Reactor Vessel (OPDRV) activities, and Required Actions C.1 and C.2 of Technical Specification (TS) 3.6.4.1, "Secondary Containment," were not completed. EGM 11-003, Revision 2, was implemented four additional times during the 2014, Unit 1 refueling outage. These conditions are being reported in accordance with 10 CFR 50.73(a)(2)(i)(B) as operations prohibited by the plant's TSs.<br /><br /> Implementation of EGM 11-003, Revision 2, during the Unit 1 refueling outage was a planned activity. As such, there was no root cause evaluation of the event. Consistent with the guidance provided in EGM 11-003, Revision 2, BSEP will submit a license amendment request to adopt a Technical Specification Task Force (TSTF) traveler associated with generic resolution of this issue within 12 months after the issuance of the Notice of Availability of the TSTF traveler.
3252014002 | Brunswick 1 | 03/09/2014 | 05/05/2014 | ML14135A05 | <strong>Secondary Containment Isolation Dampers Inoperable During Operations with Potential to Drain the Reactor Vessel</strong><br /><i>Abstract:&nbsp;</i>On March 9, 2014, Unit 1 was in Mode 5 with Operations with Potential to Drain the Reactor Vessel (OPDRVs) in progress. At 1300 Eastern Daylight Time, planned work commenced which removed both the normal and emergency electric power supplies for one train of the secondary containment isolation dampers (SCIDs). As a result, the SCIDs were declared inoperable, despite alignment of temporary control power to the SCIDs, and the Required Actions of Technical Specifications (TS) Limiting Condition for Operation (LCO) 3.6.4.2 were not carried out. Therefore, the plant entered a condition which is prohibited by the TS.<br /><br /> This event resulted from a deficiency in procedure OMMM-054, "Temporary Power Feed Documentation." The procedure did not require a Senior Reactor Operator (SRO) to determine whether a component is required to be operable while being supplied with temporary power. This resulted in SCIDs being supplied with temporary control power, not normal or emergency power, when they were required to be operable. To prevent recurrence, procedure OMMM-054 will be revised to include an SRO review for temporary power applications.
3252014003 | Brunswick 1 | 03/13/2014 | 05/09/2014 | ML14142A00 | <strong>Secondary Containment Loss of Safety Function due to Airlock Door Interlock Design</strong><br /><i>Abstract:&nbsp;</i>At 0937 Eastern Daylight Time (EDT) on March 13, 2014, Operations was informed that both the inner and outer secondary containment airlock doors, on the 50 foot elevation of the reactor building, had been simultaneously opened for approximately one minute. This event occurred while an employee was exiting secondary containment at the same time an employee was entering secondary containment. Upon recognition of the condition, the employees took action to secure both doors.<br /><br /> This condition, as well as one additional similar occurrence, are being reported in accordance with 10 CFR 50.73(a)(2)(v)(C), as an event or condition that could have prevented fulfillment of a safety function needed to control the release of radioactive material. With both doors open, Surveillance Requirement 3.6.4.1.2 of Technical Specification 3.6.4.1, Secondary Containment, was not met, rendering secondary containment inoperable. In each example, Operations with the Potential to Drain the Reactor Vessel (OPDRVs) were in progress and secondary containment was credited as operable.<br /><br /> The root cause of the events is that the design of the secondary containment airlock door interlocks is not robust enough to prevent inoperability of secondary containment. The corrective action to prevent recurrence is to implement a design change to install a new interlock for the secondary containment airlock doors.
3252014004 | Brunswick 1, Brunswick 2 | 03/20/2014 | 05/16/2014 | ML14149A24 | <strong>Fire Related Unanalyzed Condition that Could Impact Equipment Credited in Safe Shutdown Analysis</strong><br /><i>Abstract:&nbsp;</i>On March 20, 2014, as a result of the transition process from 10 CFR 50, Appendix R, to NFPA 805, a review of the Brunswick Steam Electric Plant Safe Shutdown Analysis determined that a postulated fire in specific fire areas could disable critical components, potentially resulting in equipment required for safe shutdown being inoperable. <br /><br /> The safety significance of this event is minimal. Deterministic analysis methods used to comply with Appendix R require every possible fire scenario to be addressed; however, the risk posed by these hypothetical events has been determined by analysis to be minimal. <br /><br /> Corrective actions for this event include maintaining fire watches in affected areas and revising fire response procedures to mitigate the consequences of a potential fire in these areas in order to establish compliance with Appendix R and the current licensing basis.
3252014005 | Brunswick 1 | 05/20/2014 | 07/21/2014 | ML14212A03 | <strong>Setpoint Drift in Main Steam Line Safety/Relief Valves Results in Two Valves Inoperable</strong><br /><i>Abstract:&nbsp;</i>On May 20, 2014, BSEP received the results of as-found testing on 11 safety/relief valves (SRVs) which had been removed from Unit 1 during the spring 2014 refueling outage. The testing indicated that two of the valves were found to lift outside the Technical Specifications (TS) required tolerance band of +/-3 percent, one having drifted 3.7 percent high and the other 3.4 percent low. Therefore, these two valves were determined to have been inoperable while the unit was in operation. Since TS 3.4.3, "Safety/Relief Valves," requires at least 10 of the 11 valves to be operable, this condition is being reported in accordance with 10 CFR 50.73(a)(2)(i)(B) as operation prohibited by the plant's TS.<br /><br /> Setpoint drift in the increasing direction occurred in one valve because of an inadequate surface finish on its pilot disc which caused a loss of the platinum coating followed by corrosion bonding of the disc and seat. The cause of the setpoint drift in the other valve could not be determined, and the initial lift pressure for the second valve was lower than its setpoint. Corrective actions for this event included replacing all the SRV pilot valves in Unit 1 with certified spares and completing a procedure revision for ensuring proper surface preparation.
3272014001 | Sequoyah 1 | 01/30/2014 | 03/26/2014 | ML14090A40 | <strong>Never Performed Technical Specification Surveillance for Common Spare Component Cooling System Pump</strong><br /><i>Abstract:&nbsp;</i>On December 19, 2013, an initial license operator trainee discovered a lack of procedural guidance to perform Technical Specification (TS) Surveillance Requirement (SR) 4.7.3 b, which requires Unit 1 safety injection signal (SIS) start testing for the common spare component cooling system (C-S CCS) [CC] pump. Specifically, procedure, 1-SI-OPS-082-026.B, did not verify an SIS would start the C-S CCS pump and supply the Unit 1 B train header. All other SIS configurations for starting the C-S CCS pumps were previously accounted for and verified. Initially, SQN classified the condition as a missed surveillance, as the intended aspects of SR 4.7.3 b were not satisfied. Operations invoked TS 4.0.3 to allow testing in accordance with a missed surveillance and a risk evaluation was performed. A procedure change was implemented to provide for testing SIS start of the C-S CCS pump with both units on-line. The test was performed satisfactorily and SR 4.7.3 b requirements were met. The SQN investigation revealed the omission of the C-S CCS pump from the SIS testing dated back to the development of the initial plant surveillance documents. With no record of the SR 4.7.3 b ever being satisfied for the Unit 1 B train, the condition was re-classified as a never performed surveillance on January 30, 2014.
3282014001 | Sequoyah 2 | 04/29/2014 | 06/25/2014 | ML14181A03 | <strong>Misalignment of Containment Purge Radiation Monitors Results in Condition Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On April 29, 2014, during the performance of 0-SO-30-3, "Containment Purge System Operation," the two containment purge air exhaust radiation monitors were discovered aligned to train A containment purge. From April 8 to April 28, 2014, train B containment purge was operated three times with the radiation monitors aligned to train A purge. These radiation monitors provide containment ventilation isolation (CVI) signals upon a high radiation condition to mitigate the release of radioactivity from inside containment. With the radiation monitors not aligned to the train of containment purge exhaust being operated, the ability to signal a CVI from the containment purge exhaust monitors was lost. However, during the time frame the purge monitors were misaligned, alternate automatic and manual means of performing a CVI were available. The cause of this event was operators failing to perform verbatim procedure compliance when ensuring the containment purge radiation monitor alignment prior to placing containment purge in service. Corrective actions include reinforcement of management expectations for procedure use and adherence with shift managers and crew operators.
3282014002 | Sequoyah 2 | 06/24/2014 | 08/22/2014 | ML14239A49 | <strong>Containment Vacuum Relief Valve Inoperable Resulting in a Condition Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On June 24, 2014, at 2315 Eastern Daylight Time (EDT) nightshift Operations personnel identified the containment vacuum relief valve, 2-VLV-30-573, was not in its normally closed position. Operations personnel declared the containment vacuum relief valve inoperable and entered into actions of Technical Specifications (TSs) Limiting Condition for Operation (LCO) 3.6.3, "Containment Isolation Valves" and TS LCO 3.6.6, "Vacuum Relief Lines." On June 25, 2014, at 0311 EDT, Operations personnel declared the containment isolation function of the vacuum relief valve operable with the valve closed. The containment vacuum relief valve had actuated and failed to reseat during containment venting that completed at 1647 EDT on June 24. This resulted in a containment isolation valve being inoperable for longer than permitted by TS LCO 3.6.3, and therefore a condition prohibited by TSs. The causes of this event included failure of Maintenance craft personnel to follow procedures and inadequate operating instruction for identification of relief valve position. Corrective actions include additional training for Maintenance craft personnel and a procedure revision for valve position validation.
3312014001 | Duane Arnold | 01/17/2014 | 04/30/2014 | ML14126A59 | <strong>Condition Prohibited by Technical Specifications - Past Inoperability of Standby Transformer Undervoltage Relay</strong><br /><i>Abstract:&nbsp;</i>On January 17, 2014, while operating at 100% power, Standby Transformer 1X4 Undervoltage Relay 127/SB2 failed to meet requirements of Surveillance Test Procedure (STP) 3.3.8.1-05B, 1A4 4KV Emergency Transformer Supply Undervoltage Calibration. Two relay trip circuit contacts were found to be incorrectly configured such that the relay could not perform the intended function to actuate on loss-of-voltage to trip the Standby Transformer supply breaker. A past operability review determined that the relay had been inoperable for 120 days, 8 hours and 5 minutes. The relay is required to be operable in Modes 1, 2, and 3, and when the associated "B" Emergency Diesel Generator is required to be operable by Limiting Condition for Operation (LCO) 3.8.2, AC Sources-Shutdown. The event resulted in a condition prohibited by Technical Specifications and is reportable pursuant to 10CFR50.73(a)(2)(i)(B). The safety significance is minimized due to the fact that degraded voltage relays perform a similar function and would trip the Standby Transformer supply breaker to allow the "B" Emergency Diesel Generator to carry essential loads during a Loss-of-Offsite-Power.<br /><br /> The root cause of this event was inadequate procedural guidance for both preplanned maintenance and post maintenance testing. This event did not result in a safety system functional failure. There were no radiological releases associated with this event.
3312014002 | Duane Arnold | 02/18/2014 | 04/17/2014 | ML14108A32 | <strong>Both Doors in Secondary Containment Airlock Opened Concurrently</strong><br /><i>Abstract:&nbsp;</i>On February 18, 2014, while operating at 100% power, workers opened doors concurrently when entering a secondary containment access airlock. The individuals involved each closed their respective doors upon encountering this unexpected condition; however, the result was a brief inoperability of secondary containment integrity. This resulted in an 8 hour reportable event. The Resident Inspector was notified, and Event Notification Number 49838 was made pursuant to 10 CFR 50.72(b)(3)(v)(C) due to a condition at the time of discovery that prevented the fulfillment of the Secondary Containment safety function.<br /><br /> The apparent cause of the event was determined to be excess strength of a permanent magnet on one of the doors. The monthly surveillance test has been revised to check the permanent magnet for proper adjustment and to adjust it as needed.<br /><br /> This event did not result in a safety system functional failure. There were no radiological releases associated with this event.
3312014003 | Duane Arnold | 05/30/2014 | 07/25/2014 | ML14210A35 | <strong>Both Doors in Secondary Containment Airlock Opened Concurrently</strong><br /><i>Abstract:&nbsp;</i>On May 30, 2014, while operating at 100% power, workers opened doors concurrently when entering a secondary containment access airlock. The individuals involved each closed their respective doors upon encountering this unexpected condition; however, the result was a brief inoperability of secondary containment integrity. This resulted in an 8 hour reportable event. The Resident Inspector was notified, and Event Notification Number 50153 was made pursuant to 10 CFR 50.72(b)(3)(v)(C) due to a condition at the time of discovery that prevented the fulfillment of the Secondary Containment safety function.<br /><br /> The apparent cause of the event was determined to be excess strength of a permanent magnet on one of the doors. The monthly surveillance test will be revised to address the lag between the interlock lights turning off and the door latching, to document maintenance actions to allow trending and to quantify the gap between the interlock light turning off and the door latching.<br /><br /> This event did not result in a safety system functional failure. There were no radiological releases associated with this event.
3312014004 | Duane Arnold | 05/30/2014 | 07/25/2014 | ML14210A35 | <strong>Unplanned Inoperability of High Pressure Coolant Injection</strong><br /><i>Abstract:&nbsp;</i>On May 30, 2014, at 1043, while operating at 100% power, during the performance of a routine Technical Specification (TS) required Surveillance Test Procedure (STP), the 'A' side High Pressure Coolant Injection (HPCI) (BG) isolation logic was activated. The logic activation occurred while attempting to block open contacts of HGA relay E41A-K43, HPCI Auto Isolation Logic Steam Line High Differential Pressure. The root cause of this event was the design of the HGA relay makes the act of installing relay blocks very difficult and prone to inadvertent actuation. The Resident Inspector was notified, and Event Notification Number 50154 was made pursuant to 10 CFR 50.72(b)(3)(v)(D) due to a condition at the time of discovery that prevented the fulfillment of the HPCI safety function. On May 30, 2014, at 1209, HPCI was returned to operable status after resetting the isolation logic and returning the system to standby readiness condition.<br /><br /> This event did result in a safety system functional failure. There were no radiological releases associated with this event.
3312014005 | Duane Arnold | 06/30/2014 | 08/29/2014 | ML14246A20 | <strong>Automatic Start of Standby Diesel Generators due to Grid Disturbance</strong><br /><i>Abstract:&nbsp;</i>On June 30, 2014, at 1913, while operating at 98% power, a grid disturbance resulted in an automatic start of both of the site's Emergency Diesel Generators (EDGs) (IEE Code EK). Neither EDG loaded onto its respective essential bus. The cause of the EDG starts was a momentary (approximately 13 cycles) dip in essential bus voltage to 62%. A review of the system design showed that since the EDGs started on an automatic start signal of essential bus voltage less than 65% for greater than 12 cycles, the EDGs operated as designed. Both EDGs were secured and returned to their normal standby readiness condition at 2116 on June 30, 2014. This event resulted in an 8 hour reportable event. The Resident Inspector was notified, and Event Notification Number 50246 was made pursuant to 10 CFR 50.72(b)(3)(iv)(A) due to a valid system actuation.<br /><br /> The apparent cause of the event was determined to be a valid start of the EDGs per design. This event did not result in a safety system functional failure. There were no radiological releases associated with this event.
3312014006 | Duane Arnold | 10/12/2014 | 12/09/2014 | ML14349A32 | <strong>Implementation of Enforcement Guidance Memorandum (EGM) 11-003, Revision 2</strong><br /><i>Abstract:&nbsp;</i>On October 12, 2014, while in Mode 5 for a refueling outage and prior to commencing certain planned activities, Duane Arnold Energy Center (DAEC) implemented the guidance of NRC EGM 11-003, R2, "Enforcement Guidance Memorandum 11-003, Revision 2, Dispositioning Boiling Water Reactor Licensee Noncompliance with Technical Specification Containment Requirements during Operations with a Potential for Draining the Reactor Vessel" (OPDRV). Throughout the planned OPDRV activities that continued, DAEC implemented interim actions per EGM 11-003 as an alternative to maintaining Secondary Containment operability as required by Technical Specification (TS) 3.6.4.1. While the NRC's enforcement guidance provides allowance for these actions, the OPDRV activities without Secondary Containment are still considered reportable in accordance with 10 CFR 50.73(a)(2)(i)(B) as a Condition Prohibited by Technical Specifications. The implementation of EGM 11-003, Revision 2 was a planned activity and did not require a cause evaluation. Consistent with the guidance in the EGM, Duane Arnold Energy Center will submit a license amendment request (LAR) within twelve months after issuance of a notice of availability regarding a generic resolution of the issues surrounding the need for the EGM.
3332014001 | FitzPatrick | 04/01/2014 | 06/02/2014 | ML14153A66 | <strong>Inoperable "A" EDG Subsystem and Concurrent Trip of the "B" Safety Pump Room Ventilation Fan</strong><br /><i>Abstract:&nbsp;</i>At 0630 on the morning of April 1, 2014, with James A. FitzPatrick Nuclear Power Plant (JAFNPP) operating at 100 percent power and the "A" Emergency Diesel Generator (EDG) subsystem inoperable for maintenance, a control room alarm annunciated indicating a problem with the "B" division safety pump room ventilation system. At 0645 a field operator identified the exhaust fan for the "B" division safety pump room ventilation system had tripped on thermal overload. Ventilation loss when the pumps are in service would degrade the long term performance of residual heat removal service water (RHRSW) and emergency service water (ESW) systems; degradation of the "B" ESW pump would degrade the performance of the "B" EDG subsystem. The overload relay was reset at 0704 and the fan automatically started restoring ventilation; time out of service was thirty-four minutes. The ambient temperature limit in "B" division safety pump room was never challenged.<br /><br /> The equipment failure evaluation has determined preliminary cause of the tripping of the fan to be the weakening of the Bi-Metal trip element that is heated by the current that causes the trip. This component will be replaced and the unit tested to confirm cause.
3332014002 | FitzPatrick | 10/28/2014 | 12/28/2015 | ML15363A20 | <strong>Secondary Containment Vacuum Below Technical Specification Limit</strong><br /><i>Abstract:&nbsp;</i>At 1655 and 1708 on October 28, 2014, James A. FitzPatrick Nuclear Power Plant (JAF) was operating at 100 percent power when differential pressure of the Secondary Containment Reactor Building exceeded a Technical Specification Requirement. The requirement is for the Secondary Containment to have a >/= 0.25 inch of vacuum water gauge compared to the external environment. The Reactor Building differential pressure decreased below 0.25 inch of vacuum water gauge twice: at 1655 when isolating Reactor Building Ventilation caused by the isolation valve closing sequence; and, at 1708 while restoring Reactor Building 'A' Ventilation caused by the Refuel Floor Exhaust fan 'A' discharge damper 66AOD-106A going partially closed with concurrent failure of the associated fan discharge damper position indicating switch 66PNS-106A1. This resulted in obstructing exhaust flow from the Reactor Building. Each condition existed for approximately a minute. <br /><br /> When Secondary Containment did not meet the Technical Specification Surveillance Requirement 3.6.4.1.1 for differential pressure the Limiting Condition of Operation (LCO) was not met. Therefore, Secondary Containment was Inoperable. Restoration of the LCO was completed within the allowed action completion time. This report is being submitted per 10 CFR 50.73(a)(2)(v)(C) as a condition that could have prevented the fulfillment of safety function to control the release of radioactive material.
3342014001 | Beaver Valley 1 | 01/06/2014 | 12/19/2014 | ML14358A17 | <strong>Beaver Valley Unit 1 Automatic Reactor Trip due to Main Unit Transformer Failure</strong><br /><i>Abstract:&nbsp;</i>On January 6, 2014 at 1659 hours, Beaver Valley Power Station (BVPS) Unit 1 was operating at 100 percent power. An automatic reactor trip occurred due to a main transformer differential protection main unit generator trip. All three Auxiliary Feedwater (AFW) pumps automatically started, as expected, due to lowering steam generator levels. The reactor trip response was as expected with no immediate complications. The main transformer differential protection actuation was determined to be caused by an internal winding fault in the 'B' phase windings due to a dielectric breakdown. The transformer has been replaced. <br /><br /> This event is being reported under 10 CFR 50.73(a)(2)(iv)(A) as a condition that resulted in the valid automatic actuation of systems listed in (a)(2)(iv)(B) - (1) automatic Reactor trip, (6) automatic Auxiliary Feedwater pump start. A 10 CFR 50.72 notification was made at 1909 hours on January 6, 2014 to report an automatic reactor trip and a Specified System, Auxiliary Feedwater actuation (EN 49697).
3342014002 | Beaver Valley 1 | 01/06/2014 | 03/07/2014 | ML14069A46 | <strong>Beaver Valley Unit 1 Turbine Driven Auxiliary Feedwater Pump Governor Oscillations Result in Pump Trip</strong><br /><i>Abstract:&nbsp;</i>On January 6, 2014, the Beaver Valley Power Station (BVPS) Unit 1 tripped from full power due to a main transformer differential protection main unit generator trip as a result of a main unit transformer failure. All three Auxiliary Feedwater (AFW) pumps automatically started, as expected, due to lowering steam generator levels. The Turbine Driven Auxiliary Feedwater (TDAFW) pump ran for 1 hour and 49 minutes at which time the pump tripped due to governor oscillations. The TDAFW pump was declared inoperable. Subsequent investigation determined that the governor oscillations were due to a misadjusted governor needle valve that was last set during refueling outage 1R22 in October, 2013. Therefore the pump was inoperable from the time Mode 3 was entered on November 1, 2013 at 1006 hours. Technical Specifications (TS) require three trains of AFW to be operable in Modes 1 through 3. Entry into Mode 3 and operation with an inoperable pump, for longer than permitted by the TS, constitute conditions prohibited by TS. During this time each of the Motor Driven AFW pumps were rendered inoperable, separately, for maintenance and/or testing. This constitutes a condition that could have prevented the fulfillment of a Safety Function. The governor has been properly adjusted and the appropriate procedures will be revised. <br /><br /> This event is being reported under 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by Technical Specifications and under 10 CFR 50.73(a)(2)(v)(B) as a condition that could have prevented the fulfillment of a Safety Function - Remove Residual Heat.
3342014003 | Beaver Valley 1, Beaver Valley 2 | 02/26/2014 | 04/21/2014 | ML14113A46 | <strong>Operation Outside of the Pressure and Temperature Limits Report During Isolated RCS Loop Vacuum Fill</strong><br /><i>Abstract:&nbsp;</i>During a review of external operating experience, it was discovered that Beaver Valley Power Station (BVPS) Unit 1 and Unit 2 had previously operated outside of the limits specified in the Pressure and Temperature Limits Report (PTLR) during past Reactor Coolant System (RCS) loop vacuum fill evolutions, which were performed while in Mode 5, usually following unit refueling (Mode 6). Technical Specifications (TS) Limiting Condition for Operation (LCO) 3.4.3 requires RCS pressure and temperature be maintained within the limits specified in the PTLR at all times. <br /><br /> Approved procedures permit the RCS loops to be vacuum filled, while isolated from the reactor vessel, during Mode 5. Placing a vacuum on the RCS loop results in pressures below 0 psig. Since pressures below 0 psig are not specified on the applicable PTLR figures, vacuum filling of the RCS loops results in a condition prohibited by TS which is reportable under 10 CFR 50.73(a)(2)(i)(B). <br /><br /> The evaluation of the procedure changes to permit vacuum fill of the RCS in the year 2000 focused on the technical evaluation and did not adequately consider the TS compliance aspect of a vacuum condition being below the pressure range specified on the applicable RCS PIT limits figures. The BVPS Unit 1 and Unit 2 PTLRs have been revised to address vacuum conditions.
3342014003 | Beaver Valley 1, Beaver Valley 2 | 02/26/2014 | 04/21/2014 | ML14113A46 | <strong>Operation Outside of the Pressure and Temperature Limits Report During Isolated RCS Loop Vacuum Fill</strong><br /><i>Abstract:&nbsp;</i>During a review of external operating experience, it was discovered that Beaver Valley Power Station (BVPS) Unit 1 and Unit 2 had previously operated outside of the limits specified in the Pressure and Temperature Limits Report (PTLR) during past Reactor Coolant System (RCS) loop vacuum fill evolutions, which were performed while in Mode 5, usually following unit refueling (Mode 6). Technical Specifications (TS) Limiting Condition for Operation (LCO) 3.4.3 requires RCS pressure and temperature be maintained within the limits specified in the PTLR at all times. <br /><br /> Approved procedures permit the RCS loops to be vacuum filled, while isolated from the reactor vessel, during Mode 5. Placing a vacuum on the RCS loop results in pressures below 0 psig. Since pressures below 0 psig are not specified on the applicable PTLR figures, vacuum filling of the RCS loops results in a condition prohibited by TS which is reportable under 10 CFR 50.73(a)(2)(i)(B). <br /><br /> The evaluation of the procedure changes to permit vacuum fill of the RCS in the year 2000 focused on the technical evaluation and did not adequately consider the TS compliance aspect of a vacuum condition being below the pressure range specified on the applicable RCS P/T limits figures. The BVPS Unit 1 and Unit 2 PTLRs have been revised to address vacuum conditions.
3342014004 | Beaver Valley 1, Beaver Valley 2 | 04/30/2014 | 06/27/2014 | ML14183A39 | <strong>Unanalyzed Condition Resulting from Unfused Direct Current Control Circuits</strong><br /><i>Abstract:&nbsp;</i>Based on a review of industry operating experience, it was identified that Beaver Valley Power Station (BVPS) Unit 1 and Unit 2 each have unfused direct current (DC) control circuits for DC motors which are routed from the turbine building through other fire areas. The DC breakers used to protect the motor power conductors are insufficient to protect the control conductors for these circuits. It is postulated that a fire induced short in one fire area could adversely impact safe shutdown equipment by overheating the cable and causing a secondary fire in other fire areas where the cable is routed. The postulated secondary fires or cable failures are outside the assumptions of each unit's fire protection analysis.<br /><br /> This condition is reportable under 10 CFR 50.72(b)(3)(ii)(B) / 10 CFR 50.73(a)(2)(ii)(B) as an unanalyzed condition that significantly degraded plant safety. The 10 CFR 50.72(b)(3)(ii)(B) notification was made on April 30, 2014.<br /><br /> The apparent cause was determined to be a latent error in original plant design. Compensatory fire watches have been implemented for affected fire areas. Planned corrective actions include plant modifications to the affected DC control circuits to protect against a postulated fire induced short that could overheat the cable causing a secondary fire in separate fire areas. Alternatively, other actions may be taken through an analytical resolution, if appropriate.
3342014005 | Beaver Valley 1, Beaver Valley 2 | 08/13/2014 | 10/10/2014 | ML14288A23 | <strong>Containment Equipment Hatch Missile Shield Removal Inadvertently Results In Exceeding Technical Specification 3.6.1 Required Completion Times</strong><br /><i>Abstract:&nbsp;</i>NRC Inspection Report Nos. 05000334/2014003 and 05000412/2014003 dated August 13, 2014, documented a Green non-cited violation of Technical Specification (TS) LCO 3.6.1, "Containment," since the Containment equipment hatch missile shields were removed while in a Mode in which Containment was required to be operable and the actions directed by the required action statement were not taken. An assessment performed in 2002 to permit Containment equipment hatch missile shields to be removed during Modes 1 through 4 was based on a too narrowly focused review that incorrectly determined that the removal of the missile shield did not affect Containment operability. Containment operability with the equipment hatch missile shield removed was not adequately assessed, nor were equivalent compensatory measures implemented. Therefore, the required actions of TS LCO 3.6.1, "Containment," were not entered nor met. In the past three years, the Containment equipment hatch missile shields were removed prior to four planned refueling outages, two at each Unit. <br /><br /> This event is reportable under 10 CFR 50.73(a)(2)(i)(B) as an operation or condition prohibited by technical specifications, and reportable under 10 CFR 50.73(a)(2)(v) as an event or condition that could have prevented fulfillment of the safety function of structures or systems that are needed to: (C) Control the release of radioactive material; and (D) Mitigate the consequences of an accident. <br /><br /> The apparent cause was determined to be that the relationship of TS operability and compliance with the design basis requirements was not fully understood. Too narrow a focus on TS and the TS bases for determining impact on operability was applied. This resulted in the inoperability of Containment not being recognized when the equipment hatch missile shields were removed. Corrective actions include training for engineering and operations personnel, and enhancing the work management process to ensure engineering evaluations are complete prior to removal of missile barriers.
3352014001 | St. Lucie 1 | 01/09/2014 | 09/22/2014 | ML14280A43 | <strong>Internal RAB Flooding During Heavy Rain due to Degraded Conduits Lacking Internal Flood Barriers</strong><br /><i>Abstract:&nbsp;</i>On January 9, 2014, the St..Lucie site was experiencing heavy rainfall. Storm drain blockage caused water to backup within the emergency core cooling system (ECCS) pipe tunnel. Water entered the reactor auxiliary building (RAB) through two degraded conduits that lacked internal flood barriers. At 1803 hours St. Lucie declared an Unusual Event (UE) due to storm drain capacity degradation. The UE was terminated at 0001 hours on January 10, 2014, when the storm had passed and the drains had been cleared.<br /><br /> The extent of condition identified four additional conduits that lacked the required internal flood barriers. All the affected conduits subsequently had qualified internal water seals installed.<br /><br /> During this event there was no loss of any safety related accident mitigation or safe shutdown equipment.<br /><br /> Revision 3 includes additional reporting criteria.
3362014001 | Millstone 2 | 01/31/2014 | 03/31/2014 | ML14097A01 | <strong>Completion of Plant Shutdown Required by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On January 30, 2014 at 2313, with Millstone Power Station Unit 2 (MPS2) in MODE 1 and at 100% reactor power, the circuit breaker for the group 1 pressurizer proportional heaters tripped. With the 'B' emergency diesel generator out of service for its maintenance outage and therefore inoperable, Technical Specification Action Statement (TSAS) 3.4.4 action b was entered. TSAS 3.4.4 action b requires MPS2 be in at least HOT STANDBY (MODE 3) with the reactor trip breakers open within 6 hours and in HOT SHUTDOWN (MODE 4) within the following 6 hours, unless one group of proportional heaters is restored to operable status. MPS2 completed the shutdown to MODE 3 at 0457 and restored the group 1 proportional heaters to operable status at 0747 on January 31, 2014. The initiation of the shutdown was reported to the NRC (event number 49779) pursuant to 10 CFR 50.72(b)(2)(i) - The initiation of any nuclear plant shutdown required by the plant's technical specifications.<br /><br /> After troubleshooting, faulty heater leads were lifted to remove a failed heater from service. Following appropriate testing, the group 1 proportional heater and the pressurizer were declared operable and MPS2 was subsequently returned to service.<br /><br /> This condition is being reported pursuant to 10 CFR 50.73(a)(2)(i)(A) - The completion of any nuclear plant shutdown required by the plant's technical specifications.
3362014002 | Millstone 2 | 03/12/2014 | 05/05/2014 | ML14129A46 | <strong>DC Circuit Hot Shorts</strong><br /><i>Abstract:&nbsp;</i>While Millstone Power Station Unit 2 (MPS2) was operating at 100 percent power in Mode 1 on March 12, 2014, operations determined that a concern identified by Engineering as a result of recent industry operating experience (NRC Event Number 49889) could result in an unanalyzed condition. Engineering's review of the direct current (DC) circuits associated with the main turbine emergency lube oil system determined the described condition to be applicable to MPS2.<br /><br /> This condition is reportable pursuant to 10 CFR 50.73(a)(2)(ii)(B) as an unanalyzed condition that significantly degraded plant safety. A prompt notification per EN49902 was submitted to the NRC on March 12, 2014.<br /><br /> The cause of the condition was a manufacturer's design error that was installed during plant construction. Compensatory fire watches have been implemented for affected areas of the plant. Plant modifications are planned that will protect or isolate the affected circuits leaving the initial fire area.
3362014003 | Millstone 2 | 04/05/2014 | 06/02/2014 | ML14157A30 | <strong>Loss of Safety Function due to Inoperable Enclosure Building</strong><br /><i>Abstract:&nbsp;</i>On April 5, 2014, with Millstone Power Station Unit 2 at 100% power in Mode 1, the Enclosure Building was rendered inoperable during a maintenance activity. The condition was created at approximately 1025 and restored to operable status at 1300 on April 5, 2014. Plant Technical Specification (TS) 3.6.5.2 requires that the Enclosure Building shall be operable in Modes 1, 2, 3, and 4. The TS 3.6.5.2 Action is to restore the Enclosure Building to operable status within 24 hours or be in cold shutdown within the next 36 hours. Therefore, the TS 3.6.5.2 Action requirements were met.<br /><br /> Since the Enclosure Building was inoperable from approximately 1025 until restored at 1300, the safety function of the Enclosure Building to limit radiological releases or mitigate the consequences in the event of a design basis accident could not be assured. The condition was created as the result of a human performance error while performing a maintenance activity associated with the Enclosure Building boundary. Since this was a human performance error, the event and lessons learned were communicated to the Millstone Site as a Station Human Performance Clock Reset.
3362014004 | Millstone 2 | 04/10/2014 | 06/09/2014 | ML14164A02 | <strong>Foreign Material Found in a Motor Lead Rendered a Motor Driven Auxiliary Feedwater Pump Inoperable</strong><br /><i>Abstract:&nbsp;</i>On April 10, 2014, with Millstone Power Station Unit 2 in MODE 6 at 0% reactor power, while de-terminating the motor leads for the 'B' Motor Driven Auxiliary Feedwater (MDAFW) Pump motor, foreign material (ty-wraps and a plastic bag) were found inside the cable environmental seal (Raychem boot) of the 'A' phase. An inspection of the electrical motor leads revealed no damage occurred. This motor was last re-terminated In May 2000. The motor leads to the other phases did not have any foreign material inside the Raychem boot. Since the Raychem boot was not in the as tested environmentally qualified (EQ) configuration the 'B' MDAFW pump was considered inoperable. <br /><br /> Plant Technical Specifications (TS) 3.7.2.1 Action d, requires, if two AFW pumps are inoperable in operating MODES 1, 2, and 3, the plant must be placed in at least HOT STANDBY within six hours and in HOT SHUTDOWN within the following 12 hours. <br /><br /> A review of the control room logs for the past three years determined there were 4 occasions where there were two AFW pumps inoperable for longer than allowed by TS. <br /><br /> The direct cause was an historical inappropriate maintenance practice which rendered the MDAFW pump inoperable. The 'A' phase motor lead was subsequently properly re-terminated. <br /><br /> This condition is being reported under 10 CFR 50.73(a)(2)(i)(B) as any operation or condition which was prohibited by the plant's Technical Specifications.
3362014005 | Millstone 2 | 05/17/2014 | 07/16/2014 | ML14203A04 | <strong>Train "A" Containment Spray Inoperable due to Gas Voids</strong><br /><i>Abstract:&nbsp;</i>At 1933 on May 16, 2014 while in MODE 3, Millstone Power Station Unit 2 (MPS2) exceeded the Limiting Condition for Operation (LCO) of plant Technical Specification (TS) 3.6.2.1 'Containment Spray System' Action a.1 for an inoperable containment spray pump. The 'A' containment spray (CS) pump was declared inoperable at 0018 on May 17, 2014, the date of discovery, following completion of surveillance testing to determine the presence of gas voids. However, the gas was introduced earlier during the refueling outage and the TS LCO went into effect upon first entry into MODE 3 greater than 1750 psia on May 13, 2014, at 1933. TS 3.6.2.1 Action a.1 requires that the pump be restored to OPERABLE status within 72 hours or be in at least HOT STANDBY within the next 6 hours and reduce pressurizer pressure to less than 1750 psia within the following 6 hours. MPS2 had been in a MODE where the CS system was required to be OPERABLE for 70.5 hours prior to completion of the testing. The gases were successfully removed by venting and the system was restored to OPERABLE status at 1221 on May 17, 2014.<br /><br /> This condition is being reported as any operation or condition which was prohibited by the plant's technical specifications in accordance with 10 CFR 50.73 (a)(2)(i)(B). The condition was caused by not adequately venting the CS system and delays in communicating the surveillance results, combined with a need to schedule performance of the surveillance testing earlier in a refueling outage. Corrective actions planned will improve scheduling of the testing and will result in more timely communications of the results from completed testing.
3362014006 | Millstone 2, Millstone 3 | 05/25/2014 | 07/24/2014 | ML14211A52 | <strong>Millstone Power Station Dual Unit Reactor Trip on Loss of Offsite Power</strong><br /><i>Abstract:&nbsp;</i>On May 25, 2014, with Millstone Power Station (MPS) Unit 2 and 3 (MPS2 and MPS3) in operating MODE 1, operating at 100% reactor power, a total loss of offsite power occurred in the MPS switchyard. Both MPS2 and MPS3 experienced a turbine trip on power to load imbalance followed by an automatic reactor trip. Both units' safety related emergency diesel generators (EDGs) automatically started and supplied power to their respective safety busses. As designed, the motor driven auxiliary feedwater (AFW) pumps automatically started on MPS2 and all AFW pumps automatically started on MPS3.<br /><br /> MPS declared an Unusual Event (UE) following the reactor trips and the NRC was notified (EN50142 for MPS2 and EN 50141 for MPS3). Following stabilization of both MPS2 and MPS3, the UE was terminated.<br /><br /> With both MPS2 and MPS3 at full power and one of the Transmission Owner (TO) 345 kV lines out of service for scheduled work, a phase to ground fault occurred on one of the phases on a motor operated disconnect (MOD) on one of the three remaining TO 345 kV lines. The fault was caused by an insulator failure of a MOD switch at a TO substation (offsite). This fault was also sensed as an instantaneous ground in one of the two remaining TO 345 kV lines resulting in this line also tripping. With three of the four TO 345 kV lines out of service, the MPS total electrical output overloaded the single remaining TO 345 kV Line which then also tripped resulting in a total loss of offsite AC power to MPS.<br /><br /> The TO replaced the faulty components and is investigating additional corrective actions. Additional corrective actions are being taken in accordance with the station's corrective action program.<br /><br /> This event is being reported per 10 CFR 50.73(a)(2)(iv)(A) as an event that resulted in a manual or automatic actuation of systems listed in 10 CFR 50.73(a)(2)(iv)(B)(1), (6), and (8). Actuations of the reactor protection system, the AFW system, and the EDGs are reportable under this paragraph.
3362014007 | Millstone 2 | 07/26/2014 | 09/24/2014 | ML14275A09 | <strong>Completion of Plant Shutdown Required By Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On July 26, 2014 at 1411 hours, while in operating model, at 100% power, Millstone Power Station Unit 2 (MPS2) operators commenced an orderly shutdown of MPS2 since turbine driven auxiliary feedwater (TDAFW) pump repairs and required testing would not be completed within the time frame required by Technical Specification Action Statement (TSAS) 3.7.1.2 action c. MPS2 entered operating mode 4 (hot shutdown) at 0738 hours on July 27 thus completing the shutdown as required by the TSAS. <br /><br /> The direct cause of the shutdown of MPS2 was the inability to identify the cause of the surveillance test failure and complete the repair and retesting activities within the allowed TSAS time. Subsequent troubleshooting found foreign material inside the TDAFW recirculation orifice. The foreign material was removed, the TDAFW pump was retested and satisfactorily passed the required TS surveillance test. Additional inspection did not find any additional foreign material. Additional corrective actions are being taken in accordance with the station's corrective action program. <br /><br /> This event is being reported pursuant to 10 CFR 50.73(a)(2)(i)(A) - The completion of any nuclear plant shutdown required by the plant's technical specifications.
3382014001 | North Anna 1, North Anna 2 | 05/15/2014 | 07/14/2014 | ML14205A01 | <strong>Engineered Safety Feature Actuations due to Loss of Power to "C" Reserve Station Service Transformer</strong><br /><i>Abstract:&nbsp;</i>At 1920 on May 15, 2014, with both Units 1 and 2 operating at 100% power, the load side of switchyard transformer #3 faulted, causing a loss of the "C" Reserve Station Service Transformer (RSST). The cause of the event was due to a crow making contact with Bus #5 "A" phase to ground. The loss of the "C" RSST caused a power loss on the Unit 1 "H" (1H) and the Unit 2 "J" (2J) Emergency busses and the associated Emergency Diesel Generators (EDGs) auto-started and re-energized the busses. In addition, the Unit 2 "A" Charging pump autostarted due to the under-voltage condition on the 2J bus. The pump was secured and returned to auto at 1938 on May 15, 2014. At 2046 on May 15, 2014, offsite power was restored to the 1H Emergency bus and the 1H EDG was secured. At 0410 on May 16, 2014, offsite power had been restored to the 2J Emergency bus and the 2J EDG was secured. This event was reportable per 10CFR50.72(b)(3)(iv)(A) for actuation of an Engineered Safety Feature (ESF) system. The health and safety of the public were not affected by this event.
3382014002 | North Anna 1 | 12/10/2014 | 02/04/2015 | ML15044A03 | <strong>Inadvertent Loss of Vital Instrumentation During Maintenance due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On December 10, 2014, at 1344 hours, two channels of the Unit 1 Refueling Water Storage Tank (RWST) level instrumentation were inadvertently removed from service at the same time during maintenance. Operations personnel responded by entering abnormal procedure 1-AP-3, Loss of Vital Instrumentation. Additionally, Technical Specification (TS) 3.0.3 was entered due to two channels being inoperable that affect Recirculation Spray (RS) pump auto-start logic. Had a Containment Depressurization Actuation (CDA) occurred during this time, accident mitigation may have been impacted. At 1356 hours, both level indications returned to normal. At 1417 hours, Channel II was declared operable and TS 3.0.3 was cleared. At 1439 hours, Channel I was declared operable and TS Actions were cleared. An 8-hour report was made at 1713 hours per 10 CFR 50.72(b)(2)(v)(D) for a condition that could have prevented the fulfillment of a safety function to mitigate the consequences of an accident. The health and safety of the public were not affected by this event.
3382014003 | North Anna 1 | 12/22/2014 | 02/11/2015 | ML15058A03 | <strong>Technical Specification Required Shutdown due to Reactor Coolant System Pressure Boundary Leakage</strong><br /><i>Abstract:&nbsp;</i>On December 22, 2014, Unit 1 reactor power was reduced from 100% to 30% to allow entry into the Reactor Coolant System loop rooms to investigate an increased unidentified leak rate of 0.053 gallons per minute. At 2230 on December 22, 2014, with Unit 1 operating at 30% power, during a containment walkdown, steam was discovered coming from underneath the lagging on the "B" Reactor Coolant System intermediate loop. Further investigation identified a pressure boundary leak on the "B" loop drain piping between the loop connection and 1-RC-68, the "B" Loop Cold Leg Drain Isolation Valve. At that time, the limiting action of Technical Specification 3.4.13, RCS Operational Leakage, Condition B was entered which required placing the unit in Mode 3 within 6 hours and Mode 5 within 36 hours. Due to the pressure boundary leakage, this event was reported at 0057 on December 23, 2014, in accordance with 10 CFR 50.72(b)(2), for "Initiation of plant shutdown required by Technical Specifications" and 10 CFR 50.72(b)(3)(ii)(A) for "Any event or condition that results in the condition of the nuclear power plant including its principle safety barriers, being seriously degraded." The health and safety of the public were not affected by this event.
3392014001 | North Anna 2 | 02/02/2014 | 04/02/2014 | ML14098A25 | <strong>Manual Reactor Trip During Feedwater Transient</strong><br /><i>Abstract:&nbsp;</i>At 0859 on February 2, 2014, with Unit 2 operating at 100% power, the "A" Main Feedwater (MFW) Pump, 2-FW- P-1A, had a motor lead connection that grounded and caused the power supply breakers for 2-FW-P-1A to trip open. The standby MFW pump, 2-FW-P-1C, auto started, as designed. The Reactor Operator (RO) believed the standby pump did not auto start, since one of the Control Room indicating lights did not illuminate as expected. The RO believed that only one MFW pump was running with two required for operation greater than 70% power. Based on this indication and the perceived loss of MFW, the RO initiated a manual reactor trip as directed in 2-AP-31. Although the remaining control room team members were aware that the standby pump had autostarted, they were unable to intervene in time to prevent the manual trip. Following the manual reactor trip, the unit was stabilized in Mode 3 at normal reactor coolant temperature and pressure. This event was reportable per 10CFR50.72(b)(2)(iv)(B) for actuation of the reactor protection system. Following the reactor trip, the Auxiliary Feedwater pumps automatically started as designed and provided makeup flow to the steam generators. This event was reportable per 10CFR50.72(b)(3)(iv)(A) for actuation of an Engineered Safety Feature (ESF) system. The health and safety of the public were not affected by this event.
3392014002 | North Anna 2 | 09/15/2014 | 11/12/2014 | ML14325A69 | <strong>Failed Fuel Assembly</strong><br /><i>Abstract:&nbsp;</i>On September 15, 2014, with Unit 2 defueled, debris that had the potential to be fuel fragments was located on the core plate directly below the B11 core location, where fuel assembly 4Z9 resided during Cycle 23. Video inspection of fuel assembly 4Z9 identified that the top springs of two fuel pins were dislodged. Due to the fact that the fuel damage exceeded expected conditions, at 1454 on September 15, 2014, this event was reported as an eight hour report as per 10 CFR 50.72(b)(3)(ii)(A), any event or condition that results in the condition of the nuclear plant, including its principle safety barriers, being seriously degraded. Detailed video inspections estimated that 15 fuel pellets were dislodged from fuel assembly 4Z9. During efforts to identify and recover the fuel pellets, 7 fuel pellets worth of material were not found and have already or are expected to granulate into fine particles that will dissolve in low flow areas of the primary plant systems, or be removed by normal purification processes. Since the specific location of the 7 fuel pellets is undesignated and because those pellets contain licensed material in a quantity greater than 10 times the quantity specified in App. C of 10 CFR 20, a report was made at 1227 on September 30, 2014, pursuant to 10 CFR 74.11(a) and to 10 CFR 20.2201(a)(ii). The health and safety of the public were not affected by this event.
3462014001 | Davis-Besse | 05/04/2014 | 06/27/2014 | ML14183B69 | <strong>Manual Initiation of the Reactor Protection System due to Unexpected Indication of Control Rod Movement</strong><br /><i>Abstract:&nbsp;</i>On May 4, 2014, with the Davis-Besse Nuclear Power Station in Mode 3 and the Reactor Coolant System at normal operating temperature and pressure, testing was in progress on the Control Rod Drive (CRD) System. When a Group 8 Axial Power Shaping Rod was withdrawn, indication was received of movement of a Group 4 Control Rod. The Group 4 Control Rod indication was manually driven to zero percent indication and the reactor trip breakers were opened from the Control Room.<br /><br /> The erroneous indication was due to improper connection of a Containment Electrical Penetration for CRD System position indication during the refueling outage. The penetration was rewired to permit startup activities to continue. The Post-Maintenance Test Manual will be updated to add guidance for testing Containment Electrical Penetrations associated with the CRD System.<br /><br /> This event is being reported pursuant to 10 CFR 50.73(a)(2)(iv)(A) as an event that resulted in manual actuation of the Reactor Protection System with the reactor not critical.
3462014002 | Davis-Besse | 05/05/2014 | 07/07/2014 | ML14189A41 | <strong>Manual Initiation of the Reactor Protection System due to Disconnected Cooling of a Control Rod Drive</strong><br /><i>Abstract:&nbsp;</i>On May 5, 2014, with the Davis-Besse Nuclear Power Station in Mode 3 and the Reactor Coolant System at normal operating temperature and pressure, workers were replacing a Control Rod Drive (CRD) Position Indication Tube due to incorrect indications identified during startup testing. Because of the tight working conditions, a flexible cooling line was moved aside to replace the Position Indication Tube, which caused inadvertent disengagement of a quick disconnect fitting, resulting in inadvertent isolation of cooling water to another CRD mechanism. When the CRD mechanism reached a procedural temperature limit, the reactor trip breakers were manually opened from the Control Room.<br /><br /> The cause of this event was not completely identifying and assessing all risks and consequences before conducting the tube replacement. The cooling line was reconnected, and the preventive maintenance activity for performing this work will be revised to add a specific precaution regarding the susceptibility of the cooling hose quick disconnects to become disengaged.<br /><br /> This event is being reported pursuant to 10 CFR 50.73(a)(2)(iv)(A) as an event that resulted in manual actuation of the Reactor Protection System with the reactor not critical.
3462014003 | Davis-Besse | 08/18/2014 | 10/17/2014 | ML14294A09 | <strong>Door Latch Failure Results in Loss of Emergency Ventilation System Function</strong><br /><i>Abstract:&nbsp;</i>On August 18, 2014, with the Davis-Besse Nuclear Power Station operating in Mode 1 approximately 100 percent full power, a door to a mechanical penetration room could not be secured following normal usage. This door is required to be latched closed to maintain the shield building negative pressure boundary except when open under administrative control. With the door unable to be latched closed, the Station Emergency Ventilation System could not perform its required safety function of maintaining a negative pressure in the affected area. The door was restored to the latched status in ten minutes. A similar failure to latch on August 20, 2014, was also experienced, and the door was re-latched in four minutes.<br /><br /> The cause of this event was a design flaw that could cause the latch fingers to stick, preventing the door from latching; and an infantile failure of the door closer. A vendor modified version of the latch was installed along with a new door closer to correct the problem.<br /><br /> This event is being reported pursuant to 10 CFR 50.73(a)(2)(v)(C) and (D) as an event that could have prevented fulfillment of the safety function of the Station Emergency Ventilation System.
3462014004 | Davis-Besse | 11/25/2014 | 01/23/2015 | ML15028A19 | <strong>Deficiency in Loss of Coolant Accident Analysis Adversely Affected Predicted Peak Cladding Temperature</strong><br /><i>Abstract:&nbsp;</i>On November 25, 2014, with the Davis-Besse Nuclear Power Station (DBNPS) operating in Mode 1 at approximately 100 percent power, the fuel vendor for the DBNPS notified the FirstEnergy Nuclear Operating Company (FENOC) of the final evaluation results for a deficiency discovered in the thermal conductivity model computer codes. Accounting for the deficiency resulted in the predicted analytical Peak Cladding Temperature (PCT) for Large Break Loss of Coolant Accident Conditions increasing to an estimated 2513 degrees F, which is in excess of 2200 degrees F specified in 10 CFR 50.46(b)(1). Because the station had sufficient margin in the reactor core reload analysis and had previously implemented compensatory measures recommended by the fuel vendor when the potential issue was first identified, the deficiency had no impact on current plant operation or public health and safety. The cause of this event was related to the evolution of the fuel vendor's modeling.<br /><br /> This issue is being reported in accordance with 10 CFR 50.73(a)(2)(ii)(B) as an unanalyzed condition that significantly degraded plant safety.
3482014001 | Farley 1, Farley 2 | 02/18/2014 | 04/17/2014 | ML14107A33 | <strong>Failure to Comply with Technical Specification 3.4.3 During Reactor Coolant System Vacuum Refill</strong><br /><i>Abstract:&nbsp;</i>On February 18, 2014 with FNP Units 1 and 2 operating at 100 percent thermal power, a review of industry operating experience determined that both units were in non-compliance with Technical Specification 3.4.3, Reactor Coolant System (RCS) Pressure and Temperature (P/T) Limits, during several previous refueling outages on each unit due to placing the RCS under vacuum conditions during RCS vacuum refill operations. From October 1995 through April 2012, 12 refueling outages have been conducted on Unit 1 and 11 on Unit 2 during which the RCS was placed under vacuum to perform vacuum refill operations. Technical Specification 3.4.3, applicable at all times, requires that RCS pressure, RCS temperature, and RCS heatup and cooldown rates be maintained within the limits specified in the Pressure Temperature Limit Report (PTLR). Although RCS temperature and heatup rates were maintained within limits, RCS pressure was lowered below zero pounds per square inch gage (psig), the lowest RCS pressure value identified on the curve.<br /><br /> The cause of not entering the required action for Technical Specification 3.4.3 was due to a failure to recognize that a negative RCS pressure is not allowed by Technical Specifications. An engineering review in support of the implementation of vacuum refill operations had previously determined that stress margins of the reactor pressure vessel and related components were not challenged. The station's P/T Limit curve is being revised to encompass RCS vacuum conditions.
3482014002 | Farley 1 | 02/28/2014 | 10/09/2014 | ML14282A81 | <strong>B-Train RHR Inoperable for Longer Than Allowed by Technical Specifications due to Misadjusted Flow Control Valve Linkage</strong><br /><i>Abstract:&nbsp;</i>On February 28, 2014 at 1300, with Unit 1 operating at 100 percent thermal power, a lower than expected flow rate in the B-Train Residual Heat Removal (RHR) system was observed while conducting a surveillance test per procedure FNP-1- STP-11.2. Investigation of this condition determined that the low flow rate was a result of previous maintenance performed on October 13, 2013 to replace an actuator linkage on the B-Train RHR heat exchanger discharge valve, Q1E11HCV603B. Analysis of the February 28, 2014 test results determined that the B-train RHR system flow rate was less than the minimum allowed by Technical Specifications, rendering the B-Train RHR system inoperable. Since this condition has existed for a time period in excess of the applicable Technical Specification Required Action Completion Time, this is a violation of Technical Specifications and is reportable per 10 CFR 50.73(a)(2)(i)(B). Since the A-Train of RHR has been briefly inoperable during the period of B-Train RHR inoperability, this is also reportable per 10 CFR 50.73(a)(2)(v)(B,D).<br /><br /> To correct the low flow condition the full-open position of valve Q1E11HCV603B was adjusted to provide an acceptable flow rate. Corrective action taken established and communicated - using training, briefings, and performance monitoring plans - goals and expectations to improve issue resolution and prioritization, risk management, and response to operational challenges. Procedures were revised to identify valve adjustment verification requirements. The engineering analysis performed is preliminary and this LER will be supplemented if the final analysis warrants.
3482014003 | Farley 1, Farley 2 | 04/02/2014 | 06/02/2014 | ML14153A68 | <strong>Scaling Errors Result in Inoperable Steam Flow Channels for Durations Longer Than Allowed by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>At 1819 CDT on April 2, 2014, with Unit 1 operating in Mode 1 at 100 percent power, a review of scaling data identified that Unit 1 steam generator steam flow transmitter calibration procedures contained incorrect scaling data. Further analysis determined that the 1B Steam Flow Channel Q1C22FT0484 was outside of its allowable Technical Specification tolerance since being calibrated with the incorrect scaling data during the Fall 2013 refueling outage. This steam flow channel was subsequently re-scaled and returned to operable status on April 5, 2014 at 0821.<br /><br /> At 1300 CDT on April 8, 2014, with Unit 2 operating in Mode 1 at 100 percent power, the continuing review of scaling data also identified that Unit 2 steam generator steam flow transmitter calibration procedures contained incorrect scaling data. As a result, the 2C Steam Flow Channel Q2C22FT0494 was outside of its allowable Technical Specification tolerance since being calibrated during the Spring 2013 refueling outage. This steam flow channel was subsequently re-scaled and returned to operable status on April 9, 2014 at 0040.<br /><br /> Since both of these channels had been incorrectly scaled since the beginning of each unit's operating cycle (October, 2013 for Unit 1 and May 2013 for Unit 2) this represents a condition prohibited by Technical Specifications and is reportable pursuant to 10 CFR 50.73(a)(2)(i)(B).
3522014001 | Limerick 1 | 11/10/2013 | 06/16/2014 | ML14176A13 | <strong>Inoperable Reactor Enclosure Secondary Containment Integrity due to Open Airlock</strong><br /><i>Abstract:&nbsp;</i>Two workers simultaneously opened both doors of the reactor enclosure personnel airlock when entering the airlock at the same time. One worker opened the inboard airlock door and the other worker opened the outboard airlock door. Both doors were closed in less than 10 seconds. This event resulted in a brief inoperablility of reactor enclosure secondary containment integrity. This event was caused by a weakness in the design of the reactor enclosure airlocks. The airlock doors were closed to restore reactor enclosure secondary containment integrity.
3522014002 | Limerick 1 | 12/18/2013 | 02/18/2014 | ML14049A07 | <strong>Inoperable Reactor Enclosure Secondary Containment Integrity due to Open Airlock</strong><br /><i>Abstract:&nbsp;</i>Two workers simultaneously opened both doors of a reactor enclosure personnel airlock when entering the airlock at the same time. One worker opened the inboard airlock door and the other worker opened the outboard airlock door. Both doors were closed in less than 10 seconds. This event resulted in a brief inoperability of reactor enclosure secondary containment integrity. This event was not prevented by the design of the reactor enclosure airlocks. A modification is being evaluated for the airlock doors.
3522014003 | Limerick 1 | 02/06/2014 | 03/28/2014 | ML14093A29 | <strong>Inoperable Reactor Enclosure Secondary Containment Integrity due to Open Airlock</strong><br /><i>Abstract:&nbsp;</i>A worker allowed both doors of a reactor enclosure personnel airlock to be open simultaneously. Both doors were closed in less than 10 seconds. This event resulted in a brief inoperability of reactor enclosure secondary containment integrity. The cause of this event was failure of the worker to self check. The worker opened the outboard airlock door prior to allowing the inboard airlock door to go full closed. This event was not prevented by the design of the reactor enclosure airlocks. The affected airlock doors were closed to restore reactor enclosure secondary containment integrity.
3522014004 | Limerick 1 | 03/04/2014 | 05/05/2014 | ML14125A14 | <strong>Valid Manual Actuation of the Reactor Protection System with the Reactor Critical due to Closure of Turbine Valves</strong><br /><i>Abstract:&nbsp;</i>A valid manual actuation of the reactor protection system (RPS) was initiated due to an unexpected closure of all six main turbine intercept valves (TVs). The cause of the main turbine IVs closure was due to a degraded Electro-hydraulic Control (EHC) 30 VDC house power supply. The Unit 1 EHC system was replaced with a Digital EHC (DEHC) system during the subsequent refueling outage 1R15. The Unit 2 EHC system is scheduled to be replaced with a DEHC system during the next refueling outage 2R13 in April 2015. The Unit 2 EHC house and permanent magnet generator (PMG) power supplies as-found voltages were verified to be within the calibration procedure limits and the as-left voltages were adjusted to the middle of the procedure acceptable band during the planned maintenance outage 2M49.
3532014001 | Limerick 2 | 12/18/2013 | 02/18/2014 | ML14049A08 | <strong>Inoperable Reactor Enclosure Secondary Containment Integrity due to Open Airlock</strong><br /><i>Abstract:&nbsp;</i>Two workers simultaneously opened both doors of a reactor enclosure personnel airlock when entering the airlock at the same time. One worker opened the inboard airlock door and the other worker opened the outboard airlock door. Both doors were closed in less than 10 seconds. This event resulted in a brief inoperability of reactor enclosure secondary containment integrity. This event was not prevented by the design of the reactor enclosure airlocks. A modification is being evaluated for the airlock doors.
3532014002 | Limerick 2 | 01/09/2014 | 03/07/2014 | ML14066A36 | <strong>Inoperable Reactor Enclosure Secondary Containment Integrity due to Open Airlock</strong><br /><i>Abstract:&nbsp;</i>Two workers simultaneously opened both doors of a reactor enclosure personnel airlock when entering the airlock. One worker opened the inboard airlock door and the other worker opened the outboard airlock door. Both doors were closed in less than 10 seconds. This event resulted in a brief inoperability of reactor enclosure secondary containment integrity. This event was not prevented by the design of the reactor enclosure airlocks. The affected airlock doors were closed to restore reactor enclosure secondary containment integrity.
3532014003 | Limerick 2 | 03/20/2014 | 05/19/2014 | ML14139A49 | <strong>Inoperable Reactor Enclosure Secondary Containment Integrity due to Open Airlock</strong><br /><i>Abstract:&nbsp;</i>Workers simultaneously opened both doors of a reactor enclosure personnel airlock when transporting equipment through the airlock. One worker opened the Unit 1 airlock door and the other worker opened the Unit 2 airlock door before the Unit 1 door was fully closed. Both doors were closed in less than 10 seconds. This event resulted in a brief inoperability of reactor enclosure secondary containment integrity. The cause of the event was a worker deviated from the pre-job briefing instructions regarding one worker being responsible to open and close the airlock doors while the other workers were responsible for pushing the cart through the open door. When the worker deviated from the briefing instructions the worker did not adhere to the airlock door policy. This event was not prevented by the design of the reactor enclosure airlocks since there is no mechanical interlock and the door open indicating light does not prevent simultaneous opening of both airlock doors. The affected airlock doors were closed to restore reactor enclosure secondary containment integrity. The worker was coached regarding compliance with the responsibilities assigned at the pre-job brief and airlock door use. The lessons learned were communicated to the site.
3532014004 | Limerick 2 | 04/04/2014 | 06/03/2014 | ML14154A29 | <strong>Inoperable Reactor Enclosure Secondary Containment Integrity due to Open Airlock</strong><br /><i>Abstract:&nbsp;</i>Workers simultaneously opened both doors of a reactor enclosure personnel airlock when transporting material through the airlock. One worker opened the outboard airlock door before the inboard airlock door was properly closed and latched. Both doors were closed in less than 10 seconds. This event resulted in a brief inoperability of reactor enclosure secondary containment integrity. The event was caused by the workers' failure to verify the inboard airlock door was latched fully closed prior to opening the outboard airlock door. The workers failed to properly use the self-check fundamental. The airlock doors were closed to restore reactor enclosure secondary containment integrity. The workers were coached regarding use of the self-check fundamental. The lessons learned were communicated to the site.
3532014005 | Limerick 2 | 04/24/2014 | 06/23/2014 | ML14174B41 | <strong>High Pressure Coolant Injection System Inoperability due to ECCS Actuation Instrument Channel Setpoint Drift</strong><br /><i>Abstract:&nbsp;</i>One emergency core cooling system (ECCS) actuation instrumentation channel was determined to have been inoperable for a period that exceeded the Technical Specification (TS) action allowed completion time. The as-found setpoint exceeded the required limit during three consecutive 18-month calibration surveillance tests. The channel was one of two redundant high pressure coolant injection (HPCI) system suppression pool high level channels. The apparent cause of the event was a less than adequate review of the issue report that identified three setpoint drift events on a degraded HPCI level transmitter. The degraded HPCI suppression pool level transmitter was replaced. A Plant Engineering briefing was conducted to reinforce prompt and thorough evaluation of potential system operability and regulatory impacts of repetitive TS instrument recalibrations
3532014006 | Limerick 2 | 08/05/2014 | 10/02/2014 | ML14275A27 | <strong>Inoperable Reactor Enclosure Secondary Containment Integrity Due to Open Airlock</strong><br /><i>Abstract:&nbsp;</i>A worker failed to physically challenge the latch on the inboard reactor enclosure airlock door when traversing from the refuel floor into the reactor enclosure. The next worker to use the airlock opened the outboard door causing the inboard door to open due to differential pressure across the door. The outboard door was closed in less than 10 seconds. This event resulted in a brief inoperability of reactor enclosure secondary containment integrity. The event was caused by a degraded airlock door self-closing feature on the inboard airlock door. A contributing cause was a worker failure to verify that the inboard airlock door was latched fully closed. The worker failed to properly use the self-check fundamental. The airlock doors were immediately closed to restore reactor enclosure secondary containment integrity and the degraded door self-closing feature was repaired. The worker was coached regarding use of the self-check fundamental. The lessons learned were communicated to the site.
3532014007 | Limerick 2 | 12/11/2014 | 02/04/2015 | ML15035A26 | <strong>Inoperable Reactor Enclosure Secondary Containment Integrity due to Open Airlock</strong><br /><i>Abstract:&nbsp;</i>A worker failed to verify that the inboard door was closed prior to opening the outboard door when traversing from the reactor enclosure to the refuel floor. The outboard door was closed in less than 10 seconds. This event resulted in a brief inoperability of reactor enclosure secondary containment integrity. The cause of the event was that the technician failed to use proper human performance fundamentals to make sure the blue light was off prior to proceeding and opening the second door in the airlock. The airlock doors were immediately closed to restore reactor enclosure secondary containment integrity. The workers involved were coached and lessons learned were communicated to the site.
3642014001 | Farley 2 | 01/11/2014 | 03/12/2014 | ML14072A28 | <strong>Inoperable B-Train Solid State Protection System Results in Technical Specification Required Shutdown</strong><br /><i>Abstract:&nbsp;</i>On January 11, 2014 at 14:53 CST, Farley Nuclear Plant (FNP) Unit 2 completed a shutdown from 100 percent power to Mode 3 to comply with Required Actions of Technical Specifications 3.3.1 (Reactor Trip System Instrumentation) and 3.3.2 (Engineered Safety Feature Actuation System Instrumentation). These Required Actions had been voluntarily entered on January 10, 2014 at 0919 CST in order to perform periodic logic surveillance testing on the B-Train Solid State Protection System (SSPS). FNP was unable to rectify logic testing failures encountered during the testing within the time requirements of the Required Actions, necessitating the shutdown. This shutdown is reportable under 10 CFR 50.73(a)(2)(i)(A). Subsequent troubleshooting identified the direct cause of the logic test failures to be due to foreign material causing an intermittent short between two logic card connector pins. Following removal of the foreign material the SSPS was restored to operable status and Unit 2 was restarted on January 14, 2014. The root cause of this event was determined to be that station leadership did not appropriately manage the risk associated with past indeterminate SSPS failures. Corrective actions include an intensive inspection of both units' SSPS cabinets for foreign material, to revise troubleshooting procedures to include component validation during troubleshooting and to establish a practice of timely issue resolution when the direct cause of a failure was not validated during initial troubleshooting.
3642014002 | Farley 2 | 10/14/2014 | 12/12/2014 | ML14346A39 | <strong>Manual Reactor Trip due to Loss of 2B Startup Auxiliary Transformer and Loss of Offsite Power</strong><br /><i>Abstract:&nbsp;</i>On 10/14/14 at 0341 CDT, Unit 2 reactor was manually tripped after a lightning strike In the High Voltage Switchyard (HVSY) led to a phase 3 to ground fault on a 500kV transmission line resulting in a B train Loss of Site Power (LOSP). The fault caused the 2B Startup Auxiliary Transformer (SAT) Instantaneous overcurrent relay to actuate and resulted in deenergizing the 2B SAT. A missing nut in the Power Circuit Breaker (PCB) protection circuitry caused a high resistance on one side of the current transformer circuit resulting in an imbalance in current flows and an actuation in the primary differential instantaneous overcurrent relaying. The B train LOSP in conjunction with the 2B Emergency Diesel Generator (EDG) being out of service for a planned maintenance outage caused a loss of Component Cooling Water (CCW) to the Reactor Coolant Pumps (RCP). The Unit 2 Abnormal Operating Procedures for loss of CCW and loss of A or B Train Electrical Power were entered and the reactor was manually tripped and the RCPs were secured. The reactor trip is reportable per 10 CFR 50.73(a)(2)(iv)(A) for manual actuation of the reactor protection system. Additionally, the reactor trip resulted in a valid actuation of the Auxiliary Feedwater system which is reportable per 10 CFR 50.73(a)(2)(iv)(A).<br /><br /> Corrective actions include: installed the missing PCB current transformer (CT) nut; satisfactorily tested primary and secondary protective relaying for 2B SAT; and strengthening of switchyard standards of the utility performing the maintenance. Extent of Condition walkdowns were performed for other circuits in the HVSY and repaired as necessary
3642014003 | Farley 2 | 11/15/2014 | 01/13/2015 | ML15014A18 | <strong>Reactor Protection System Actuation due to Invalid Digital Rod Position Indication Signal</strong><br /><i>Abstract:&nbsp;</i>On 11/15/2014 at 0348 CST while withdrawing control rods for reactor startup and low power physics testing with control bank C at approximately 50 steps and the reactor subcritical, Digital Rod Position Indication (DRPI) for one of the control rods (M12) changed to 90 steps. The control room operators stopped withdrawing rods and entered the Abnormal Operating Procedure (AOP) for Malfunction of the Rod Control System. The reactor trip breakers were opened at 0353 CST and all rods inserted as expected. Causal analysis determined that the DRPI signal for rod M12 was invalid due to a failure of the detector/encoder card associated with the M12 rod.<br /><br /> This notification is being made as required by 10CFR 50.73(a)(2)(iv)(A) due to a manual actuation of the reactor protection system occurring when the control room operators opened the Unit 2 reactor trip breakers via the main control board hand switch during reactor startup procedures. This was a valid actuation of the reactor protection system. For corrective actions, the suspect DRPI detector/encoder card was replaced. The card will be sent to a vendor for failure analysis to determine the component on the card that actually failed. As an enhancement action, the AOP for Malfunction of the Rod Control System will be revised to assess rod position indication malfunction.
3662014001 | Hatch 2, Hatch 1 | 06/05/2014 | 11/20/2014 | ML14325A64 | <strong>Incorrectly Sized Thermal Overloads Result in a Condition Prohibited by Plant Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On 06/05/2014 at 0955 EDT, the 2A Emergency Diesel Generator (EDG) Room Exhaust Fans, 2X41-C010A and 2X41-C010B, were found in a tripped condition during the 2A Diesel Generator monthly surveillance. The 2A Diesel Generator was declared inoperable and the required actions were taken in accordance with the Technical Specifications. The thermal overloads for the pan assemblies feeding the fans had tripped due to incorrectly sized thermal overload heaters. New thermal overload heaters had been previously installed in February 2013 in conjunction with a modification that installed new pan assemblies. The new thermal overload heaters were found to be incorrectly sized, leading to thermal overloads with trip settings that were close to the normal operating current for the fans, resulting in premature trips of the thermal overloads.<br /><br /> On 06/06/2014 at 0542 EDT, Maintenance found the 1A EDG room exhaust fans, 1X41-C002A and 1X41-C002B, in the tripped condition and attributed their trip to the incorrectly sized thermal overloads. The pan assemblies for these fans had been replaced in April 2014 as part of the same modification as that performed on the 2A EDG pan assemblies. No other EDGs ventilation fan assemblies had been previously replaced.<br /><br /> The thermal overloads for the pan assemblies associated with the 1A and 2A EDG ventilation fans were replaced and the fans were returned to service.
3682014001 | Arkansas 2 | 03/31/2014 | 05/15/2014 | ML14135A24 | <strong>Operation of Switchgear Rooms' Ventilation Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>While performing a post-assessment of a 10 CFR 50.59 evaluation performed in 2002 for a modification to the Arkansas Nuclear One (ANO) Unit 2 switchgear room exhaust fans, ANO identified that automatic action had been replaced with credit for manual operator action. During additional evaluations of this concern, it was identified that there was one occasion within the last three years in which the room coolers and exhaust fan configuration did not support the operability of the switchgear room without reliance on operator action, which was longer than the time allowed by Technical Specification.<br /><br /> The apparent cause of this condition is the inappropriate credit of operator action in place of an automatic action.<br /><br /> As a corrective action, caution cards were promptly placed on the Control Room hand switches and local breakers associated with the exhaust fans.
3682014002 | Arkansas 2 | 04/03/2014 | 06/02/2014 | ML14153A38 | <strong>Automatic Reactor and Main Generator Trip with a Subsequent Emergency Feedwater Actuation and Start of an Emergency Diesel Generator</strong><br /><i>Abstract:&nbsp;</i>On April 3, 2014, at approximately 1300 CST, Arkansas Nuclear One Unit 2 (ANO-2) tripped from 100% power due to a fault in 161kV Russellville East Line. The fault caused a momentary degraded voltage state on the 161kV and 500kV grid at ANO and an undervoltage condition for ANO-2 Startup #3 Transformer (SU3). This under voltage condition caused SU3 undervoltage relays to initiate a fast transfer of ANO-2 4160V bus (2A-1) and 6900V bus (2H-1), to Startup Transformer #2 (SU2). Buses ANO-2 6900V (2H-2) and 4160V (2A-2) were not allowed to fast transfer to SU2 because of operational restraints per design. The removal of power to 2A-2 caused an auto start of the ANO-2 Emergency Diesel Generator (2K-4B) due to under voltage on safety bus 2A-4 which is normally fed from 2A-2. Bus 2A-2 slow transferred back to SU3. 2K-4B did not tie to 4160V safety bus (2A-4) as voltage had recovered prior to the diesel reaching rated speed and voltage. Bus 2H-2 was de-energized causing the loss of two Reactor Coolant Pumps (RCPs) which led to a reactor trip on low RCP speed and the actuation of the Emergency Feedwater System (EFW) on low Steam Generator Level. It was determined that a lighting strike caused a three phase fault on the 161kV Russellville East Line causing the ANO-2 trip. The corrective action is for Entergy Arkansas to review the adequacy of 161kV Russellville East Transmission Line Lightning Protection System.
3682014003 | Arkansas 2 | 04/27/2014 | 06/26/2014 | ML14177A30 | <strong>Axial Shape Index Trip at the End-of-Life During Rapid Plant Shutdown</strong><br /><i>Abstract:&nbsp;</i>During severe weather on April 27, 2014, both units at Arkansas Nuclear One (ANO) were informed of a system-wide grid emergency and were ordered to come off-line as soon as possible. Both units commenced a rapid plant shutdown. ANO, Unit 2 (ANO-2) was at the end of the core life. During the shutdown, the Axial Shape Index (ASI) became more negative (power rising to the upper portion of the core) during the shutdown. This led to one channel of the Plant Protection System (PPS) to be actuated on an ASI auxiliary trip. At this time, the direction to manually trip the reactor was given, but before the action could be taken, an automatic reactor trip occurred due to the two-out-of-four PPS logic being made up for the ASI conditions.<br /><br /> The cause of this condition was not effectively executing the reactivity management plan by delaying insertion of Control Element Assemblies (CEAs) and not inserting CEAs deep enough to maintain ASI within the desired control band.<br /><br /> Training material is being modified to include details on the dynamic effects of ASI change that occurs at the end-of-cycle. Additionally, improvements to the guidance in the reactivity plans that involve rapid plant shutdowns are being made as are changes to the standards for use of CEAs during transients.
3682014004 | Arkansas 2 | 06/09/2014 | 10/23/2014 | ML14301A04 | <strong>Technical Specification 3.0.4 Violation due to a Mode Change with an Inoperable Emergency Feedwater Pump</strong><br /><i>Abstract:&nbsp;</i>On June 12, 2014, at 1136 Central Standard time (CST), while shutdown in Mode 3, it was determined that on June 9, 2014, at 1820 CST Arkansas Nuclear One - Unit-2 (ANO-2) made a Mode Change from Mode 4 to Mode 3 with one of the two required Emergency Feedwater Pumps (EFW) inoperable due to a human performance error. The work instructions for the normal control system calibration performed in Mode 5 was not performed as written and did not require a second verification after critical adjustments were performed. This permitted an undetected mis-adjustment of the low governor frequency null voltage to exist within the governor control circuit resulting in EFW pump 2P-7A being inoperable. The 2P-7A inoperability resulted in a violation of Technical Specification (TS) 3.0.4 which precludes entry in a mode or other specified condition in the Applicability statement when a Limiting Condition of Operation (LCO) is not met and the Action requires a plant shutdown if the LCO is not met within a specified interval. LCO 3.7.1.2 requires two EFW pumps to be OPERABLE in Modes 1, 2, and 3. EFW pump 2P-7A has a 72-hour Allowable Outage Time with a required plant shutdown per TS 3.7.1.2 Action statement. The condition was corrected and a surveillance test assuring Operability was completed on June 11, 2014, at 0420 CST. 2P-7A EFW pump was declared Operable on June 11, 2014, at 0523 CST. This issue resulted in minimal safety significance.
3692014001 | McGuire 1 | 08/21/2014 | 12/17/2014 | ML15005A04 | <strong>Condition Prohibited by Technical Specifications (TS) due to Emergency Diesel Generator 1B Failure</strong><br /><i>Abstract:&nbsp;</i>On August 18, 2014, approximately 14 hours into a 24 hour surveillance test of Emergency Diesel Generator (EDG) 1B, Operators noted cylinder 5L exhaust temperature decreased by 130 degrees Fahrenheit and power indication began oscillating. Operations began an orderly shutdown of EDG 1B. Subsequently, Operators in the diesel room reported an unusual noise, at which time Operations immediately unloaded and stopped EDG 1B. EDG 1B was subsequently repaired and tested satisfactorily. This event is being reported under 10 CFR 50.73(a)(2)(i)(B) as an operation or condition which was prohibited by the plant's Technical Specification due to EDG 1B repair and testing exceeding the 72 hour completion time as mandated by TS 3.8.1.<br /><br /> On August 21, 2014, McGuire Unit 1 requested a Notice of Enforcement Discretion (NOED) in anticipation of exceeding TS 3.8.1 "AC Sources - Operating" Required Action Completion Time. The NOED was granted by the NRC on the same day.<br /><br /> The cause of the EDG 1B cylinder 5L failure is high cycle fatigue of the inlet valve due to the combined effects of three inlet valve train parts which were manufactured outside of original equipment manufacturer (OEM) specified tolerances. Procurement of the applicable parts has been placed on hold until the parts specification is revised.
3692014002 | McGuire 1 | 09/27/2014 | 11/24/2014 | ML14365A04 | <strong>Degraded Condition due to Rejectable Flaws on 1B and 1C Safety Injection Lines</strong><br /><i>Abstract:&nbsp;</i>While Unit 1 was in a refueling outage on September 26, 2014, manual ultrasonic (UT) examinations identified indications on Safety Injection (NI) system piping. On September 27, phased-array UT techniques confirmed two indications as rejectable flaws. Because the flaws were rejectable under American Society of Mechanical Engineers (ASME) Code requirements, this event is reportable as a degraded condition in accordance with 10CFR50.73(a)(2)(ii)(A). Stress analysis showed that the cracks would not have prevented the piping from performing its safety function, so this event did not impact public health and safety.<br /><br /> The cause of both flaws is a legacy issue of previous leakage past valve 1NI-3 (Unit 1 Cold Leg Injection Isolation) creating a high frequency thermal cycle condition. When combined with original construction deficiencies in the affected lines, this condition initiated the fatigue cracks identified during the UT examinations.<br /><br /> Actions were taken to repair the NI piping on Unit 1 and to inspect other susceptible lines before the unit restarted from its refueling outage. As part of planned corrective actions, valves with the potential to cause cold water in-leakage to these lines will be monitored for leakage.<br /><br /> Reference previous McGuire Unit 2 LER 370/2014-01, Revision 1, dated July 24, 2014.
3702014001 | McGuire 2 | 04/03/2014 | 07/24/2014 | ML14224A00 | <strong>Degraded Condition due to Rejectable Flaw on Safety Injection Piping</strong><br /><i>Abstract:&nbsp;</i>While Unit 2 was in a refueling outage on April 1, 2014, manual ultrasonic (UT) examinations identified indications on Safety Injection (NI) system piping. On April 3, 2014, phased-array UT techniques confirmed one indication as a rejectable flaw. Because the flaw was rejectable under American Society of Mechanical Engineers (ASME) Code requirements, it is reportable as a degraded condition. Stress analysis showed that the crack would not have prevented the piping from performing its safety function, so this event did not impact public health and safety.<br /><br /> The cause of the flaw is a legacy issue of previous leakage past valve 2NI-3 (Unit 2 Cold Leg Injection Isolation) creating a high frequency thermal cycle condition. This condition initiated the fatigue crack identified during the UT examination. Additionally, this flaw was missed during the previous refueling outage as a result of a probable skill-based human performance error.<br /><br /> Actions were taken to repair the NI piping on Unit 2 and to re-inspect other susceptible lines before the unit restarted from its refueling outage. Based on an extent of condition evaluation, a reasonable assurance of operability exists for similar Unit 1 configurations. As part of planned corrective actions, 2NI-3 (and its Unit 1 equivalent) will be isolated from the safety injection line.
3732014001 | LaSalle 1, LaSalle 2 | 02/18/2014 | 04/21/2014 | ML14121A07 | <strong>Secondary Containment Inoperable due to Interlock Doors Open</strong><br /><i>Abstract:&nbsp;</i>On February 18, 2014, Unit 1 was in Mode 5 with fuel moves in progress during refueling outage L1R15, and Unit 2 was in Mode 1 at 100% power. At 1820 hours CST, it was reported that both air-lock doors of the Unit 2 Reactor Building 710' elevation between the Unit 2 diesel generator corridor and the Unit 2 Reactor Building were open at the same time for approximately 3 seconds. While both interlock doors were open, Technical Specification (TS) Surveillance Requirement (SR) 3.6.4.1.2 ("Verify one secondary containment access door in each access opening is closed") was not met. Secondary containment was declared inoperable for the time that both interlock doors were open. TS 3.6.4.1 Required Action (RA) C.1 to suspend fuel movements on Unit 1 and RA A.1 to restore secondary containment to OPERABLE status within 4 hours were entered and exited at 1820 CST on February 18, 2014.<br /><br /> The cause of the event was degradation of the door closure mechanism and door frame seal. A contributing cause was a less than robust design of the door interlock assembly. Corrective actions from the previous occurrences to identify, procure and install a more robust interlock assembly design were still in progress at the time of the event. Additional corrective actions included creating a periodic preventative maintenance task to inspect, tighten, and replace fasteners as necessary.
3732014002 | LaSalle 1 | 03/29/2014 | 05/23/2014 | ML14143A13 | <strong>Unit 1 Division 3 Ventilation Failure</strong><br /><i>Abstract:&nbsp;</i>On March 29, 2014, Unit 1 was in Mode 1 at 100% power. At 1620 hours CDT, the Division 3 Core Standby Cooling System (CSCS) Pump Room, Switchgear Room, and Battery Room Ventilation failed in such a manner that heat could not be removed from the rooms. Due to the lack of ventilation in the Division 3 switchgear room the High Pressure Core Spray (HPCS) system was declared inoperable and Condition B of Technical Specification (TS) 3.5.1 was entered.<br /><br /> The cause of the event was a failure of the hydramotor pump bearing for the 1VD19Y, Division 3 CSCS Ventilation Return Fan Outlet Damper. Loss of hydraulic pressure in the hydramotor resulted in 1VD19Y failing in the closed position. The corrective action for the event was replacement of the hydramotor for the 1VD19Y damper.
3732014003 | LaSalle 1, LaSalle 2 | 04/30/2014 | 06/27/2014 | ML14178B23 | <strong>Secondary Containment Inoperable due to Interlock Doors Open</strong><br /><i>Abstract:&nbsp;</i>On April 30, 2014, Unit 1 was in Mode 1 at 100% power and Unit 2 was in Mode 5 with fuel moves in progress for maintenance outage L2M17. At 1037 hours CDT, it was reported that both air lock doors on the Unit 2 Auxiliary Building 710' elevation between the Chemistry Hot Lab and the Reactor Building were open at the same time for approximately 5 seconds. While both interlock doors were open, Technical Specification (TS) Surveillance Requirement (SR) 3.6.4.1.2 ("Verify one secondary containment access door in each access opening is closed") was not met for both Units 1 and 2. Secondary containment was declared inoperable for the time that both interlock doors were open. TS 3.6.4.1 Required Actions (RA) C.1, C.2 and C.3 to immediately suspend irradiated fuel movements, core alterations, and OPDRVs on Unit 2 and RA A.1 to restore secondary containment to OPERABLE status within 4 hours were entered and exited at 1037 CDT on April 30, 2014.<br /><br /> The cause of the event was determined to be that the single mounting bolt holding the armature plate to door #247 had become disengaged and the plate had fallen to the floor, causing the electromagnetic locking function to fail. The armature mounting bolt had not been properly tensioned and Loctite had not been used during installation of the armature plate. Corrective actions were to reinstall the armature plate with proper tensioning of the mounting bolt and with Loctite applied to the threads. All other susceptible armature plate mountings at LaSalle were inspected and verified for proper torque and use of Loctite.
3732014004 | LaSalle 1, LaSalle 2 | 08/28/2014 | 10/27/2014 | ML14310A29 | <strong>Auxiliary Electric Equipment Room HVAC Inoperable due to Compressor Trip</strong><br /><i>Abstract:&nbsp;</i>On August 28, 2014, both Units 1 and 2 were in Mode 1 at 100% power. The 'B' train of Auxiliary Electric Equipment Room ventilation (VE) was inoperable due to a planned repair of an oil leak. The Main Control Room ventilation envelope consists of both the Main Control Room and the Auxiliary Electric Equipment Room. Both the Control Room HVAC (VC) and VE were required to be operable at the time of the occurrence. Technical Specification (TS) 3.7.5 Required Action (RA) A.1 had been entered to restore the control room area ventilation (VC) air conditioning subsystem to operable status within 30 days.<br /><br /> At 1227 hours CDT, the Main Control Room received a start alarm on the Unit 1 plant process computer (PPC) for the 'A' train VE compressor. A check of the PPC computer point indicated that the 'A' train VE compressor was not running. The rounds operator responded and reported that the 'A' train VE compressor was cycling on and off. The 'A' train of VC/VE was declared inoperable. With both trains of VC/VE inoperable, the Station entered TS 3.7.5 RA B.1 to verify control room area temperature less than 90 degrees once per four hours, and RA B.2 to restore one control room area ventilation air conditioning subsystem to operable status within 72 hours.<br /><br /> The cause of the event was a shorted wire on liquid line solenoid valve 0RG053A that caused the solenoid valve to close, resulting in the compressor shutting down on low suction pressure. The corrective action was to repair the wiring problem and return the compressor to service.
3742014001 | LaSalle 2 | 08/05/2014 | 10/03/2014 | ML14276A26 | <strong>Reactor Scram Due to Main Steam Isolation Valve Stem-Disk Separation</strong><br /><i>Abstract:&nbsp;</i>On August 5, 2014, at approximately 1734 hours CDT, Unit 2 automatically scrammed from 100% power on high neutron flux, followed by a Group I containment isolation. Following the Group I isolation, the control room operators noted that the position indication for valve 2B21-F022C, the inboard 2C Main Steam Isolation Valve (MSIV), showed dual indication rather than full closed. <br /><br /> Troubleshooting of the 2C MSIV determined that the valve stem disk had separated from the stem, which allowed the main disk to drop into the main steam flow path. The resulting reactor pressure transient added positive reactivity, which caused the high neutron flux scram. Increased steam flow in the other three main steam lines resulted in a nearly simultaneous high main steam line flow Group I containment isolation. <br /><br /> The cause of the stem-disk separation on the 2C MSIV was fretting wear attributable to marginal design. The root cause of the event was a legacy decision made in 2008 deferring installation of a manufacturer upgrade that would have prevented the failure. Corrective actions include installing the upgrade on all MSIVs on both units, and reviewing previous deferral decisions made using the same decision-making process.
3822014001 | Waterford 3 | 05/08/2013 | 05/07/2015 | ML15128A50 | <strong>Room Cooler Breaker Inoperability Causes Past Inoperability of Containment Spray System Train</strong><br /><i>Abstract:&nbsp;</i>On May 8, 2013 at 19:53, a safety-related circuit breaker failed when Operations personnel attempted to start Shutdown Cooling Heat Exchanger Room B air handling unit. In accordance with Operations administrative procedure for Technical Specification and Technical Requirements Compliance, Operations personnel entered the applicable Technical Specification Limiting Condition for Operation for Containment Spray (CS) train B. A replacement breaker was installed and a successful start of the air handling unit was performed. CS Train B was declared operable at 17:30 on May 9, 2013.<br /><br /> An evaluation of the failure determined that the air handling unit had been effectively rendered inoperable since installation of the circuit breaker on April 18, 2013. Containment Spray train B was inoperable from 03:09 on April 17, 2013, when the train was declared inoperable to perform preventative maintenance until 17:30 on May 9, 2013, a total of 22.6 days. This time period exceeds the Technical Specification allowed outage time of 7 days. Technical Specification 3.6.2.1 was not complied with, which requires that with one CS system [train] inoperable, restore the system [train] to operable status within 7 days or be in at least Hot Standby within the next six hours. During this time frame CS 'A' was inoperable for 6.65 hours. Since both trains of Containment Spray were inoperable this is considered a Safety System functional failure due to the system being unable to mitigate the consequences of an accident.
3822014002 | Waterford 3 | 03/01/2014 | 04/29/2014 | ML14120A02 | <strong>Inadequate Tightening of Starting Air Filter Housing results in Inoperable Train A Emergency Diesel Generator</strong><br /><i>Abstract:&nbsp;</i>During an operator tour of the train A Emergency Diesel Generator (EDG) room on March 1, 2014 at approximately 12:39, it was discovered that the filter housing cover on the EDG A Starting Air Filter had unfastened from its base and was lying on the floor. The last successful start of the EDG A that demonstrated its capability to meet its safety function was on February 27, 2014 at 11:33 and it is postulated that the cover became unfastened during that run. Therefore, EDG was potentially inoperable for 2 days as a result of this condition. Since the condition was unknown at the time, the Technical Specifications required test of EDG B was not performed within 8 hours and the requirement to demonstrate the operability of the remaining A.C. circuits at least once per 8 hours or to be in Hot Shutdown within the next 6 hours was not performed.<br /><br /> The cause was insufficient tightening of the filter housing cover during maintenance on April 8, 2013. The insufficient tightening had not been preventing the EDG A's ability to start within the required times prior to its becoming unfastened. EDG A was returned to OPERABLE condition by refastening the filter housing cover to its base. The other filter housings on EDG A and EDG B were verified to be properly fastened. An evaluation is being conducted to determine if a torque requirement is necessary for the filter housing covers.
3822014003 | Waterford 3 | 08/18/2014 | 10/17/2014 | ML14290A60 | <strong>Unexpected Loss of Wet Cooling Tower fan results in both trains of Ultimate Heat Sink Inoperable.</strong><br /><i>Abstract:&nbsp;</i>During a planned system outage of train B Component Cooling Water (CCW), which rendered train B Ultimate Heat Sink (UHS) inoperable, there was an unexpected trip of train A Auxiliary Component Cooling Water (ACCW) Wet Cooling Tower (WCT) fan, which rendered the train A UHS also inoperable. This resulted in both trains of the UHS system inoperable for approximately 83 minutes. <br /><br /> The ACCW WCT Fan 6A tripped at approximately 0853, rendering the redundant train A UHS inoperable, causing entry into 1 hour TS LCO 3.7.4 ACTION (b), which requires restoring at least one UHS train to OPERABLE status within 1 hour or be in at least HOT STANDBY within the next 6 hours and COLD SHUTDOWN within the following 30 hours. Then at approximately 0948 the WCT Fan 6A electric motor thermal overload relays were reset, the fan restarted, and operated properly. At 1016, CCW train B had been restored from the planned maintenance and was declared operable, exiting TS LCO 3.7.4 ACTION (b). <br /><br /> The direct cause to the WCT fan 6A trip was due to localized heating at the motor starter T-lead connection on the thermal overload. Technicians found the lug was tight (galled) but the motor T-lead showed looseness when moved. The lug was replaced. The cause was determined to be the procedure contained insufficient detail on how to verify successful implementation for tightening a mechanical lug, and corrective action is planned to add the appropriate detail.
3822014004 | Waterford 3 | 10/22/2014 | 06/03/2015 | ML15154B39 | <strong>Emergency Diesel Generators Rendered Inoperable By Potential Water Intrusion Into Diesel Fuel Oil Feed Tanks</strong><br /><i>Abstract:&nbsp;</i>During a walkdown of the Emergency Diesel Generator Feed Tank A and B vent lines on October 22, 2014, an NRC Component Design Basis Inspection inspector identified corrosion on the Emergency Diesel Generator Feed Tank A and B vent lines where the vent lines pass through the roof. A visual inspection was performed and revealed that the corrosion had created through wall holes that could allow water into both the train A and B Emergency Diesel Generator Feed Tanks.<br /><br /> Follow up analysis has determined that some rainfall amount less than the postulated Probable Maximum Precipitation event could have resulted in water intrusion into the Emergency Diesel Generator A and B Feed Tanks that exceeds the 0.1 percent water content allowed by the vendor technical manual. This could have potentially affected the operability of both the A and B Train Emergency Diesel Generator Feed Tanks and subsequently both trains of the Emergency Diesel Generators. It is unknown how long this corrosion has existed. Compensatory measures were put in place to prevent water ingress should a large rainfall event occur.<br /><br /> This condition is reportable under the following criteria: 10 CFR 50.73(a)(2)(i)(B), 10 CFR 50.73(a)(2)(v)(D), and 10 CFR 50.73(a)(vii).
3872014001 | Susquehanna 1, Susquehanna 2 | 02/06/2014 | 04/07/2014 | ML14097A48 | <strong>Operation of the Reactor Pressure Vessel at Less Than 0 psig Resulting in a Violation of Technical Specification 3.4.10, Reactor Coolant System Pressure and Temperature Limits</strong><br /><i>Abstract:&nbsp;</i>On February 6, 2014, Susquehanna Steam Electric Station (SSES) discovered a previously unrecognized failure to enter Technical Specification (TS) LCO 3.4.10 when on 27 occasions during the past 3 years, the Reactor Pressure Vessel (RPV) pressure dropped below 0 psig during past reactor startups and shutdowns. At the time of discovery, both units were operating in Mode 1 at 100 percent thermal power. All systems were performing as designed. This LER is being submitted to the NRC in accordance with 10 CFR 50.73(a)(2)(i)(B) for a condition prohibited by TS 3.4.10 since the condition existed for a time longer than permitted by the TS.<br /><br /> The apparent cause of the failure to enter the LCO was the condition was procedurally allowed and aligned with training provided to the licensed operators. As a result, operating with the RPV being below 0 psig was not recognized as a condition prohibited by TS until the receipt and evaluation of INPO OE 309129. There were no actual or potential consequences to the health and safety of the public as a result of this event. The 27 instances did not challenge any design or safety limit. Nuclear safety was not compromised because the negative (vacuum) internal pressures identified do not invalidate any analyses for the SSES RPVs.<br /><br /> Completed Action: 1) The Unit 2 operating procedure for reactor startup and heatup has been revised to proceduralize plant start-up with the MSIVs closed and then opening them between 10 and 40 psig RPV pressure. Startup in this manner maintains RPV pressure above 0 psig at all times and minimizes level transients caused by pressure changes when opening the MSIVs, and 2) Operators were trained on the revised reactor startup and heatup procedure.<br /><br /> Planned Action: Prior to startup from the 2014 Unit 1 refueling outage, the Unit 1 operating procedure for reactor startup and heatup will be revised to be consistent with the changes that were made to the corresponding Unit 2 procedure.
3872014002 | Susquehanna 1, Susquehanna 2 | 02/12/2014 | 04/09/2014 | ML14100A00 | <strong>Secondary Containment Door Found Ajar</strong><br /><i>Abstract:&nbsp;</i>On February, 12, 2014 at approximately 0711 hours, while performing shift rounds, a security officer found Door-612 wedged open with the Secondary Containment Boundary Door sign between the door and frame (hinge side). Door-612 provides access from the HVAC room to the Central Railroad Bay. The security officer immediately contacted the Central Alarm Station (CAS), and CAS contacted the Control Room. Prior to departing the Door-612 area, the security officer closed the door and re-positioned the sign. The action of closing the door restored the required configuration and secondary containment integrity. Operations performed a status walk down to ensure no other secondary containment door was in this condition. Secondary Containment differential pressure was maintained throughout the period that Door-612 was open.<br /><br /> In accordance with 10CFR50.72(b)(3)(v)(C), an 8-hour ENS notification (# 49821) was made to the NRC for an event or condition that at the time of discovery, could have prevented the fulfillment of the safety function.<br /><br /> The most probable causes were: 1) Door-612 was not sufficiently challenged and 2) the latching device is not sufficient to ensure proper closure of the door.<br /><br /> Key corrective actions include: 1) Issuing a Site Communication to define expectations to site personnel on requirements when closing Secondary Containment doors, 2) Replacing Door-612, 613, 721, and 718 to include a three-point latching device, and 3) Until new latch design is installed, require Operations to inspect Door-612 every 2 hours when secondary containment is aligned in a refuel floor hatch removal configuration.<br /><br /> There were no actual consequences to the health and safety of the public as a result of this event.
3872014003 | Susquehanna 1, Susquehanna 2 | 03/04/2014 | 05/01/2014 | ML14121A55 | <strong>Loss of Secondary Containment During Technical Specification SR 3.6.4.1.5 Drawdown Testing</strong><br /><i>Abstract:&nbsp;</i>On March 4, 2014 at 0025 EST, during Technical Specification (TS) surveillance SR 3.6.4.1.5, drawdown testing of Secondary Containment failed to meet acceptance criteria of SR 3.6.4.1.5 due to maximum flow rate exceeding the allowable value. The testing was performed with the Unit 1 Railroad Bay aligned as Zone III to verify integrity while aligned in a previously untested alignment. The untested alignment was with the Unit 2 Reactor Building HVAC shutdown and a controlled Zone II Secondary Containment breech established. Actual in-leakage while in the untested alignment was 3301 cubic feet per minute (cfm), which is in excess of the TS SR 3.6.4.1.5 acceptance criteria of less than or equal to 2885 cfm. This event was determined to be reportable as an 8 hour ENS (# 49867) in accordance with 10 CFR 50.72(b)(3)(v)(c) for a loss of safety function. There is no redundant Susquehanna Secondary Containment system. This LER is being submitted in accordance with 10 CFR 50.73(a)(2)(v)(C), for an event or condition that at the time of discovery, could have prevented the fulfillment of the safety function of Secondary Containment to control the release of radioactive material.<br /><br /> The direct cause of this event was due to air in-leakage into Secondary Containment past Door-101 and the Truck Bay Access Hatch Cover 2H24. The apparent cause was due to inadequate margin for the untested configuration with Unit 2 Reactor Building HVAC shutdown and a controlled Zone II Secondary Containment breach established.<br /><br /> Completed Actions: 1) Secondary Containment ventilation was realigned to a known previously successfully tested alignment, 2) Installed shielding on the Core Spray piping adjacent to the Control Structure to gain margin in SSES's analysis for Control Room Operator dose post-accident, and 3) Revised the Unit 1 and Unit 2 Tech Spec Bases 3.6.4.1 to increase SGTS Exhaust Flow Rate. Planned Actions: 1) Repair/replace the bottom seal plate and the top and bottom seals on Door-101, 2) Caulk joints for 2H24 Hatch, and 3) Re-perform Secondary Containment drawdown tests per SE-170-011 for Zone I / Ill aligned in the untested configuration.<br /><br /> There were no actual consequences to the health and safety of the public as a result of this event.
3872014005 | Susquehanna 1, Susquehanna 2 | 04/17/2014 | 06/12/2014 | ML14163A25 | <strong>Loss of Secondary Containment Due to Differential Pressure Not Meeting Technical Specification 3.6.4.1</strong><br /><i>Abstract:&nbsp;</i>On April 17, 2014 at 0335, secondary containment Zone Ill differential pressure went to 0.15 inch of vacuum water gauge after the planned shutdown of the Unit 1 portion of Zone Ill ventilation. As a result, Zone Ill differential pressure did not meet the criteria (vacuum 0.25 inch of vacuum water gauge) of Surveillance Requirement (SR) 3.6.4.1.1 and Limiting Condition for Operation (LCO) 3.6.4.1 was entered for both Unit 1 and Unit 2. Zone II ventilation remained in service and stable during the events. Zone I ventilation remained isolated with secondary containment relaxed for a refueling outage on Unit 1. Unit 1 Zone Ill ventilation was subsequently restored, Zone Ill differential pressure was restored, and LCO 3.6.4.1 was exited at 0420. <br /><br /> The direct cause of the event was misalignment between the upper and lower set of damper blades on a manual outside air damper causing an excessive opening in the upper set of blades. This prevented sufficient restriction of supply air flow into Zone III secondary containment during the change in the ventilation line up. The apparent cause of the damper misalignment was an inadequate preventative maintenance frequency. Corrective actions include cleaning, adjusting, and lubricating the affected damper and increasing the frequency of its preventative maintenance activity. <br /><br /> There were no actual or potential consequences to the health and safety of the public as a result of the event.
3872014006 | Susquehanna 1, Susquehanna 2 | 04/16/2014 | 06/12/2014 | ML14163A24 | <strong>Implementation of Enforcement Guidance Memorandum (EGM) 11-003, Revision 2</strong><br /><i>Abstract:&nbsp;</i>The condition reported by this LER was an expected condition, which was the result of planned activities in support of a routine refueling outage. As described in the LER, the U. S. Nuclear Regulatory Commission (NRC) provided enforcement guidance, applicable to boiling water reactor licensees, that allows the reported condition. Although this allowance is provided by the NRC's enforcement guidance, the planned activities are still considered reportable in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by Technical Specifications (TS). <br /><br /> Between 4/16/2014 and 5/23/2014, Susquehanna Steam Electric Station (SSES) performed Operations with the Potential for Draining the Reactor Vessel (OPDRV) activities on Unit 1 while in Mode 5 without an operable secondary containment, as expected and allowed by the enforcement guidance. Although NRC Enforcement Guidance Memorandum (EGM) 11-003, Revision 2 allows the implementation of interim actions as an alternative to full compliance, this condition is still considered a condition prohibited by TS 3.6.4.1. The OPDRV activities were planned activities that were completed under the guidance of plant procedures and are considered to have low safety significance based on interim actions taken. Since these actions were deliberate, no cause determination was necessary. A license amendment request will be submitted following NRC approval of the Technical Specifications Task Force (TSTF) traveler associated with generic resolution of this issue.
3872014007 | Susquehanna 1, Susquehanna 2 | 04/24/2014 | 06/12/2014 | ML14163A31 | <strong>Loss of Secondary Containment Pressure During RPS Transfer</strong><br /><i>Abstract:&nbsp;</i>On April 24, 2014 at 0230 hours, secondary Containment Zone III differential pressure lowered to less than the required 0.25 inches vacuum water gauge (WG) when restoring Unit 1 Zone III ventilation during a routine swap of Reactor Protection System (RPS) power supplies, due to a trip of the Unit 1 Zone III supply fan. Zone I ventilation was isolated with secondary containment relaxed for a refuel outage on Unit 1. Zone II ventilation remained in service and stable. Zone III differential pressure recovered to Surveillance Requirement (SR) 3.6.4.1.1 requirements of 0.25 inches WG at 0243 hours and was verified to be stable. Limiting Condition for Operation (LCO) 3.6.4.1 was entered at 0230 hours and exited at 0313 hours. Technical Specification secondary Containment operability requires a negative pressure of at least 0.25 inches WG for all three Reactor Building Ventilation Zones when secondary containment is required. <br /><br /> In accordance with 10CFR50.72(b)(3)(v)(C), an 8-hour ENS notification (# 50055) was made to the NRC for an event or condition that at the time of discovery, could have prevented the fulfillment of the safety function. <br /><br /> The apparent cause was a deficiency with procedure steps that did not account for actual/designed system response. <br /><br /> Key corrective actions taken included revising applicable Unit 1 and Unit 2 procedures to enhance restoration of ventilation during RPS transfers. A key planned corrective action includes a procedure review to ensure all steps are correct and will not result in unexpected loss of secondary containment and/or other unexpected response. <br /><br /> There were no actual or potential consequences to the health and safety of the public as a result of this event.
3872014008 | Susquehanna 1, Susquehanna 2 | 06/12/2014 | 08/11/2014 | ML14223A73 | <strong>Loss of Both Trains of Control Structure Chilled Water due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On June 12, 2014 at 1444 hours, while restoring from a quarterly surveillance test, a Susquehanna Steam Electric Station (SSES) Plant Control Operator (PCO) manipulated a control switch for an OPERABLE Control Structure Chilled Water (CSCW) pump to the off position, which rendered a division of CSCW inoperable. The redundant division of CSCW was previously taken out of service to perform the surveillance test. Upon rendering both trains of CSCW inoperable, Limiting Condition for Operation (LCO) 3.0.3, was entered at 1444 hours, and then exited at 1446 hours when the PCO recognized the incorrect switch had been manipulated and returned Division 1 of CSCW to service. The SSES Technical Specifications for Control Structure (CS) HVAC and Control Room Emergency Outside Air Supply (CREOAS) require both divisions of CSCW to be OPERABLE during normal plant operations. In accordance with 10 CFR 50.72(b)(3)(v)(D), an eight-hour ENS notification (# 50198) was made to the NRC for an event or condition that at the time of discovery, could have prevented the fulfillment of a safety function. The apparent cause was less than adequate use of Human Performance error prevention tools. The immediate corrective action taken was to issue operations directive to require a peer check by another licensed reactor operator for all manipulations performed in the control room. A key planned corrective action is to revise the surveillance procedure used during this event to require concurrent verification for all irreversible steps. There were no actual or potential consequences to the health and safety of the public as a result of this event.
3872014009 | Susquehanna 1, Susquehanna 2 | 06/13/2014 | 08/11/2014 | ML14223A75 | <strong>Loss of Both Trains of Control Structure Chilled Water During Application of Clearance Order</strong><br /><i>Abstract:&nbsp;</i>On June 13, 2014 at 0452 hours, while applying a Clearance Order (CO) to repair an Instrument Air valve, Susquehanna Steam Electric Station (SSES) operators opened the circuit breaker supplying power to the A Control Structure (CS) Chiller Condenser Circulating Pump, tripping Division 1 of CS Chilled Water (CSCW). The breaker supplying power to Division 2 was already open, rendering both Divisions of CSCW inoperable which prompted entry into Limiting Conditions for Operation (LCOs) 3.0.3, 3.7.3, and 3.7.4 at 0452 hours. LCO 3.0.3 was exited at 0503 hours when SSES operators closed the breaker and returned Division 1 of CSCW to service. LCOs 3.7.3 and 3.7.4 were exited at 0507 hours when SSES operators returned Division 2 of CSCW to service. The SSES Technical Specifications for CS HVAC and Control Room Emergency Outside Air Supply (CREOAS) require both Divisions of CSCW to be OPERABLE during normal plant operations. In accordance with 10 CFR 50.72(b)(3)(v)(D), an eight-hour ENS notification (# 50200) was made to the NRC for an event or condition that at the time of discovery, could have prevented the fulfillment of a safety function. The apparent cause was that the CO writer did not engage engineering for a final peer check of the impacts and effects of the CO prior to application of the CO. Key planned corrective actions include revising the CO procedure to require system engineering review prior to establishing a CO when engineering has evaluated the impacts and effects of the CO; and labelling the breakers that control the CS Chiller Condenser Circulating pumps (A and B) to indicate that if both breakers are open a loss of both trains of CSCW will occur. There were no actual or potential consequences to the health and safety of the public as a result of this event.
3872014011 | Susquehanna 1 | 12/13/2014 | 02/11/2015 | ML15042A46 | <strong>Degraded Condition due to Reactor Coolant Pressure Boundary Leakage Caused by an Inadequate Weld</strong><br /><i>Abstract:&nbsp;</i>On December 13, 2014, Unit 1 entered a planned outage due to excessive unidentified drywell leakage. During a walk down performed to identify sources of drywell leakage, a leak was reported on the Unit 1 "B" Reactor Recirculation (RXR) Pump Lower Seal Cavity Vent piping. The leak was identified at the inboard pipe-to-union weld and required a weld repair prior to returning Unit 1 to service. The leaking weld was attached to the vendor supplied replacement pump seal chamber. <br /><br /> This event was reported under 10 CFR 50.72(b)(3)(ii)(A) and per the guidance of NUREG 1022, Revision 3, Section 3.2.4 as a degraded condition (EN 50686). <br /><br /> The most likely cause of the weld crack was determined to stem from a poor weld provided by the manufacturer of the pump component. The apparent cause for the vendor weld failure was from a lack of fusion between weld passes. A weld repair was performed on the cracked weld. Pipe-to-union welds on replacement shaft connections currently installed on the 1B and 2A RXR pumps will be cut out and rewelded in upcoming refueling outages. Future shaft replacements for the 2B and 1A RXR pumps utilize a vendor upgraded design that has eliminated the subject weld. <br /><br /> There were no actual consequences to the health and safety of the public as a result of this event.
3882014001 | Susquehanna 2, Susquehanna 1 | 11/05/2014 | 12/31/2014 | ML15005A38 | <strong>Both Doors of a Secondary Containment Personnel Airlock Momentarily Open due to a Personnel Error Resulting in Entry into Secondary Containment Technical Specification Limiting Condition for Operation</strong><br /><i>Abstract:&nbsp;</i>On November 5, 2014 at 1115 hours, Secondary Containment Zone 3 (Unit 1 & 2 Reactor Building) was unintentionally cross tied to Secondary Containment Zone 2 (Unit 2 Reactor Building) for several seconds during passage of personnel through a personnel airlock. Secondary Containment Zone 2 and Zone 3 ventilation remained in service and stable. Limiting Condition for Operation (LCO) 3.6.4.1 was entered and exited based on the prohibited crosstie of Secondary Containment Zones. This event was reported under 10 CFR 50.72(b)(3)(v)(C) as a loss of a safety function. There is no redundant Susquehanna Secondary Containment System.<br /><br /> The cause of the event was a human performance error in that a self-check was not performed prior to opening the airlock door. The individual was coached on the importance of self-check for verifying conditions are met prior to passage through a Secondary Containment airlock door. A communication to all station personnel will be distributed reinforcing the significance of secondary containment airlocks, the conditions required for passage through an airlock, and how to verify these conditions.<br /><br /> There were no actual consequences to the health and safety of the public as a result of this event.
3892014001 | St. Lucie 2 | 07/25/2014 | 01/30/2015 | ML15043A15 | <strong>Unit Shutdown due to Leak on Safety Injection Tank Vent Valve Piping</strong><br /><i>Abstract:&nbsp;</i>On July 25, 2014 with St. Lucie Unit 2 in Mode 1 at 100% power, a leak was confirmed on a one inch pipe between a safety injection tank (SIT) and a discharge header vent valve. In accordance with Technical Specifications (TS) and plant procedures, operators subsequently shut down the unit to repair the leak. The shutdown was uncomplicated and all plant safety systems functioned as designed. The leaking vent line and valve assembly were replaced and returned to service on July 28, 2014. <br /><br /> Engineering evaluation identified the direct cause of the pipe leak as through-wall cracking from high cycle, low stress fatigue. This condition is reportable in accordance with the following requirements: 1) 10 CFR 50.73(a)(2)(ii)(A), 2) 10 CFR 50.73(a)(2)(i)A, 3) 10 CFR 50.73(a)(2)(i)B, 4) 10 CFR 50.73(a)(2)(v)(D), 5) 10CFR50.73(a)(2)(ii)(B) and 6) 10 CFR 50.73(a)(2)(vii)(B). <br /><br /> This supplement revises the event description, analysis of event and safety significance and adds additional reporting criteria. This condition was determined not to be a significant impact on the health and safety of the public.
3892014002 | St. Lucie 2 | 11/12/2014 | 04/03/2015 | ML15103A48 | <strong>Unit 2 Shutdown due to Spurious Closure of Main Feed Isolation Valve (MFIV)</strong><br /><i>Abstract:&nbsp;</i>On November 12, 2014 Unit 2 was in Mode 1 at 100 percent power when the 2B steam generator main feedwater isolation valve (MFIV) HCV-09-2B spuriously stroked closed. This resulted in a manual reactor trip of Unit 2 due to rapidly lowering steam generator water level. The reactor trip was normal and uncomplicated. All safety related systems functioned as designed. There were no unexpected automatic safety system actuations as a result of the trip.<br /><br /> A root cause evaluation (RCE) determined the spurious closure of the MFIV was a result of an insufficient preventive maintenance (PM) strategy to detect and mitigate environmental conditions that would affect the MFIV HCV-09-2B relay box. Corrective actions included replacement of the relays in the MFIV relay boxes and moving or eliminating the relay components by modification. This condition is reportable in accordance with the following requirements: 1) 10 CFR 50.73(a)(2)(i)(A)and 2) 10 CFR 50.73(a)(2)(iv)(A). This supplement revises the cause, corrective actions and operating experience (OE) for this event. This event was determined to have minimal safety significance and no impact on the health and safety of the public.
3902014001 | Watts Bar 1 | 01/24/2014 | 03/20/2014 | ML14080A07 | <strong>Loss of Air to Train A Motor Driven Auxiliary Feedwater Pump Level Control Valves</strong><br /><i>Abstract:&nbsp;</i>On January 24, 2014, 1525 Eastern Standard Time (EST) with Watts Bar Nuclear (WBN) Unit 1 at 100 percent rated thermal power, two Train A Motor Driven Auxiliary Feedwater (AFW) Pump Level Control Valves (LCV) failed open due to loss of air. The valves 1-LCV-3-156-A and 1-LCV-3-164-A failed open following removal of the backup nitrogen control system. Upon investigation two essential air isolation valves 0-ISV-32-371 and 0-ISV-32-373, which are normally open to supply essential air from the Auxiliary Compressed Air System (ACAS) to motor driven AFW LCVs, were found closed.<br /><br /> Valves 0-ISV-32-371 and 0-ISV-32-373 were immediately opened which restored essential air to 1-LCV-3-156-A and 1-LCV-3-164-A. Technical Specification (TS) Limiting Condition for Operation (LCO) 3.7.5 was entered at 1525 on January 24, 2014 when Train A Motor Driven AFW was declared inoperable. Upon restoration of air to LCVs, TS LCO 3.7.5 was exited at 1612 on January, 24, 2014.<br /><br /> The cause of this event was that valves 0-ISV-32-371 and 0-ISV-32-373 were closed as part of work order activities and Operations personnel failed to restore the valves to their normal open position.
3902014002 | Watts Bar 1 | 02/11/2014 | 04/11/2014 | ML14101A14 | <strong>Non-conservative Operator Manual Actions Identified in Appendix R Analysis</strong><br /><i>Abstract:&nbsp;</i>On February 11, 2014, Watts Bar Nuclear Plant (WBN) engineering and operations personnel discovered that nonconservative operator manual action times were credited in Appendix R analyses. Preliminary Westinghouse transient analysis calculations of WBN Unit 1 fire protection features revealed that there was less time than previously credited to perform certain operator manual actions to prevent pressurizer overfill during certain Appendix R fire scenarios. The Westinghouse analysis assumes the time required to isolate the normal charging path, secure the second charging pump and isolate the emergency charging path is approximately 12.5 minutes. Watts Bar Unit 1 procedures are nonconservative in that they allow these actions to be completed in 18 minutes.<br /><br /> The Tennessee Valley Authority (TVA) has verified that potentially impacted Appendix R equipment remains functional; however, a compensatory fire watch has been established for the affected areas until plant modifications are completed. This event was caused by an error in a fire protection program design calculation prior to commercial operation of Unit 1. Modifications to address this issue will be completed during the Fall 2015 refueling outage.
3902014003 | Watts Bar 1 | 07/13/2014 | 09/11/2014 | ML14254A07 | <strong>Manual Reactor Trip due to Automatic Feedwater Heater Isolation</strong><br /><i>Abstract:&nbsp;</i>On July 13, 2014 at 1937 [EDT], Watts Bar Nuclear Plant operators manually tripped the Unit 1 reactor due to automatic isolation of all low pressure feedwater heaters. Concurrent with the reactor trip, the Auxiliary Feedwater system actuated as designed.<br /><br /> All Control and Shutdown rods fully inserted. All safety systems responded as designed and the unit was stabilized in Mode 3, with decay heat removal via Auxiliary Feedwater, steam dumps and the main condenser, with the station in a normal shutdown electrical alignment.<br /><br /> The need to manually trip the reactor was determined to be the result of two separate age related failures associated with the control scheme of the #7 Heater Drain Tank (HDT). The root cause of these failures was that replacement preventative maintenance (PM) tasks did not exist for these components. The components in question were replaced and corrective actions have been developed to generate replacement PMs for both components. In addition, replacement PMs will be developed for similar critical components of the Secondary Systems based on EPRI Guidance
3952014001 | Summer 1 | 04/14/2014 | 06/12/2014 | ML14167A37 | <strong>Component Cooling System Emergency Makeup "B" Valve Failed to Stroke Open Rendering Train of Component Cooling Inoperable</strong><br /><i>Abstract:&nbsp;</i>On April 14, 2014, while performing a surveillance test, the normally closed Component Cooling (CC) System emergency makeup valve (XVG09627B-CC) failed to stroke open. This surveillance test is performed each refueling outage and was last successfully tested during a mid cycle outage on March 30, 2013. The emergency makeup supply to the CC System is provided by the Service Water (SW) System. The SW System functions as a source of emergency makeup in the event of a complete loss of the normal makeup capability provided by the Demineralized Water System or if leakage exceeds the normal makeup capacity. The safety related function of XVG09627B-CC is to open to allow SW from the B Train to provide makeup to the B train CC system. By failing to open, this valve was unable to perform its design function without additional operator action. Since the valve did not stroke open on April 14, 2014, the station has concluded the valve may not have operated if required during the remaining operating cycle after the successful test on March 30, 2013. While XVG09627B-CC was unavailable, it was discovered that XVG09627A-CC was also inoperable. A PRA risk evaluation determined the event of both valves being inoperable is of low safety significance. The cause of this event is believed to be low valve manipulation frequency, added frictional forces and possible spring degradation. XVG09627B-CC has been rebuilt with new closure and trip springs and new packing that has a lower friction resistance. The valve supports were adjusted to enhance the alignment of the operator and the pressure regulator closing force was reduced. This report is submitted in accordance with 10CFR50.73(a)(2)(i)(B) and 10CFR50.73(a)(2)(v)(D).
3952014002 | Summer 1 | 04/18/2014 | 06/16/2014 | ML14169A03 | <strong>Reactor Vessel Head Penetration Weld Indications Attributed to Primary Water Stress Corrosion Cracking</strong><br /><i>Abstract:&nbsp;</i>On April 18, 2014, V.C. Summer Nuclear Station (VCSNS) Unit I identified three reactor vessel head (RVH) penetrations (9, 43, and 51) that did not meet the requirements of 10 CFR 50.55a(g)(6)(ii)(D) and American Society of Mechanical Engineers (ASME) Section XI Code Case N-729-1. On April 26, 2014, the RVH penetration inspections were finalized and two additional penetrations (15 and 22) were identified for repair. The station was in a refueling outage (RF21) and the plant was defueled. The indications were not through wall as indicated by volumetric and bare metal visuals. The inspection results are reportable in accordance with 10 CFR 50.73(a)(2)(ii)(A).<br /><br /> The flaws were repaired using the embedded flaw repair process in accordance with NRC approved WCAP-15987-P, Revision 2-P-A and Relief Request RR-4-05. The apparent cause of the flaws is attributed to primary water stress corrosion cracking.
3952014003 | Summer 1 | 04/26/2014 | 06/24/2014 | ML14177A53 | <strong>Component Cooling System Emergency Makeup "A" Valve Failed to Stroke Open Rendering Train of Component Cooling Inoperable</strong><br /><i>Abstract:&nbsp;</i>On April 26, 2014, while performing a surveillance test, the normally closed Component Cooling (CC) System emergency makeup valve (XVG09627A-CC) failed to stroke open. During the second attempt XVG09627A-CC opened in 11.29 seconds, which exceeded the maximum allowed stroke time of ten (10) seconds. This surveillance test is performed each refueling outage and was last successfully tested during the fall 2012 refueling outage (RF20). The emergency makeup supply to the CC System is provided by the Service Water (SW) System. The SW System functions as a source of emergency makeup in the event of a complete loss of the normal makeup capability provided by the Demineralized Water System or if leakage exceeds the normal makeup capacity. The safety related function of XVG09627A-CC is to open to allow SW from the "A" Train to provide makeup to the "A" train CC system. By failing to open, this valve was unable to perform its design function without additional operator action. Since the valve did not stroke open on April 26, 2014, the station has concluded the valve may not have operated if required during the operating cycle. While XVG09627A-CC was unavailable, it was determined that XVG09627B-CC was also inoperable. A PRA risk evaluation determined the event of both valves being inoperable is of low safety significance. The cause of this event is believed to be low valve manipulation frequency, added frictional forces, and possible spring degradation. XVG09627A-CC has been rebuilt with new closure and trip springs and new packing that has a lower friction resistance. The pressure regulator closing force was also reduced. This report is submitted in accordance with 10CFR50.73(a)(2)(i)(B).
3952014004 | Summer 1 | 07/22/2014 | 09/19/2014 | ML14265A41 | <strong>Condensate System Bypass Valve Failure and a Procedure Deficiency Cause Loss of Feedwater and Automatic Reactor Trip</strong><br /><i>Abstract:&nbsp;</i>On 7/22/2014 at 0414, VC Summer Nuclear Station automatically tripped due to low Steam Generator water level in "C" Steam Generator. The trip was the result of the Condensate Bypass Valve, XVB09210-WI, failing to open as required while removing the Condensate Demineralization (WI) System from service during plant startup. With flow removed from the WI system and bypass valve XVB09210-WI closed, condensate flow to the Deaerator Storage Tank (DAST) was isolated. All operating main Feedwater pumps tripped on DAST Low-Low level setpoint. The water level in the Steam Generators decreased and resulted in a reactor trip.<br /><br /> The cause of this event was failure of XVB09210-WI to stroke open due to a failed solenoid actuator and a procedure deficiency in manipulating the WI System. For corrective actions, the solenoid actuator for XVB09210-WI was replaced and the system operating procedure for the WI system has been revised to direct the operator to verify that XVB09210-WI is has actuated open before reducing the flow through the Condensate Polishing Demineralizers.<br /><br /> This report is submitted in accordance with 10CFR50.73(a)(2)(iv)(A).
3972014001 | Columbia | 01/09/2014 | 05/29/2014 | ML14161A14 | <strong>Secondary Containment Pressure Exceeded</strong><br /><i>Abstract:&nbsp;</i>On January 9, 2014 at 1743 and 1834 hours secondary containment was declared inoperable during repositioning of the dampers. These two events had durations of 3 and 2 minutes respectively. Control Room operators took manual control of the Reactor Building Exhaust Air flow system to restore secondary containment in the first event, and the controller restored pressure automatically in the second. <br /><br /> On January 15, 2014 at 0907 hours and February 17, 2014 at 0304 hours secondary containment was declared inoperable during repositioning of the dampers and during high winds respectively. These two events had durations of 6 and 2 minutes respectively. The system controller automatically restored secondary containment differential pressure in both events. <br /><br /> In each of these events secondary containment vacuum was not maintained greater than or equal to 0.25 inches of vacuum water gauge as required by Technical Specification 3.6.4.1, due to less than optimal control system tuning for the system. Corrective actions include determining, implementing, and documenting the optimum control system tuning for the system, increasing margin by lowering differential pressure set point, and alerting operations before the Technical Specification limit for secondary containment pressure is reached.
3972014002 | Columbia | 03/11/2014 | 05/02/2014 | ML14135A04 | <strong>Unnanalyzed Condition Resulting from Direct Current (DC) Ammeter Circuits Without Overcurrent Protection</strong><br /><i>Abstract:&nbsp;</i>On March 11, 2014, with the plant operating in Mode 1 at 100 percent power, an extent of condition evaluation, resulting from a review of nuclear industry operational experience, identified areas in the plant that may be susceptible to secondary fires due to hot shorts from unfused ammeters in the Direct Current distribution system. In the postulated event, a fire in the station cable raceway, cable spreading room, or Control Room could cause a ground loop through unprotected ammeter wiring or control circuit wiring and potentially result in excessive current flow and heating to the point of causing a secondary fire. The postulated secondary fire could affect the availability of equipment needed to place the plant in a safe shutdown condition. This scenario has not been analyzed in accordance with 10 CFR 50 Appendix R commitments. Compensatory hourly fire watch measures have been put In place and will remain in place for the affected areas of the plant until analyses are completed and modifications are put in place to eliminate the concern. The condition affects 14 Class 1E DC ammeters and 2 non-Class 1E DC ammeters in 3 plant divisions. The cause of the unfused DC ammeter circuits is that the original plant design did not include overcurrent protection features to isolate fault current in the current flow path from the shunts for each direct current battery or charger to the remote ammeter circuits in the Control Room. The corrective action plant modification will provide fuses to the unprotected ammeters.
3972014003 | Columbia | 03/12/2014 | 05/12/2014 | ML14142A01 | <strong>Degraded Tornado Missile Barrier</strong><br /><i>Abstract:&nbsp;</i>On March 12, 2014, it was identified that three manhole covers (E10, E11p, and E 15) for vaults containing 4160 volt electric cables were missing the hold down bolts. The hold down bolts are required as part of the tornado missile barrier for the manhole cover for the underground electric vault. It was later determined that the hold down bolts for manhole cover E11 (Division 2 Service Water) had been identified as missing since September 6, 2013. When the bolts were identified as missing on September 6, 2013, the manhole cover and bolts were not recognized as a tornado missile barrier; because this information was not available in routinely used databases and procedures. No compensatory action was taken until March 12, 2014, when large concrete blocks were placed on top of the manholes to prevent the covers from potential removal in the event of a tornado. The degraded missile barrier is considered to have rendered the Division 2 Service Water system inoperable from September 6, 2013, to March 12, 2014. This is reportable as a condition prohibited by Technical Specifications,
3972014004 | Columbia | 08/14/2014 | 10/09/2014 | ML14296A38 | <strong>TS Surveillance 3.7.1.1 Compliance, UHS Spray Pond Level</strong><br /><i>Abstract:&nbsp;</i>On August 14, 2014 it was discovered that Columbia Generating Station's (Columbia) method of complying with Technical Specification (TS) Surveillance Requirement (SR) 3.7.1.1 for Ultimate Heat Sink (UHS) spray pond level was Inadequate. The SR requires level in each spray pond to be verified to be greater than or equal to the minimum water level whereas procedures allowed for an arithmetic average of the two ponds to be taken when a single Service Water (SW) pump is in operation which creates a differential between the pond levels. The two spray ponds that make up Columbia's UHS are connected by a siphon line to allow water to be shared between the two ponds. Columbia's original TS did not specify that a minimum water level be checked in each pond and a procedural note was added to clarify compliance with the TS SR during single SW pump operation. When Columbia upgraded the TSs in 1997 the word 'each' was introduced to the TS. Corrective actions include a TS amendment submitted to the NRC on August 22, 2014.
4002014001 | Harris | 01/18/2014 | 03/19/2014 | ML14078A32 | <strong>Manual Reactor Trip due to Indications of a Fire</strong><br /><i>Abstract:&nbsp;</i>On January 18, 2014, while operating at 75 percent power in Mode 1, Harris Nuclear Plant manually actuated the reactor protection system to trip Unit 1 due to indications of a fire in the 480V 1D2 transformer. After the reactor trip, the auxiliary feedwater system automatically initiated and provided feedwater to the steam generators. De-energizing auxiliary bus 1D caused a temporary loss of power to the 6.9kV 1A-SA safety bus, and thus the "A" auxiliary feedwater pump which was recovered when the "A" emergency diesel generator started and re-energized the 1A-SA bus. All safety systems responded as expected during this event.<br /><br /> The root cause was determined to be a combination of age and various electro-magnetic conditions which over time led to failure of the 1D2 transformer. Corrective actions include transformer replacements and additional testing. The impact on safety due to this event is a small risk increase of approximately 3E-6/yr in delta core damage frequency.
4002014002 | Harris | 06/12/2014 | 08/11/2014 | ML14223B21 | <strong>Inadequate DC Cable Protection Could Adversely Affect Safe Shutdown</strong><br /><i>Abstract:&nbsp;</i>On June 12, 2014, while operating at 100 percent power in Mode 1, Harris plant personnel determined that inadequate cable protection existed in control cables for the Turbine Emergency Oil Pump. The cables had no electrical protection devices (fuses) other than the circuit breaker. The control cables are routed through several fire areas, including the main control room, and under postulated conditions, could have created a common enclosure fire hazard situation. Compensatory measures (hourly fire watches) were implemented for affected areas of the plant to ensure continued public safety until electrical protection devices were installed.<br /><br /> The apparent cause was the historical installation of an unfused section of cable in the control circuit of the Turbine Emergency Oil Pump.
4002014003 | Harris | 10/08/2014 | 12/08/2014 | ML14342A81 | <strong>Diesel Fuel Oil Storage Building Moderate Energy Line Break Design Deficiency</strong><br /><i>Abstract:&nbsp;</i>On October 8, 2014, while operating at 100 percent power in Mode 1, Harris Nuclear Plant (HNP) personnel determined that the calculation for Diesel Fuel Oil Storage Building (DFOSB) Internal Flooding was invalid during an extent of condition evaluation. The evaluation determined that the calculation identified a single active failure to occur by the failure of a single sump pump and neglected the fact that the power source to both sump pumps was the common Motor Control Center (MCC-1-4B13). It was also determined that the internal flood event postulated for a moderate energy line break would challenge Operations' capability to respond to the event and to isolate the pipe break, prior to the flood water affecting the safety related Diesel Fuel Oil (DFO) Transfer Pumps. The DFO Transfer Pumps are used to refill the Emergency Diesel Generator (EDG) Day Tanks when the EDGs are running for an extended period of time in response to a loss of offsite power. The DFOSB fire suppression system supply was isolated promptly and a compensatory fire watch was placed at the DFOSB. Backup fire suppression is provided by staged fire extinguishers. The apparent cause was identified as a historical deficiency associated with the original design of the plant and inadequate technical rigor used to revise the calculation for DFOSB Internal Flooding in 2003.
4102014001 | Nine Mile Point 2 | 02/16/2014 | 08/14/2014 | ML14234A09 | <strong>Emergency Diesel Generator Actuation due to Loss of Offsite Power Source Line 5</strong><br /><i>Abstract:&nbsp;</i>On February 16, 2014 at 1216, Nine Mile Point Unit 2 (NMP2) was operating at 100 percent power when an automatic actuation of the Division I and III Emergency Diesel Generators (EDG) occurred due to a loss of a 345 kV bus owned by National Grid. The bus outage resulted in the loss of off-site power source (Line 5) owned by Exelon. Automatic actuation of the EDGs is reportable under 10 CFR 50.72(b)(3)(iv)(A) and 10 CFR 50.73(a)(2)(iv)(A). The cause of the loss of Line 5 is due to a faulted current transformer associated with 345kV Breaker R210 owned by National Grid, the transmission owner. The faulted transformer caused a voltage transient for both station service and offsite power loads. This resulted in the loss of: 1) the service water radiation monitor and radwaste/reactor building vent gaseous effluent monitoring systems 2) the 'C' and 'D' Reactor Water Cleanup (WCS) filter strings, and 3) spent fuel pool cooling. The voltage transient also caused Feed Water level control valve actuator controls to lock up and go to manual operation. The causal analysis identified the failure mechanism of the CT as an insulation breakdown internal to the CT. The corrective actions include purchasing spare CTs and performing follow up tests and repairs on damaged equipment. NMP1 LER 2008-001 and NMP2 LER 2012-004 are similar LERs submitted previously which involve the actuation of the EDGs due to a loss of Power Line 5.
4102014002 | Nine Mile Point 2 | 02/27/2014 | 04/28/2014 | ML14135A18 | <strong>High Pressure Core Spray System Inoperability due to Inoperable High Pressure Core Spray Diesel Generator</strong><br /><i>Abstract:&nbsp;</i>At 0330 on February 27, 2014, the High Pressure Core Spray (HPCS) System was declared inoperable. The unplanned inoperability of the HPCS System is reportable in accordance with 10 CFR 50.72(b)(3)(v)(D) and 10 CFR 50.73(a)(2)(v)(D). The event occurred during the Division III Emergency Diesel Generator (EDG), 2EGS*EG2, post maintenance testing (PMT). The EDG testing identified erratic performance of a voltage regulator that was subsequently attributed to a degraded motor operated potentiometer (MOP) and other potentiometers within the voltage regulator. With EDG inoperability due to ongoing PMT, HPCS inoperability was declared. This action prevented NMP2 from exceeding a TS LCO action statement associated with EDG inoperability. The corrective action taken was to replace the defective potentiometers. With the satisfactory completion of the EDG PMT, the HPCS and EDG were declared operable on February 27, 2014 at 1013.
4102014003 | Nine Mile Point 2 | 03/04/2014 | 05/02/2014 | ML14135A18 | <strong>Uninterruptible Power Supply Failure and Subsequent Manual Scram</strong><br /><i>Abstract:&nbsp;</i>On March 4, 2014, at approximately 0143, Nine Mile Point Unit 2 (NMP2) was manually scrammed because of rising reactor recirculation pump (RRP) seal and motor temperatures. Prior to the scram, a failure of the Uninterruptible Power Supply, 2VBB-UPS3B, to provide uninterruptible power occurred. The malfunction of the Uninterruptible Power Supply (UPS) resulted in the inboard Primary Containment cooling water isolation valves closing and a Reactor Protection System (RPS) half scram. The closing of the inboard isolation valves resulted in the loss of cooling flow to the RRP seals and motors. The cause of the UPS malfunction was a degraded subcomponent associated with the UPS. The causal analysis for this event identified that it resulted from inadequate vendor and industry guidance/operating experience associated with the maintenance of a UPS related subcomponent. Corrective actions planned or taken include replacing degraded UPS subcomponents, revising preventative maintenance strategy, and working with the vendor to identify a list of single point of vulnerability (SPV) components that can prohibit the UPS from transferring to its alternate source when needed. The reportable condition described in this LER is documented in the plant's corrective action program as CR-2014-001725.
4102014004 | Nine Mile Point 2 | 03/10/2014 | 05/07/2014 | ML14139A00 | <strong>Actuation of the Alternate Rod Insertion System and Subsequent Reactor Scram</strong><br /><i>Abstract:&nbsp;</i>On Monday March 10, 2014 at 1628 hours, Nine Mile Point Unit 2 (NMP2) experienced an actuation of the Alternate Rod Insertion (ARI) system which resulted in an automatic reactor scram from 99.2% thermal power. An inadvertent Reactor Water Low-Low Level 2 signal from transmitters 2ISC*LT8A and 2ISC*LT8B initiated the Division I ARI which resulted in a Reactor Recirculation Pump trip and a full reactor scram. The event was caused by instrument perturbation while Maintenance I&C technicians were performing minor maintenance associated with changing labels on instrument drain valves in the vicinity of trip sensitive equipment. Safety related and other important equipment functioned properly during and after the scram. This event is reportable under 10 CFR 50.73(a)(2)(iv)(A). The causal analysis identified that station personnel have not adequately internalized the risk and implemented rigorous process and behavioral barriers to mitigate the vulnerabilities associated with work on or near trip sensitive equipment. Corrective actions taken or planned include: 1) Protect the trip sensitive equipment and 2) Implementing new fleet procedures/processes for work around trip sensitive equipment. A similar event was documented in NMP2 LER 2010-001.
4102014005 | Nine Mile Point 2 | 03/12/2014 | 05/09/2014 | ML14141A53 | <strong>Secondary Containment Inoperable Due to Sustained High Winds</strong><br /><i>Abstract:&nbsp;</i>On March 12, 2014, at 1422 Nine Mile Point Unit 2, declared the secondary containment inoperable due to the secondary containment experiencing a positive differential pressure (dP) condition. This condition is reportable under 10 CFR 50.72 (b)(3)(v)(C) and 10 CFR 50.73(a)(2)(v)(C) as any event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to control the release of radioactive material. The positive dP was the result of sustained high winds from the northeast associated with Winter Storm Vulcan. The reactor building was isolated at 1630 and secondary containment declared operable at 1700 when secondary containment vacuum was restored to greater than 0.25 inches of vacuum water gauge. The causal evaluation identified that procedural guidance does not provide operators the direction to place the Standby Gas Treatment System in service and/or isolate the Reactor Building to maintain a negative pressure in the secondary containment prior to exceeding the Technical Specification (TS) limit for secondary containment dP. Corrective actions taken or planned include revising a plant procedure to provide direction to initiate the Standby Gas Treatment System and isolate the Reactor Building during high wind conditions prior to exceeding the TS limit for secondary containment dP. The event described in this LER is documented in the plant's corrective action program as CR-2014-002028. NMP2 LER 2013-005 reported similar events.
4102014006 | Nine Mile Point 2 | 03/24/2014 | 05/23/2014 | ML14161A14 | <strong>Secondary Containment Inoperability Following Auxiliary Boiler Trip</strong><br /><i>Abstract:&nbsp;</i>On March 24, 2014 at 0031, while shutting down in preparation for a refueling outage, Nine Mile Point Unit 2 (NMP2) experienced a loss of Reactor Building heating due to a trip of the Auxiliary Boiler system. While responding to lowering temperatures and rising pressure in secondary containment, secondary containment pressure degraded beyond the Technical Specification limit of 0.25 inch of vacuum water gauge. This required declaring secondary containment inoperable. Operators responded by re-aligning the Reactor Building standby gaseous treatment system (GTS) from primary containment purge mode to reactor building suction mode and isolating the normal Reactor Building ventilation system to restore operability of secondary containment. Operators also took action to restore the auxiliary boiler system in order to support restoring Reactor Building heating and ventilation to a normal lineup. The isolation of the Reactor Building ventilation system impacted the functionality of the Vent Wide Range Gaseous Monitoring System. The event causal analysis identified that management and oversight of auxiliary boiler operation and maintenance was less than adequate resulting in poor reliability due to hardware deficiencies and chemistry control which caused ground fault trips. Corrective actions planned or taken include: 1) Revising a plant procedure to ensure operating parameters are maintained within specifications during boiler operations and 2) Revising a plant procedure to require a chemistry sample be taken each shift, analyzed and reported to operations when an auxiliary boiler is in operation. A previous LER on a similar event was not identified
4102014007 | Nine Mile Point 2 | 04/02/2014 | 10/05/2015 | ML15313A02 | <strong>Secondary Containment Inoperable due to Simultaneous Opening of Airlock Doors</strong><br /><i>Abstract:&nbsp;</i>On April 2, 2014, at approximately 0123 hours, the secondary containment of the Nine Mile Point Unit 2 (NMP2) Reactor Building was breached when workers opened both inner and outer airlock doors, R261-1 and R261-2, simultaneously while passing through. The integrity of the airlock was re-established within 4 to 5 seconds when one of the doors was closed and latched. A second opening of both airlock doors occurred at 1140 that same day. Secondary containment differential pressure never exceeded the minimum Technical Specification limit of 0.25 inch of vacuum water gauge. These events are significant in that the secondary containment was momentarily breached during replacement of the Reactor Recirculation Pump "B" seal, an activity which had the potential for draining the reactor vessel (OPDRV). The causal analysis identified that workers did not use their human performance verification tools to ensure the opposing outer door of the airlock was closed prior to opening the inner door. Corrective actions taken include coaching and counseling for workers involved in the event on the importance of applying their human performance tools of self-checking and peer-checking when passing through secondary containment doors. A previous LER submitted on a similar event could not be identified.
4102014008 | Nine Mile Point 2 | 06/10/2014 | 08/08/2014 | ML14226A98 | <strong>Secondary Containment Inoperable due to Reactor Building Exhaust Fan Trip</strong><br /><i>Abstract:&nbsp;</i>Nine Mile Point Unit 2 (NMP2) secondary containment was declared inoperable on June 10, 2014 from 2032 until 2036. The event occurred while the plant was restoring the Reactor Building Ventilation System to normal line up. Exhaust Fan 2HVR-FN5A tripped following planned post maintenance testing which resulted in building differential pressure (dP) exceeding the Technical Specification (TS) limit of 0.25 inch vacuum water gauge. Secondary containment dP was restored within TS limits by starting the Standby Exhaust Fan. Both the TS Action Statement and plant procedure were exited at 2036 when secondary containment was declared operable. The cause of the exhaust fan trip was a faulty flow switch. Corrective actions taken or planned to prevent a recurrence include: 1) replaced Flow Switch 2HVR-FS12A, 2) revising the Preventative Maintenance (PM) strategy for Reactor Building ventilation supply and exhaust fan flow switches, and 3) revising a plant procedure to clarify fan start requirements. There were no previously submitted similar LERs identified. The reportable condition has been documented in the plant's corrective action program as CR-2014-005610.
4122014001 | Beaver Valley 2 | 05/01/2014 | 06/27/2014 | ML14181B08 | <strong>Unacceptable Indication Identified During Reactor Vessel Head Inspection</strong><br /><i>Abstract:&nbsp;</i>On May 1, 2014, during the Beaver Valley Power Station, Unit No. 2 (BVPS-2) seventeenth refueling outage (2R17), the results of planned ultrasonic examinations performed on Penetration No. 41 of the reactor vessel head did not meet the applicable acceptance criteria. The indication was not through wall as there was no evidence of leakage at this penetration based on inspections performed on top of the reactor vessel head. The reactor vessel head examinations were being performed to meet the requirements of 10 CFR 50.55a(g)(6)(ii)(D) for reactor vessel head inspections to find potential flaws/indications well before the structural integrity of the reactor vessel head pressure boundary is significantly challenged. Indications that cannot be dispositioned as acceptable per ASME Code Section XI in a Reactor Coolant System pressure boundary are reportable under 10 CFR 50.72(b)(3)(ii)(A) / 50.73(a)(2)(ii)(A) as a condition of the nuclear power plant, including its principal safety barriers, being degraded.<br /><br /> Primary Water Stress Corrosion Cracking (PWSCC) of the Alloy 600 penetration tube material was determined to be the apparent cause of the identified flaw. Reactor head Penetration No. 41 was repaired in accordance with the applicable embedded flaw repair methodology which was approved by the Nuclear Regulatory Commission for use at BVPS-2. The safety significance of this indication was very low.
4122014002 | Beaver Valley 2 | 05/20/2014 | 07/21/2014 | ML14204A07 | <strong>Manual Reactor Trip due to High Steam Generator Water Level During Plant Start</strong><br /><i>Abstract:&nbsp;</i>On May 20, 2014, at 0835 hours during a plant startup following the seventeenth refueling outage, Beaver Valley Power Station (BVPS) Unit 2 operations personnel manually tripped the reactor when it was recognized that the pre-determined trip criteria of 85 percent narrow range water level in the 'A' Steam Generator would be met. This manual trip criterion was reached after the steam generator water level began to oscillate following the start of the second condensate pump. Due to low decay heat input the main steam line isolation valves were shut in order to limit reactor coolant system cool down. Plant trip response was as expected without complications, and all control rods fully inserted in the core.<br /><br /> This event is being reported pursuant to 10 CFR 50.73(a)(2)(iv)(A) as a condition that resulted in the valid manual or automatic actuation of any of the systems listed in (a)(2)(iv)(B) - (1) Reactor Protection System (RPS) and (2) Multiple Main Steam Isolation Valves (MSIVs). A 10 CFR 50.72 notification was made at 1052 hours on May 20, 2014, to report the manual reactor trip and main steam line isolation (EN# 50124).<br /><br /> The cause of this event has been determined to be the lack of an integrated secondary startup procedure. Station operating procedures will be revised to prevent recurrence.
4122014006 | Beaver Valley 2 | 12/09/2014 | 02/05/2015 | ML15040A08 | <strong>Unplanned Automatic Actuation of Both Standby Service Water Pumps</strong><br /><i>Abstract:&nbsp;</i>On December 9, 2014, at 1929 hours Beaver Valley Power Station (BVPS) Unit 2 experienced an unplanned automatic start of both Standby Service Water Pumps (2SWE-P21A and 21B). An equipment clearance was being restored when 2SWE-P21A pump started automatically. Within seconds of the automatic start, 2SWE-P21B pump started due to a brief low header pressure condition that occurred while the discharge valve for the 2SWE-P21A pump was cycling open prior to the 2SWE-P21A pump reaching its rated speed and discharge pressure. Operations confirmed plant stability and verified that the standby pumps were not required to be running. Both pumps were secured and placed in automatic after approximately five minutes of run time.<br /><br /> The cause of this event was a circuit interaction which occurred when a 120 VAC breaker was closed.<br /><br /> This event is reportable pursuant to 10 CFR 50.73(a)(2)(iv)(A) as a condition that resulted in the actuation of an emergency service water system that does not normally run and that serves as an ultimate heat sink which is a system listed in 10 CFR 50.73(a)(2)(iv)(B)(9).<br /><br /> Corrective actions include providing additional clearance instructions to ensure that appropriate actions are taken for clearances involving NAS cards.
4132014001 | Catawba 1 | 03/07/2014 | 05/06/2014 | ML14127A45 | <strong>Condition Prohibited by Technical Specifications (TS) and Notice of Enforcement Discretion (NOED) due to Misaligned Connecting Rod Bearing on Diesel Generator (DG) 1A</strong><br /><i>Abstract:&nbsp;</i>On March 7, 2014 at 0929 hours, TS 3.8.1, "AC Sources - Operating" was violated as a result of maintenance activities on DG 1A to replace a connecting rod bearing that was found to have rotated from its normal horizontal position. Catawba had previously requested a NOED on March 6, 2014 in anticipation of exceeding the applicable TS 3.8.1 Required Action Completion Time. The NOED was subsequently granted by the NRC on that same day. This event is therefore reportable under 10 CFR 50.73(a)(2)(i)(B) as an operation or condition which was prohibited by the plant's TS. The affected bearing was proactively replaced, leading to the need for the NOED. The most probable cause of the rotation of the affected bearing is inadequate procedural control of lubricating oil temperature prior to starting an engine following extended periods of maintenance. Corrective actions taken in response to this event include revisions to plant procedures governing DG maintenance and operation. It was subsequently determined that the affected DG 1A bearing would have been able to perform its specified safety function in the as-found condition. During the period that DG 1A was inoperable while the affected bearing was being replaced, DG 1B was operable. Therefore, this event had no adverse effect upon the health and safety of the public.
4162014002 | Grand Gulf 1 | 03/17/2014 | 05/15/2014 | ML14135A21 | <strong>Manual Actuation of the Reactor Protection System due to Steam Leak with Reactor Core Isolation Cooling Manual Initiation</strong><br /><i>Abstract:&nbsp;</i>On March 17, 2014, at 05:14 Central Daylight Time with the plant at 41 percent rated core thermal power during power ascension from refueling outage 19, Grand Gulf Nuclear Station manually actuated the Reactor Protection System (RPS) to shut down the reactor due to a steam leak in the turbine building. All control rods fully inserted and all safety systems operated as designed. The Main Steam Isolation Valves (MSIVs) were manually shut and the Reactor Core Isolation Cooling (RCIC) System was manually initiated. No Safety Relief Valves (SRVs) actuated automatically. Manual cycling of SRVs and RCIC was used to maintain reactor water level and pressure within normal bands. Group 2 and 3 Residual Heat Removal (RHR) isolation signals were received. However, no valve movement occurred since the affected valves are normally closed. The cause of the manual RPS actuation was a steam leak in the turbine building resulting from a failed turbine first stage pressure sensing line (TFSPSL) followed by a failed main steam line four inch drain line. The failed drain line has been replaced and both TFSPSLs have been removed. Temporary modifications have been issued for implementation of "a current source" strategy. This action removes the TFSPSLs and installs two electronic modules as an interim action while a design change to eliminate the need for the TFSPSLs is being developed. The event posed no threat to public health and safety.
4162014003 | Grand Gulf 1 | 03/29/2014 | 05/28/2014 | ML14148A04 | <strong>Automatic Actuation of the Reactor Protection System due to Load Reject Relay Fault</strong><br /><i>Abstract:&nbsp;</i>On March 29, 2014, at 10:08 Central Daylight Time with the plant at 87 percent rated core thermal power, Grand Gulf Nuclear Station experienced an automatic actuation of the reactor protection system and plant scram due to a Main Turbine Overspeed Protection Load Reject Relay (LRR) fault. All control rods fully inserted and safety systems operated as designed. No safety relief valves lifted and no isolation signals were received. Reactor Water Level increased, resulting in a Level 9 SCRAM signal which caused an automatic trip of both reactor feed pumps to reduce reactor water inventory. However, reactor feedwater was promptly restored. The cause of the event was an L-RR fault which caused a fast closure signal to the Main Turbine Control Valves (TCV). The TCV closure resulted in the automatic actuation of the reactor protection system and plant scram. Investigations determined the cause of the LRR fault was a failed ceramic capacitor on a Multiplier Module (MM) card. The failed MM card has been replaced as well as the LRR power supply, power measurement input module and voltage measurement input module. The event posed no threat to public health and safety.
4232014001 | Millstone 3 | 01/26/2014 | 03/17/2014 | ML14084A30 | <strong>Limiting Condition for Operation Exceeded upon Approval of Enforcement Discretion</strong><br /><i>Abstract:&nbsp;</i>At 1350 on January 26, 2014 while operating in Mode 1 at approximately 96% power, Millstone Power Station Unit 3 (MPS3) exceeded the Limiting Condition for Operation of plant Technical Specification (TS) 3.7.1.2 "Auxiliary Feedwater System" Action C for an inoperable auxiliary feedwater pump. The turbine driven auxiliary feedwater pump (TDAFWP) had been declared inoperable at 1350 on January 23, 2014. TS 3.7.1.2 Action C requires that the pump be restored to operable status within 72 hours or be in at least HOT STANDBY within the next 6 hours and in HOT SHUTDOWN within the following 12 hours. The TDAFWP had been declared inoperable on January 23, 2014 when the pump tripped during a test. Subsequent repairs, maintenance, and testing were nearing completion but, would require additional time beyond the 72 hour TS Action C requirements. In a teleconference call on January 26, 2014, Dominion Nuclear Connecticut, Inc. (DNC) requested a notice of enforcement discretion (NOED) from the requirements of TS 3.7.1.2, Action C. The NRC exercised enforcement discretion to not enforce compliance with TS 3.7.1.2, Action C, for an additional period of 36 hours (to expire at 0150 January 28, 2014). The TDAFWP was restored to OPERABLE status at 0505 on January 27, 2014.<br /><br /> This condition is being reported as any operation or condition which was prohibited by the plant's technical specifications in accordance with 10 CFR 50.73 (a)(2)(i)(B).
4232014002 | Millstone 3 | 03/12/2014 | 05/05/2014 | ML14129A46 | <strong>DC Circuit Hot Shorts</strong><br /><i>Abstract:&nbsp;</i>While Millstone Power Station Unit 3 (MPS3) was operating at 100 percent power in Mode 1 on March 12, 2014, operations determined that a concern identified by Engineering as a result of recent industry operating experience (NRC Event Number 49889) could result in an unanalyzed condition. Engineering's review of direct current (DC) circuits associated with the main turbine emergency lube oil and main generator emergency seal oil pumps determined the described condition to be applicable to MPS3.<br /><br /> This condition is reportable pursuant to 10 CFR 50.73(a)(2)(ii)(B) as an unanalyzed condition that significantly degraded plant safety. A prompt notification per EN49903 was submitted to the NRC on March 12, 2014.<br /><br /> The cause of the condition was a manufacturer's design error that was installed during plant construction. Compensatory fire watches have been implemented for affected areas of the plant. Plant modifications are planned that will protect or isolate the affected circuits leaving the initial fire area.
4232014003 | Millstone 3 | 05/01/2014 | 06/30/2014 | ML14189A07 | <strong>Turbine Driven Auxiliary Feedwater Pump Operability Impacted by Incorrect Bearing</strong><br /><i>Abstract:&nbsp;</i>On May 1, 2014 with Millstone Power Station Unit 3 in operating mode 1 and 100% reactor power, an evaluation determined the installation of an incorrect vendor supplied bearing introduced a non-conforming condition, which over time and under certain variable conditions, resulted in excessive friction affecting the ability of the turbine driven auxiliary feedwater (TDAFW) pump to operate properly and could render it inoperable. Plant Technical Specification 3.7.1.2 Action c, requires, if one auxiliary feedwater pump is inoperable in operating modes 1, 2, and 3, the pump must be returned to operable status within 72 hours, or the plant be placed in at least hot standby within six hours and in hot shutdown within the following 12 hours.<br /><br /> An investigation determined the installation of an incorrect bearing in the TDAFW pump steam supply valve control linkage during refueling outage 3R15 (spring of 2013) caused a discrepant condition rendering the TDAFW pump inoperable for periods of time exceeding the limiting conditions for operations action statement for TS 3.7.1.2. The bearing manufacturer issued a 10 CFR 21 report on this issue. (ADAMS accession # ML14079A353).<br /><br /> The incorrect bearing was replaced, the governor and associated linkage were groomed/adjusted, and the TDAFW pump was tested satisfactorily. Additional corrective actions are being taken in accordance with the station's corrective action program.<br /><br /> This condition is reportable pursuant to 10 CFR 50.73(a)(2)(i)(B), any operation or condition which was prohibited by the plant's TS.
4232014004 | Millstone 3 | 12/12/2014 | 02/09/2015 | ML15049A29 | <strong>Unlatched Dual Train HELB Door Results in Potential Loss of Safety Function</strong><br /><i>Abstract:&nbsp;</i>On December 12, 2014, with Millstone Power Station Unit 3 (MPS3) at 100% power in operating mode 1, an operator discovered a door for the MPS3 East Motor Control Center Rod Control area would not latch upon exit from the room. Upon discovery, the door was declared non-functional. Since this door is a dual train High Energy Line Break (HELB) boundary door, it affected the operability of both trains of 480 volt safety related switch gear. Plant Technical Specification (TS) 3.0.3 was entered. Maintenance personnel repaired the lockset mechanism. Proper operation of the door was restored within 35 minutes of being identified not functioning properly and TS 3.0.3 was exited. On January 15, 2015, with MPS3 at 100% power in operating mode 1, an individual processed through the door normally and upon checking the door after passage the worker noted the door did not latch. The Control Room was promptly notified. The door was repaired and retested satisfactorily. TS 3.0.3 was entered and exited appropriately. The door was inoperable for approximately 19 minutes.<br /><br /> Although no definite failure mechanism was identified, there have been several occasions where a security door lockset has been jammed due to usage of the emergency-use-only door hardware (crash bar/thumb piece). In both cases the door lockset mechanism was manually manipulated, lubricated and then tested several times satisfactorily by maintenance personnel. Inspection of the lockset mechanism did not find any foreign material in the lockset mechanism. Management issued a special communication to remind plant personnel that security doors not be accessed by the use of the crash bar or door thumb piece/knob/lever except for an emergency. Additional corrective actions are being taken in accordance with the station's corrective action program.<br /><br /> These events are being reported pursuant to 10 CFR 50.73(a)(2)(v)(D), as a condition that could have prevented the fulfillment of a safety function for systems needed to mitigate the consequences of an accident.
4242014001 | Vogtle 1, Vogtle 2 | 02/20/2014 | 04/11/2014 | ML14104B43 | <strong>Operation Outside of Pressure and Temperature Limit Report Curve Required by Technical Specification 3.4.3</strong><br /><i>Abstract:&nbsp;</i>On February 20, 2014 with VEGP Units 1 and 2 operating at 100 percent thermal power, VEGP identified that both units had operated outside the Pressure / Temperature Limit Report (PTLR) curve required by Technical Specification LCO 3.4.3 RCS Pressure and Temperature Limits following the seven previous refueling outages on each unit. From October 2003 through May 2013, seven refueling outages have been conducted on each unit in which the Reactor Pressure Vessel (RPV) was placed under vacuum to perform fill and vent operations. LCO 3.4.3 requires that Reactor Coolant System (RCS) pressure, temperature, and heatup and cooldown rates be maintained with the limits specified in the Pressure Temperature Limit Report (PTLR) and is applicable at all times. Although minimum RCS temperature and heatup rates were maintained within limits, RCS pressure was lowered below 0 pounds per square inch gauge (psig), the lowest RCS pressure value identified on the curve.<br /><br /> The cause of not entering LCO 3.4.3 was the condition was procedurally allowed and aligned with Operations training. These events are of very low safety significance and resulted in no adverse effects on the health or safety of the public.
4242014002 | Vogtle 1 | 04/12/2014 | 06/05/2014 | ML14156A52 | <strong>Unit 1 Manual Reactor Trip due to Main Steam Isolation Valve Failure</strong><br /><i>Abstract:&nbsp;</i>On 4/12/14 at 20:08, Unit 1 Reactor was manually tripped from 28 percent power. The manual trip occurred during power ascension following the 1R18 refueling outage. Control room operators received a Loop 1 Train B main steam isolation valve (MSIV) trouble annunciator followed by the MSIV not fully open annunciator. Control room operators recognized steam generator 1 level and loop 1 steam flow lowering and manually tripped the reactor.<br /><br /> Unit 1 was stabilized in Mode 3. Plant systems responded as expected with decay heat removal via Auxiliary Feedwater and steam discharge to the Main Condenser. Unit 2 was unaffected and there were no adverse effects on plant safety or on the health and safety of the public. This incident is of very low safety significance.
4242014003 | Vogtle 1 | 05/30/2014 | 07/28/2014 | ML14209A48 | <strong>Failure to Meet Acceptance Criteria of Technical Specification 5.5.11 Ventilation Filter Testing Program</strong><br /><i>Abstract:&nbsp;</i>At 11:16 on May 30, 2014 Operations declared 1A CREFS inoperable upon notification that 1A Control Room Emergency Filtration System (CREFS) charcoal adsorber sample taken on April 15, 2014 had a 99.66 percent retention value. This failed to meet the Technical Specification 5.5.11 Ventilation Filter Testing Program (VFTP) retention criteria of 99.8 percent. This report is made pursuant to 10 CFR 50.73 (a)(2)(i)(B) as a condition prohibited by Technical Specifications.<br /><br /> The charcoal was replaced and on June 6, 2014 Unit 1A CREFS was returned to service. During the event, Unit 1 was operating at 100 percent rated thermal power at steady-state conditions and Unit 2 was unaffected. Therefore, there were no adverse effects on plant safety or on the health and safety of the public. This incident is of very low safety significance
4242014004 | Vogtle 1 | 07/27/2014 | 09/25/2014 | ML14268A36 | <strong>Manual Reactor Trip due to Loss of Feedwater flow</strong><br /><i>Abstract:&nbsp;</i>On July 27, 2014 at approximately 1409 Eastern Daylight Time, Vogtle Unit 1 was operating in Mode 1 at 100 percent power. While surveillance testing was being performed on the Main Feed Pump A (MFP A) a control oil leak developed in the lockout solenoid valve. The reduced control oil pressure resulted in a reduction of feed pump speed. Control Room Operators observed lowering feedwater flow to the Steam Generators and manually actuated the Reactor Protection System (RPS) system which resulted in a turbine-generator trip. All rods fully inserted into the core, the Main Feedwater Isolation system and the Auxiliary Feedwater system automatically actuated as expected. The unit was stabilized in Mode 3 and decay heat was discharged to the condenser. The cause of the event was a failure of the trip lockout solenoid valve which led to reduced pressure on the trip relay for MFP-A which reduced the speed of the pump and consequently the total feed flow to the Steam Generators.<br /><br /> The safety significance of the event is very low. Unit 2 was not affected and there were no adverse effects on the health and safety of the public.
4252014001 | Vogtle 2 | 04/08/2014 | 05/30/2014 | ML14154A05 | <strong>Automatic Reactor Trip due to Low Steam Generator Level</strong><br /><i>Abstract:&nbsp;</i>On April 8, 2014 at approximately 04:30 Eastern Standard Time, Vogtle Unit 2 was operating at Mode 1 at 100 percent power when Unit 2 received a Steam Generator 3 narrow range low-low level automatic Reactor Protection System actuation as a result of the Loop 3 Main Feedwater Regulating Valve failing closed. The RPS actuation resulted in a trip of the turbine-generator. All rods fully inserted into the core, the Main Feedwater Isolation system and the Auxiliary Feedwater system automatically actuated as expected. The plant was stabilized in Mode 3 and the decay heat was discharged to the condenser. The cause of the event was a failure of the Steam Generator 3 Main Feed Regulator Valve control system.<br /><br /> The safety significance of the event is very low. Unit 1 was not affected and there were no adverse effects on the health and safety of the public.
4252014002 | Vogtle 2 | 08/22/2014 | 10/16/2014 | ML14289A26 | <strong>Containment Spray Pump Technical Specification Exceeded Upon Enforcement Discretion Approval</strong><br /><i>Abstract:&nbsp;</i>On August 22, 2014 at 02:00 Eastern Daylight Time (EDT), Vogtle did not meet the Technical Specification (TS) 3.6.6 "Containment Spray and Cooling Systems" Condition A completion time due to maintenance activities on the 28 Containment Spray (CS) pump. On August 21, 2014, the NRC granted Vogtle's request for a Notice of Enforcement Discretion (NOED), which was initiated in anticipation of exceeding the applicable TS required action completion time. Upon verbal approval of the NOED, Vogtle subsequently exceeded the required action completion time of LCO 3.6.6 Condition A to repair the 2B CS pump. Therefore, this event is reportable under 10 CFR 50.73(a)(2)(i)(B) as an operation or condition prohibited by the TS. <br /><br /> While the 2B CS pump was being restored no other safety-related or non-safety-related risk significant systems were out of service. Therefore, this event had no adverse effect on the health and safety of the public. This event is of very low safety significance.
4252014003 | Vogtle 2 | 10/12/2014 | 12/11/2014 | ML14345A32 | <strong>Unit 2 Manual Reactor Trip due to Out of Sequence Control Rod Movement</strong><br /><i>Abstract:&nbsp;</i>On October 12, 2014 at approximately 0944 EST, while performing Unit 2 reactor startup, control rods were being inserted to stabilize Rx power for Low Power Physics Testing. With the rod bank selector switch in Manual, operators observed control bank A inserting instead of the expected D bank inserting. Operators took action to trip the reactor and stabilize the plant. The cause of this event was incorrect setup of the Rod Bank Overlap unit.<br /><br /> Upon tripping the reactor, plant systems responded per design and Unit 2 was stabilized in Mode 3. Unit 1 was not affected and there were no adverse effects on the health and safety to the public. Therefore, the safety significance of this event is very low.
4402014001 | Perry | 01/03/2014 | 03/04/2014 | ML14066A03 | <strong>Failure to Comply with Technical Specification 3.4.11 - Reactor Coolant System Pressure/Temperature Limits</strong><br /><i>Abstract:&nbsp;</i>On January 3, 2014, it was determined that the Perry Nuclear Power Plant had not complied with Technical Specification (TS) 3.4.11, Reactor Coolant System (RCS) Pressure and Temperature (KT) Limits, between June 2011 and September 2013, during cooldown and start-up of the plant to support plant outages. Technical Specification Figure 3.4.11-1 contains P/T limit curves for heatup, cooldown, and inservice leak and hydrostatic testing. The heatup curve provides limits for both heatup and criticality. Each P/T limit curve defines an acceptable region for normal operation. The P/T curves do not graphically go below 0 psig.<br /><br /> PNPP typically starts up under a slight vacuum with main steam valves open to the condenser. This is done to minimize the impact to systems that might see a pressure surge if the main steam isolation valves were kept closed during startup and then opened under pressure from the vessel.<br /><br /> The cause is a lack of effective leadership intrusiveness, specifically related to work prioritization supporting the timely resolution of deficiencies associated with TS 3.4.11. Corrective actions include training and submittal of a license amendment to revise TS 3.4.11.<br /><br /> Engineering analysis concluded there is no adverse hardware condition created from the vacuum used during start-up and the associated risk from the probabilistic standpoint is considered to be small.
4402014002 | Perry | 05/07/2014 | 07/07/2014 | ML14191A63 | <strong>Division 2 Diesel Generator Inoperability Results in Loss of Safety Function and Condition Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On May 7, 2014, at 1158 hours, with the Perry Nuclear Power Plant (PNPP) in Mode 1 at 100% power, the division 2 emergency diesel generator (EDG) was declared inoperable after a lube oil system leak was identified on the right bank turbocharger during the monthly surveillance run. An emergency shutdown of the EDG was performed. The leak was caused by a cracked 1/2" to 1/4" Swagelok coupling.<br /><br /> The crack propagation was determined to have started during the monthly surveillance run on April 12, 2014. Therefore, a condition prohibited by technical specifications existed for the period of April 28 through May 8, 2014, as the division 2 EDG was inoperable for the period. Additionally, review of PNPP plant narrative logs identified the division 1 EDG was inoperable during its monthly surveillance run for approximately 3.5 hours on May 3 and 4, 2014, resulting in a condition that could have prevented the fulfillment of a safety function.<br /><br /> The root cause was determined to be cyclical fatigue of a tube fitting resulting from tubing misalignment. The tubing misalignment was a result of not providing adequate maintenance and installation guidance.<br /><br /> This event was determined to be of low safety significance.<br /><br /> This event is being reported under 10CFR50.73(a)(2)(i)(B) as an Operation or Condition Prohibited By Technical Specifications and 10CFR50.73(a)(2)(v)(D) Event or Condition that Could Have Prevented Fulfillment of a Safety Function.
4402014003 | Perry | 06/19/2014 | 08/15/2014 | ML14227A72 | <strong>Unanalyzed Condition Resulting From Unfused Direct Current Control Circuits</strong><br /><i>Abstract:&nbsp;</i>Based on a review of industry operating experience, it was identified that the Perry Nuclear Power Plant (PNPP) has unfused direct current (DC) control circuits that are routed from the respective equipment to other plant areas including the Unit 1 Control Room, Division 1 Cable Spreading, and Division 1 Cable Chase. Without overcurrent protection for these circuits, the potential exists that an initial fire event affecting these circuits could cause short circuits that would cause excessive current through the circuit beyond the capacity rating of the conductors. This could lead to a secondary fire in another plant area where these circuits are routed, challenging the ability to achieve and maintain safe shutdown.<br /><br /> This condition is being reported under 10CFR50.73(a)(2)(ii)(B) as an unanalyzed condition that significantly degraded plant safety. Notification was made under 10CFR50.72(b)(3)(ii)(B) on June 19, 2014 (EN 50213).<br /><br /> The cause was determined to be latent design deficiency in the identified circuits dating back to original design and installation that was not identified during the design review for 10 CFR 50 Appendix R Section III.G (Fire protection of safe shutdown capability). Compensatory fire watches have been implemented for the affected fire areas. Planned corrective actions include plant modifications to install overcurrent protection in the affected DC control circuitry.<br /><br /> This event was determined to be of low safety significance.
4402014004 | Perry | 10/20/2014 | 12/17/2014 | ML14356A02 | <strong>Loss of Feedwater Results in Automatic Reactor Protection System Actuation</strong><br /><i>Abstract:&nbsp;</i>On October 20, 2014, at 0217 hours, the reactor protection system (RPS) automatically actuated due to a loss of feedwater flow to the reactor pressure vessel (RPV). There were no complications during the shutdown as all control rods fully inserted and pressure was maintained by normal means. The High Pressure Core Spray (HPCS) and the Reactor Core Isolation Cooling (RCIC) systems actuated based on a valid low reactor water level initiation and injected to restore RPV water level. <br /><br /> The cause of the event was failure of a balance-of-plant static transfer switch, which provides electrical power to the digital feedwater control system. A circuit card in the static transfer switch degraded, which caused a loss of power during manual transfer operations. The electrical loads serviced by the inverter were placed on an alternate power source using the bypass test switch. A design change was completed to provide diverse power sources for the digital feedwater control system availability logic to prevent similar occurrences. <br /><br /> The safety significance of this event is considered to be small. This event is being reported in accordance with 10 CFR 50.73(a)(2)(iv)(A) as an event or condition that resulted in an automatic actuation of the RPS, HPCS, and RCIC systems, and Operational Requirements Manual section 7.6.2.1, which requires a Special Report submittal following an Emergency Core Cooling System actuation and injection into the reactor coolant system.
4402014005 | Perry | 11/07/2014 | 01/06/2015 | ML15009A03 | <strong>Loss of Feedwater Results in Automatic Reactor Protection System Actuation</strong><br /><i>Abstract:&nbsp;</i>On November 7, 2014, at 0847 hours, the reactor protection system (RPS) automatically actuated due to a loss of feedwater flow to the reactor pressure vessel (RPV). There were no complications during the shutdown as all control rods fully inserted and pressure was maintained by normal means. The high pressure core spray (HPCS) and the reactor core isolation cooling (RCIC) systems actuated based on a valid low reactor water level initiation and injected to restore RPV water level.<br /><br /> The cause of the event was determined to be the injection of an invalid runback signal from the redundant reactivity control system (RRCS) into the digital feedwater control system (DFWCS). The design change which implemented DFWCS was identified to have a latent design flaw and a design change will be implemented to eliminate these single point vulnerabilities.<br /><br /> The safety significance of this event is considered to be small. This event is being reported in accordance with 10 CFR 50.73(a)(2)(iv)(A) as an event or condition that resulted in an automatic actuation of the RPS, HPCS, and RCIC systems, and also Operational Requirements Manual (ORM) section 7.6.2.1, which requires a special report submittal following an emergency core cooling system actuation and injection into the reactor coolant system.
4432014001 | Seabrook | 04/01/2014 | 05/19/2014 | ML14142A21 | <strong>Automatic Reactor Trip due to Delay in Automatic Bus Transfer Resulting in RCP Loop Low Flow</strong><br /><i>Abstract:&nbsp;</i>On April 1, 2014 at 00:26 while operating at approximately 15% power following turbine shutdown and removal of the main generator from service, Seabrook Station experienced an automatic reactor trip on reactor coolant two loop loss of flow. The loss of flow was the result of the unexpected closure of the main generator breaker (MGB) "B" phase resulting in 345KV bus 6 de-energizing to isolate the generator breaker. All buses transferred to the reserve auxiliary transformers as designed; however, a slight delay in the automatic transfer for bus 1 resulted in two reactor coolant pumps (RCP) tripping. The RCPs tripping resulted in an automatic reactor trip due to reactor coolant loop low flow. The emergency feedwater system actuated on low SG level, and plant equipment functioned as expected. No adverse consequences resulted from this event.<br /><br /> The root cause is inadequate procedural guidance as the procedure used for MGB operation lacked appropriate information regarding local/remote selector switch position, mitigating actions, and minimizing time with MGB protection defeated. Corrective action is to revise the procedure to add controls to communicate potential risk while switch is in the local position, ensure the use of guarded equipment controls, and minimize the time spent with the switch in local without breaker lock rods installed.
4432014002 | Seabrook | 04/06/2014 | 08/07/2014 | ML14225A65 | <strong>Reactor Coolant Pump Undervoltage Time Delay Relays Exceed Acceptance Criteria</strong><br /><i>Abstract:&nbsp;</i>On April 6, 2014, while the plant was in refueling outage sixteen, it was determined during surveillance testing that three of four reactor coolant pump (RCP) undervoltage (UV) reactor trip channels exceeded the Technical Specification (TS) channel response time acceptance criteria of 1.5 seconds for the RCP UV reactor trip function. The condition for the RCP UV time delay relays exceeding tolerance was experienced on all four channels; however, only three of the four channels did not meet their TS required response times. Since this condition involved multiple similar components, there is evidence indicating that this condition may have arisen over time and three channels of RCP UV were inoperable concurrently. This resulted in the plant operating in a condition prohibited by the TS.<br /><br /> The root cause was determined to be the revisions of the Design Control Manual in 1991 and earlier did not require a failure modes and effects analysis as part of the design change packages that installed the E7022PA relays. The RCP UV time delay setting was not identified as a critical attribute and the manufacturer's recommendations for applications requiring very precise time delay settings were overlooked and not incorporated into station procedures. Corrective actions already taken include the replacement of one relay and adjustment of all relays to acceptable response times. Planned corrective actions are to revise procedures to energize relays for at least 3 hours before performing testing, to perform rechecks at 72 hours during outages and perform additional rechecks if adjustments were made.
4452014001 | Comanche Peak 1 | 01/18/2014 | 03/19/2014 | ML14087A00 | <strong>Unit 1 Automatic Reactor Trip due to Generator Lockout Relay Trip</strong><br /><i>Abstract:&nbsp;</i>At 0840 hours, on January 18, 2014, Unit 1 was operating at approximately 100% power when an automatic reactor trip occurred due to a generator lock out relay trip and turbine trip. The plant responded as expected to the transient. The cause of this event was a Unit 1 Generator Current Transformer (CT) cable shorting to ground. Vibration of the cable and contact of the cable with the free end of the conduit resulted in physical wear of the cable jacket and insulation that over the period of more than 12 years (from 2002 to 2014) cut through the jacket and insulation and allowed the conductor to contact the metal of the conduit. The corrective actions included reworking the grounded cable. The Unit 1 and Unit 2 Generator CT cables will be inspected, insulated, retrained, and/or replaced at each unit's next refueling outage. The Unit 1 and Unit 2 Generator CT conduits will have insulated bushings installed at the conduit exits where the conduit is not connected to a device or panel within a hub. No component or system failures occurred. All times in this report are approximate and Central Standard Time unless noted otherwise.
4452014002 | Comanche Peak 1, Comanche Peak 2 | 02/04/2014 | 04/03/2014 | ML14101A36 | <strong>Non-Compliance with Pressure-Temperature Limits Report During RCS Vacuum Fill</strong><br /><i>Abstract:&nbsp;</i>On February 4, 2014, Luminant Power recognized Operating Experience at another station to be potentially applicable to Comanche Peak Nuclear Power Plant (CPNPP). An NRC inspection report described a failure to comply with reactor coolant system (RCS) Pressure/Temperature (P/T) Limits when RCS pressure decreases below 0 pounds per square inch gauge (PSIG). At the time of discovery, CPNPP's Pressure Temperature Limit Report (PTLR) only described pressures equal to or greater than 0 PSIG. However, since early 1996, CPNPP's analyses and procedures allowed drawing a vacuum during RCS refill following refuelings. Therefore, Luminant Power is conservatively reporting RCS pressure below 0 PSIG as a violation of Technical Specification 3.4.3 "RCS Pressure and Temperature (P/T) Limits."<br /><br /> The coordination of the change in RCS operating conditions was less than adequate, in that the associated affected documents were not revised as a result of failing to correctly identify the documents and/or involve all applicable parties, as well as the subtlety of the PTLR pressure value discrepancy. The apparent cause of not maintaining RCS pressure within the limits described in the PTLR was a legacy design implementation error. The apparent mental model by licensed operations personnel was not aligned with the literal applicability of the PTLR curves, in that the curves are applicable during RCS vacuum fill conditions, and not limited to only heat-up, cool-down, and inservice leak/hydrostatic testing conditions. Luminant Power interpreted the PTLR to only apply to RCS pressure conditions above atmospheric pressure, and therefore did not consider it in conflict with the adoption of the vacuum refill analysis and procedure. Corrective actions included revising the PTLR to specify negative 14.7 pounds per square inch gage (PSIG) as the lower limit. The explicit PTLR compliance error during vacuum refill did not adversely affect the health and safety of the public or station personnel.<br /><br /> All times in this report are approximate and Central Daylight Time unless noted otherwise.
4452014003 | Comanche Peak 1 | 11/20/2014 | 01/19/2015 | ML15035A06 | <strong>Safety Chiller Inoperable for Longer Than Allowed by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On August 28 2014, the condenser pressure on the Unit 1, train A Safety Chiller was determined to be 20 psig and rising. On November 20, 2014, a past operability review was completed that determined the Unit 1, train A Safety Chiller was inoperable for approximately 192 hours from August 21, 2014 to August 29, 2014, which exceeded the 72 hour completion time of Technical Specification 3.7.19. The cause of this event was the pressure switch on the safety chilled water purge system failed to actuate a purge valve to remove non-condensable gases from the Safety Chiller. Corrective actions included replacement of the purge high pressure switch and revising the maintenance procedures to require a verification of the purge unit function on start-up of the chiller prior to declaring the chiller operable.<br /><br /> All times in this report are approximate and Central Time unless noted otherwise.
4462014002 | Comanche Peak 2 | 04/25/2014 | 06/24/2014 | ML14188C07 | <strong>Both Trains of RHR Inoperable During Testing in MODE 3</strong><br /><i>Abstract:&nbsp;</i>On April 25, 2014, valve 2-8809B, RHR to CL 2-03/2-04 INJ ISOL VLV was closed during performance of boundary valve testing per procedure OPT-615B, "RCS PRESSURE BOUNDARY LEAKAGE TEST FOR LOOP 3 CL INJECTION VALVES" while Unit 2 was in MODE 3. Closure of valve 2-8809B rendered both Residual Heat Removal (RHR) trains inoperable resulting in entry into Technical Specification (TS) Limiting Condition for Operation (LCO) 3.0.3.<br /><br /> The cause of the event has been determined to be due to a failure to transmit pertinent information to support a decision to change plant operating modes. Corrective actions include procedure revisions.<br /><br /> All times in this report are approximate and Central Daylight Time unless noted otherwise.
4462014003 | Comanche Peak 2 | 05/19/2014 | 09/18/2014 | ML14273A44 | <strong>Two Pressurizer Safety Valves As-Found Lift Settings Found Outside Technical Specification Limits</strong><br /><i>Abstract:&nbsp;</i>On May 19, 2014, Comanche Peak Nuclear Power Plant (CPNPP) Unit 2, discovered that two of the three Pressurizer Safety Valves (PSVs), which had been removed from the system and shipped off-site for testing in support of the fourteenth refueling outage, failed their as-found lift tests with lift pressures above the Technical Specification (TS) 3.4.10 setpoint of >/= 2410 psig and <1= 2485 psig These failures resulted in the determination that this condition was reportable pursuant to 10CFR50.73 (a)(2)(i)(B); "Any operation or condition which was prohibited by the plant's Technical Specifications." <br /><br /> There was no material condition issue associated with the PSVs that contributed to the test failures. The PSVs are performing within their design capabilities. The cause of the test failures was determined to be set point drift and the close tolerance required by the TS acceptance criteria. Additionally, it was also noted that the preventive maintenance frequency for the PSVs may have an effect on set point drift. As part of the correct action program, a revision to the preventive maintenance frequency is being considered.
4462014005 | Comanche Peak 2 | 08/20/2014 | 10/20/2014 | ML14308A07 | <strong>Centrifugal Charging Pump Inoperable for Longer than Allowed by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On August 3, 2014, while starting Centrifugal Charging Pump (CCP) 2-02, the CCP 2-02 Main Lubricating Oil pump (MLOP) decoupled from its drive shaft. On August 20, 2014 an evaluation was completed that determined CCP 2-02 was inoperable from July 6, 2014 to August 3, 2014, which exceeded the completion times of Technical Specification 3.5.2. During this time, CCP 2-01 was also inoperable for 1 hour 44 minutes on July 14, 2014, and for 1 hour 4 minutes on July 18, 2014. The cause of this event was the design of the CCP MLOP coupling requires blind fitting of the drive pins into the drive pin holes and does not definitively allow for post-installation verification. Corrective actions include replacement of the CCP 2-02 MLOP shaft hub and speed increaser bushings, modification of the MLOP coupling design, procedure revisions, and Maintenance personnel training.<br /><br /> All times in this report are approximate and Central Time unless noted otherwise.
4542014001 | Byron 1, Byron 2 | 01/23/2014 | 03/24/2014 | ML14083A15 | <strong>0A Essential Service Water (SX) Makeup Pump Unexpected Auto Start During 0B SX Pump Monthly Surveillance</strong><br /><i>Abstract:&nbsp;</i>On January 23, 2014, Byron Unit 1 and Unit 2 were in Mode 1 with reactor power at 100 percent. At 0539, the 0A Essential Service Water (SX) Makeup Pump auto-started while lowering basin level for the scheduled 0B SX Makeup Pump monthly run surveillance. The 0A SX Makeup Pump was running for approximately 21 minutes until it could be secured per the operating procedure. At the time of the 0A SX Makeup Pump autostart, SX tower basin levels were being lowered for a scheduled 0B SX Makeup Pump auto-start per 0BOSR 7.9.6-2, "Essential Service Water Makeup Pump 0B Monthly Operability Surveillance".<br /><br /> Since the auto-start of the opposite train SX makeup pump was not part of a preplanned sequence during the surveillance, this is a reportable condition in accordance with 10 CFR 50.73(a)(2)(iv)(A) as an event or condition that resulted in manual or automatic actuation of an Emergency Service Water System that does not normally run and that serves as an ultimate heat sink, which is listed in paragraph 10 CFR 50.73(a)(2)(iv)(B).<br /><br /> The cause of the event was that the operating procedure directs the controller to be set at a level that leaves little margin to the SX Makeup Pump automatic start level switch setpoint, especially when adverse environmental conditions such as high winds and wave action exist.
4542014002 | Byron 1, Byron 2 | 02/19/2014 | 04/10/2014 | ML14100A10 | <strong>Non-Compliance with Technical Specification 3.4.3 - RCS Pressure and Temperature (P/T) Limits</strong><br /><i>Abstract:&nbsp;</i>On February 19, 2014, it was determined that the Byron Station has not complied with Technical Specifications (TS) 3.4.3, "RCS Pressure and Temperature (PIT) Limits," between March 2011 and October 2013, during start-up of the plant following plant refueling outages. Byron TS 3.4.3 Limiting Condition for Operation (LCO) states that ARCS pressure, RCS temperature, and RCS heatup and cooldown rates shall be maintained within the limits specified in the PTLR." During previous Reactor Coolant System (RCS) vacuum fill operations at Byron Station Unit 1 and Unit 2, RCS pressure exceeded the Pressure and Temperature Limits Report (PTLR) P/T curve lower bound in that the P/T curve does not indicate a limit below 0 psig. This TS non-compliance is reportable in accordance with 10 CFR 50.73(a)(2)(i)(B), "Any operation or condition prohibited by the plant's Technical Specifications".<br /><br /> The cause of operation outside of the P/T curve limits is the application of an inadequate operating procedure that allowed the P/T lower pressure bound to be exceeded during RCS fill operations.<br /><br /> RCS fill pressures below the P/T curve lower bound did not affect the integrity of the RCS system.
4542014003 | Byron 1 | 03/15/2014 | 05/14/2014 | ML14134A08 | <strong>Byron Unit 1 Diesel Generator Actuation due to System Auxiliary Transformer 142-2 Relay Actuation and Loss of Off-site Power (LOOP)</strong><br /><i>Abstract:&nbsp;</i>On March 15, 2014, at 1102 hours, Byron Station Unit 1 experienced a Loss of Off-site Power (LOOP) event. The event occurred during refuel outage B1R19 with Unit 1 in Mode 6 during reactor core offload activities. Both Unit 1 Emergency Diesel Generators (DGs) auto-started and re-energized the safety related buses as designed. During the activity, the plant received a System Auxiliary Transformer (SAT) differential relay actuation that initiated a trip and lockout of the Unit 1 SAT feed breakers, thereby resulting in a Unit 1 LOOP with subsequent DG auto-start. This condition is reportable to the NRC in accordance with 10 CFR 50.73(a)(2)(iv)(A), "Any event or condition that resulted in manual or automatic actuation of any of the systems listed in paragraph (a)(2)(iv)(B) of this section".<br /><br /> The most probable cause of the LOOP with subsequent DG auto-start was a combination of equipment failures involving a faulty test switch that caused a charge to build up in the energized-open circuit and a subsequent electrical discharge when an over-current relay was reinstalled.
4552014004 | Byron 2 | 10/07/2014 | 12/05/2014 | ML14339A53 | <strong>Byron Station Unit 2 Reactor Pressure Vessel Head Control Rod Drive Mechanism Penetration Nozzle Weld Indication Attributed to Primary Water Stress Corrosion Cracking</strong><br /><i>Abstract:&nbsp;</i>On October 7, 2014, at 1830 CST, an indication was discovered on Byron Station, Unit 2, Reactor Pressure Vessel (RPV) Penetration No. 6. The indication was located on the outside diameter of the penetration tube and the deepest wall depth was 0.222 inches, approximately 34.11 percent through wall.<br /><br /> The indication was subsequently repaired using the embedded flaw technique in accordance with NRC approved WCAP-15987, Revision 2-A and WCAP-16401, Revision 0. The apparent cause of the indication is attributed to Primary Water Stress Corrosion Cracking. Corrective actions include repair of the indication on Penetration No. 6 and revising the frequency of the Unit 2 volumetric examinations on all 78 RPV penetrations to every refueling outage.<br /><br /> This event is reportable in accordance with 10 CFR 50.73(a)(2)(ii)(A), any event or condition that resulted in the condition of the nuclear power plant, including it principle safety barriers, being seriously degraded.
4562014001 | Braidwood 1, Braidwood 2 | 02/19/2014 | 04/17/2014 | ML14107A43 | <strong>Inadequate Procedural Guidance Results in Non-Compliance with Technical Specification 3.4.3 - RCS Pressure and Temperature (P/T) Limits</strong><br /><i>Abstract:&nbsp;</i>On February 19, 2014, it was determined that the Braidwood Generating Station has not complied with Technical Specifications (TS) 3.4.3, "RCS Pressure and Temperature (P/T) Limits," between March 2011 and October 2013, during start-up of the plant following plant refueling outages. Braidwood TS 3.4.3 Limiting Condition for Operation (LCO) states that "RCS pressure, RCS temperature, and RCS heatup and cooldown rates shall be maintained within the limits specified in the PTLR." During previous Reactor Coolant System (RCS) vacuum fill operations at Braidwood Station Unit 1 and Unit 2, RCS pressure exceeded the Pressure and Temperature Limits Report (PTLR) P/T curve lower bound in that the P/T curve does not indicate a limit below 0 psig. This TS non-compliance is reportable in accordance with 10 CFR 50.73(a)(2)(i)(B), "Any operation or condition prohibited by the plant's Technical Specifications".<br /><br /> The cause of operation outside of the P/T curve limits is the application of an inadequate operating procedure that allowed the P/T lower pressure bound to be exceeded during RCS fill operations.<br /><br /> RCS fill pressures below the P/T curve lower bound did not affect the integrity of the RCS system.
4562014003 | Braidwood 1, Braidwood 2 | 06/25/2014 | 08/25/2014 | ML14237A54 | <strong>Unanalyzed Condition due of Lack of Procedure Guidance Related to the Ultimate Heat Sink</strong><br /><i>Abstract:&nbsp;</i>On June 25, 2014, during the review of a License Amendment Request (LAR) to increase the Ultimate Heat Sink (UHS) maximum temperature, a question was raised whether the various pumps taking suction from the lake should be secured for UHS level inventory conservation. A review of the Braidwood abnormal operating procedures was performed and no procedure was identified to shut down the non-essential service water (WS) pumps on a loss of the cooling lake dike. Subsequent Engineering review determined the insufficient procedure guidance represented an unanalyzed condition because the design analysis did not consider the UHS inventory loss due to the running WS pump. This event is reportable in accordance with 10CFR50.73(a)(2)(ii)(B), "Any event or condition that resulted in the nuclear power plant being in an unanalyzed condition that significantly degraded plant safety".<br /><br /> The cause of this event is ambiguity in the UFSAR regarding the CW and WS not operating following a postulated loss of the dike event. This resulted in station personnel not recognizing procedure guidance was required to proactively secure the WS pumps to incorporate UHS design analysis requirements.<br /><br /> Based on the UHS inventory loss taking an extended period of time and operator capability to identify and respond to plant and equipment indications to secure the WS pumps, the ultimate heat sink remained operable and was capable of performing its safety function.
4572014002 | Braidwood 2 | 01/18/2012 | 05/05/2014 | ML14125A24 | <strong>Age Related Degradation of Heat Trace Leads to Refueling Water Storage Tank Vent Path Temperature Decreasing Below Technical Specification Value</strong><br /><i>Abstract:&nbsp;</i>On January 18, 2012 at 0653, the heat trace controller fuse for the Unit 2 Refueling Water Storage Tank (RWST) cleared, resulting in the RWST vent path temperature to decrease below the Technical Specification (TS) Surveillance Requirement (SR) limit of 35 degrees Fahrenheit. This resulted in the RWST being declared inoperable and Unit 2 entered Limiting Condition for Operation Action Requirement (LCOAR) per TS 3.5.4, Condition B, requiring restoration of the vent path temperature to >/= 35 degrees Fahrenheit within one hour or be in hot standby in six hours and cold shutdown in 36 hours. After successful heat trace controller fuse replacement, the heat trace raised the Unit 2 RWST vent path temperature to 40 degrees Fahrenheit by 08:44 on the same day and LCOAR 3.5.4 was exited. The RWST is considered a single train system and as a result of the vent path temperature decreasing below the TS limit, this event is reportable in accordance with 10 CFR 50.73(a)(2)(v)(D), "Any event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident".<br /><br /> The cause of this event is age related degradation of heat trace due to lack of preventative maintenance replacement activities.<br /><br /> Due to no blockage being established along the vent path, the Unit 2 RWST vent line was capable of performing its safety function during the less than two hours the RWST was inoperable.
4582014001 | River Bend | 01/09/2014 | 03/10/2014 | ML14079A04 | <strong>Unanalyzed Condition Associated with Unfused Ammeters in DC Battery Indication Circuits</strong><br /><i>Abstract:&nbsp;</i>On January 9, 2014, with the plant operating at 100 percent power, the final review of industry operating experience regarding the adverse effects of unfused direct current ammeter circuits in the main control room determined the described condition to be applicable to River Bend Station, resulting in a potentially unanalyzed condition with respect to 10 CFR 50 Appendix R analysis requirements. This condition is being reported in accordance with 10 CFR 50.73(a)(2)(ii)(B). Interim compensatory measures have been implemented. This condition has existed since the plant was constructed. Neither the original design criteria nor any industry standards in effect at the time accounted for the possibility of the multiple short-to-ground failure mode and therefore, did not require overcurrent protection for remote ammeter circuits. This condition was documented in the station's corrective action program. Compensatory measures were established to restore margin potentially reduced by postulated fire scenarios. The compensatory actions credit operator presence in the plant for maintaining heightened awareness and taking action to minimize fire hazards. Compensatory actions are incorporated in pertinent operating procedures. The compensatory actions remain in effect. There have been no actual adverse safety consequences resulting from the reported condition. The administrative controls of the fire protection program, the availability of fire detection and suppression systems, and a trained on-site fire brigade all combine to make it highly unlikely that a fire could occur and progress in a manner that actually leads to the event postulated in this scenario.
4582014002 | River Bend | 10/17/2014 | 12/16/2014 | ML15006A02 | <strong>Reactor Scram due to Average Power Range Monitor High-flux Signal Following a Malfunction of the Main Turbine Electro-hydraulic System</strong><br /><i>Abstract:&nbsp;</i>On October 17, 2014, at approximately 3:03 a.m. CDT, a reactor scram occurred in response to a high neutron flux signal from the average power range monitors (APRMs). The plant was operating at 100 percent power at the time. Immediately prior to that signal, an apparent malfunction in the main turbine electro-hydraulic control (EHC) system caused both the main turbine steam bypass valves to fully open, and also commanded all four main turbine control valves to close. The resulting increase in reactor steam pressure caused reactor power to immediately rise to the trip setpoint of the APRMs, at which point the actuation of the reactor protection system (RPS) occurred. After the scram occurred, an operator in the auxiliary control room erroneously removed all the main condensate system demineralizers from service, isolating condensate flow to the suction header of the main feedwater pumps. The running feedwater pump tripped on low suction pressure. The mis-operation of the demineralizer system was promptly corrected, and the main feedwater system was restored to service. The cause of the EHC malfunction has not been determined. Potential failure points were identified, and those circuitry parts were replaced. A human performance error review was conducted regarding the mis-operation of the condensate demineralizers, and appropriate procedure revisions have been made. This event is being reported in accordance with 10CFR50.73(a)(2)(iv) as an automatic actuation of the RPS system.
4582014002 | River Bend | 10/17/2014 | 08/17/2016 | ML16235A48 | <strong>Reactor Scram due to Average Power Range Monitor High-flux Signal Following a Malfunction of the Main Turbine Electro-hydraulic System</strong><br /><i>Abstract:&nbsp;</i>On October 17, 2014, at approximately 3:03 a.m. CDT, a reactor scram occurred in response to a high neutron flux signal from the average power range monitors ( APRMs ). The plant was operating at 100 percent power at the time. Immediately prior to that signal, an apparent malfunction in the main turbine electro-hydraulic control (EHC) system caused both the main turbine steam bypass valves to fully open, and also commanded all four main turbine control valves to close. The resulting increase in reactor steam pressure caused reactor power to immediately rise to the trip setpoint of the APRMs, at which point the actuation of the reactor protection system (RPS) occurred. After the scram occurred, an operator in the auxiliary control room erroneously removed all the main condensate system demineralizers from service, isolating condensate flow to the suction header of the main feedwater pumps. The running feedwater pump tripped on low suction pressure. The mis-operation of the demineralizer system was promptly corrected, and the main feedwater system was restored to service. The cause of the EHC malfunction has not been determined. Potential failure points were identified, and those circuitry parts were replaced. A human performance error review was conducted regarding the mis-operation of the condensate deminerlizers, and appropriate procedure revisions have been made. This event is being reported in accordance with 10CFR50.73(a)(2)(iv) as an automatic actuation of the RPS system, and in accordance with 10CFR50.73(a)(2)(v) as a condition that potentially caused the loss of safety function of the affected RPS instruments.
4582014003 | River Bend | 06/10/2014 | 10/13/2015 | ML15300A26 | <strong>Operations Prohibited by Technical Specifications due to Concurrent Inoperability of Reactor Protection System Channels</strong><br /><i>Abstract:&nbsp;</i>On June 10, 2014, with the plant operating at 100 percent power, technicians performing a scheduled surveillance test found that one instrument channel in the reactor protection system failed its time response acceptance criterion. This was the second of two such tests that failed in similar fashion. Since it is conceivable that the second tested channel was out of specifications at the time the first channel was tested, this condition caused independent redundant channels in the same trip system to be inoperable at the same time. The actions required by the applicable Limiting Condition for Operation were not taken since the operators were not aware of the latent condition at the time of the first surveillance test failure. This condition is reportable in accordance with 10CFR50.73(a)(2)(i)(b) as operations prohibited by Technical Specifications, as well as 10CFR50.73(a)(2)(vii), a potential common-cause inoperability of independent trip channels. Due to the design redundancy of the independent channels of the RPS system, this condition would not have prevented the system from performing its safety function. Had an actual field MSIV isolation occurred with the channel response times in their as-found condition, the reactor scram signal would have still occurred within the specified instrument response time. The investigation of this event determined that the response time test failures were not caused by failed or degraded relays outside of the current design. Due to the design release time of the Agastat relays, the MSIV closure / RPS trip circuits could exceed the TRM acceptance criterion even if all relays in the circuit operated within design specifications. It was confirmed that this condition affected only the four channels containing Agastat relays. An analysis of the affected scram function determined that a change in the acceptance criterion 0.09 seconds to 0.15 seconds is justified. That change is being implemented in accordance with station procedures,
4582014004 | River Bend | 07/30/2014 | 09/26/2014 | ML14294A73 | <strong>Unanalyzed Condition of the Ultimate Heat Sink that Degraded its Ability to Perform its Design Safety Function due to Water Inventory Less than Requirement of Accident Analsyis</strong><br /><i>Abstract:&nbsp;</i>On July 30, 2014, with the plant operating at 100% power, a review of an engineering analysis of the ultimate heat sink (UHS) determined that the UHS was in an unanalyzed condition that degraded plant safety. This condition was the result of a design basis deficiency for the UHS that did not account for the adverse effects of system leakage on compliance with the 30-day inventory required by Regulatory Guide 1.27. The system design basis requires that 30-day inventory be maintained, with the assumption that no replenishment of the UHS inventory occurs for the entire duration of the postulated event. In support of the development of the engineering analysis, compensatory measures have been implemented which provide adequate assurance that the UHS will perform its design safety function. Corrective actions to restore full compliance with design basis requirements are in development. This event is being reported in accordance with 10 CFR 50.73 (a)(2)(ii) as an unanalyzed condition that degrades the safety function of the UHS.
4582014005 | River Bend | 08/01/2014 | 09/26/2014 | ML14294A73 | <strong>Loss of High Pressure Core Spray / Suppression Pool Safety Functions and Operations Prohibited by Technical Specifications due to Leakage through Pump Test Return Line</strong><br /><i>Abstract:&nbsp;</i>On August 1, 2014, at approximately 9:42 p.m. CDT, with the plant operating at 100 percent power, the high pressure core spray (HPCS) system was declared to be inoperable as a result of an engineering evaluation of an apparent leakage path through a part of the system. The evaluation determined that, should the HPCS system be initiated in response to a design basis event, the leakage path through a pump test return line to the condensate storage tank (the symptoms of which were first seen on July 12) could potentially cause the suppression pool inventory to be depleted to the extent that the pool would not support its 30-day mission time assumed in the station's accident analysis. Operators closed the HPCS pump suction valve at the suppression pool on August 1, resulting in the inoperability of the system. This event is being reported in accordance with 10 CFR 50.73(a)(2)(v) as a condition that defeated the safety function of the the HPCS system. A subsequent evaluation confirmed that, had the HPCS system actuated in response to a design basis event, the leakage through the pump test return line would have depleted the suppression pool inventory before the completion of its 30-day mission time. Regarding the suppression pool, this event constituted operations prohibited by Technical Specifications (10 CFR 50.73 (a)(2)(i)(b)), as well as a condition that defeated the safety function of the suppression pool (10 CFR 50.73 (a)(2)(v)). A blind flange was installed in the pump test return line to the condensate storage tank in order to isolate the leakage path, and the HPCS system was restored to an operable status on August 5. Repairs on the test return line isolation valves are scheduled.
4582014006 | River Bend | 12/25/2014 | 02/19/2015 | ML15055A57 | <strong>Automatic Reactor Scram and Primary Containment Isolation due to Loss of Power on the Division 2 Reactor Protection System with a Concurrent Division 1 Half-scram</strong><br /><i>Abstract:&nbsp;</i>On December 25, 2014, at 0836 CST, a reactor scram occurred while the plant was operating at approximately 85 percent power. This event resulted from the loss of power on the Division 2 reactor protection system (RPS) bus, in conjunction with a pre-existing halfscram on Division 1. The loss of Division 2 RPS power also resulted in a Division 2 containment isolation signal. Approximately four minutes after the scram, reactor water level increased to the Level 8 setpoint, causing the running main feedwater pump to trip. As reactor water level decreased back through the normal operating range, operators attempted to re-start main feedwater pump "C," but its supply breaker failed to close. Main feedwater pump "A" was subsequently returned to service. As reactor water level decreased to the point at which the startup feedwater regulating valve (FRV) should have opened to establish automatic control, the valve failed to open. Attempts to open it with a manual input signal were unsuccessful, and the "C" main FRV was put back into service. By that time, reactor water level had decreased slightly below the Level 3 RPS actuation setpoint, resulting in a second scram signal. This event is being reported in accordance with 10 CFR 50.73(a)(2)(iv)(A) as an automatic actuation of the RPS system and the primary containment isolation logic. No plant parameters required the actuation of any standby diesel generators or emergency core cooling systems. No reactor safety-relief valves actuated. This event was of minimal safety significance with respect to the health and safety of the public.
4612014001 | Clinton 1 | 01/22/2014 | 03/20/2014 | ML14091A24 | <strong>Premature Failure of Air Supply Solenoid Results in Isolation of Fuel Building Ventilation System and Loss of Secondary Containment Differential Pressure</strong><br /><i>Abstract:&nbsp;</i>On 1/22/14, the plant was at 97 percent reactor power and operators were placing Main Control Room Ventilation (VC) system Train B in service. While starting the VC Train B supply fan, operators received unexpected alarms caused by the trip of the in-service Fuel Building Ventilation system (VF) supply fan with the Fuel Building and Secondary Containment (SC) differential pressures (d/p) no longer being maintained negative, as required. In response to the loss of SC d/p, operators entered Emergency Operating Procedure (EOP) - 8, SC Control, declared SC inoperable, and entered the Technical Specification Actions. Troubleshooting and circuit analysis identified that the power source for VF inboard exhaust isolation damper also includes VC system supply air B zone isolation dampers and return air B dampers. During start of the VC system B train, the VC system dampers cycled and the VF system inboard exhaust isolation damper closed. The cause of this event was a prematurely degraded VF exhaust isolation damper air supply solenoid that responded to a minor perturbation of supply voltage or surge of current on the bus by dropping out during the VC Train B startup resulting in isolation of the VF system inboard exhaust isolation damper and a VF system trip. The prematurely degraded solenoid has been replaced. The VF system damper failed closed, fulfilling its safety function.
4612014002 | Clinton 1 | 03/25/2014 | 05/22/2014 | ML14163A12 | <strong>Lowering Condenser Vacuum due to B Train Steam Jet Air Ejector Instability Results in Manual Reactor Scram</strong><br /><i>Abstract:&nbsp;</i>On 3/25/14 the plant was in Mode 1, steady state at 85 percent reactor power. Operators in the Main Control Room (MCR) observed Offgas (OG) flow rate lowering, condenser vacuum lowering, and condensate water temperature rising. The 13' Steam Jet Air Ejector (SJAE) was in service at the time. As condenser vacuum lowered from 29 inches Mercury (Hg) to 27.4 inches Hg, Operators entered the Loss of Vacuum off-normal procedure and commenced a rapid power reduction. While reducing power, the MCR team began preparations to place the 'A' SJAE in service. At 1942 hours with Reactor power at 46 percent and vacuum at 24 inches Hg and lowering, Operators placed the Mode Switch in shutdown. All control rods were fully inserted. The plant responded as expected with no complications. No safety systems actuations occurred nor were required to place the plant in a safe and stable condition. The cause for this event is unstable pressure control of B SJAE due to a system resonance or instability. The root cause of the system resonance is indeterminate at this time pending additional testing. Corrective action for this event includes replacing the SJAE pressure controller and developing a comprehensive test plan that will dampen or eliminate the system resonance.
4612014003 | Clinton 1 | 06/22/2014 | 09/12/2014 | ML14276A03 | <strong>Misapplication of Support System Technical Specification Requirements Resulted in Implementation of Non-Conservative Guidance for Removal of Essential Switchgear Heat Removal System from Service</strong><br /><i>Abstract:&nbsp;</i>On 6/22/14, during a planned outage of the Division 1 Essential Switchgear Heat Removal (VX) system, the NRC questioned the practice of entering the actions of the station Operational Requirements Manual (ORM) 2.4.9 for VX when the VX system is inoperable without entering any Technical Specification (TS) Limiting Condition for Operation (LCO) Conditions and Required Actions for the systems the VX system supports. As a result of the question and until the station resolved the acceptability of the practice, Operations issued Night Order 2014-04 on 6/27/14, to direct operators to declare the following systems inoperable any time a safety-related divisional VX system is not functional in its ability to maintain area temperatures: Divisional DC Sources (TS LCOs 3.8.4 and 3.8.5); Divisional Inverters (TS LCOs 3.8.7 and 3.8.8); and Electrical Power Distribution Systems (TS LCOs 3.8.9 and 3.8.10). On 7/17/14 during investigation of this issue, the station determined that TS LCO 3.8.4 and TS LCO 3.8.9 should have been entered on 6/22/14 and the LCO limits were exceeded. The cause of this event was misapplication of support system TS Requirements to the non-TS VX system which resulted in implementation of non-conservative guidance for removal of the VX system from service. Corrective action includes revising the ORM, TS Bases, and reinforcing the definition of operable-operability.
4612014005 | Clinton 1 | 09/16/2014 | 12/31/2015 | ML16006A04 | <strong>Failure of Shutdown Service Water Pump Results in Loss of Division 3 Emergency Diesel Generator and High Pressure Core Spray Safety Functions</strong><br /><i>Abstract:&nbsp;</i>On 9/16/14 during Division 3 operability testing of the Division 3 Shutdown Service Water (SX) pump, the pump was started and motor thermal overload protection tripped off the pump after 36 seconds. There was no evidence the pump had rotated. Operators immediately declared the Division 3 SX system, the Division 3 Emergency Diesel Generator, and the High Pressure Core Spray system inoperable due to the pump trip as required by Technical Specifications. The cause of the pump failure to start was a failure of the suction bell bushing assembly. Failure of the suction bell bushing assembly would have occurred during the previous successful run of 1SX01PC on 5/30/14, resulting in 109 days with the Division 3 SX pump inoperable, which is beyond the Limiting Condition for Operation (LCO) Required Action Completion Time of 14 days to restore HPCS. This resulted in a condition prohibited by Technical Specifications. The root cause is the procedures used to develop plant modification change packages contained an inadequate process to identify the need for further reviews and the level of design detail required by those reviews. A new pump has been installed and the pump was restored to operable status on 9/21/14. An eight-hour ENS notification (#50463) was made at 2220 CDT on 9/16/14. This event is reportable under 10CFR50.73(a)(2)(i)(B) and 10CFR50.73(a)(2)(v)(D).
4822014001 | Wolf Creek | 01/06/2014 | 03/06/2014 | ML14071A30 | <strong>Failure to Comply With Required Action of Technical Specification 3.4.3 While Performing a Vacuum Fill of the Reactor Coolant System</strong><br /><i>Abstract:&nbsp;</i>During a review of outside operating experience it was discovered that the Wolf Creek Generating Station (WCGS) had been in violation of Technical Specification 3.4.3, "RCS Pressure and Temperature (P/T) Limits." Limiting Condition of Operation 3.4.3 requires the Reactor Coolant System (RCS) pressure, temperature and heatup and cooldown rates be maintained within the limits specified in the Pressure/Temperature Limits Report (PTLR) at all times. <br /><br /> WCGS draws a vacuum on the RCS at the end of refueling outages to fill the RCS using procedure SYS BB-112, "Vacuum Fill of the RCS." The RCS heatup and cooldown limitations in the PTLR only specify a pressure to 0 psig. A vacuum was drawn on the RCS two times during the past three years which was outside the limitations contained in the PTLR.<br /><br /> The apparent cause is inadequate engineering evaluation and procedure reviews resulted in allowing operations below the heatup and cooldown limitations specified in the PTLR. Procedure SYS BB-112 was cancelled to ensure a vacuum is not drawn on the RCS.
4822014003 | Wolf Creek | 04/20/2014 | 06/19/2014 | ML14175A12 | <strong>Failure of Safety Injection Accumulator Vent Line due to Low Stress - High Cycle Fatigue Results in Degraded Reactor Coolant Boundary</strong><br /><i>Abstract:&nbsp;</i>On April 20, 2014 at 1030 Central Daylight Time (CDT) during the Wolf Creek Generating Station (WCGS) Mid-Cycle Outage 20, a Health Physics technician observed water leaking approximately 2.5 gallons per hour from the 3/4-inch line upstream of Safety Injection (SI) system valve EPV0109. This is the 3/4-inch vent line on the combined Safety Injection and Residual Heat Removal (SI/RHR) outlet piping to SI Accumulator Tank 'D.'<br /><br /> The flawed socket weld and vent valve assembly was replaced with a like-for-like valve assembly on April 25, 2014. A hardware failure analysis (HFA) was performed on the failed portion of the vent line. The results of the analysis indicate the cause of the through-wall cracking to be low stress - high cycle fatigue.<br /><br /> The safety significance of this event is low. The Reactor Coolant System (RCS) leakage that resulted from the cracked vent line is within the capability of reactor makeup systems and a complete failure is bounded by the Loss of Coolant Accident (LOCA) analysis.
4822014004 | Wolf Creek | 06/02/2014 | 07/31/2014 | ML14224A01 | <strong>Condition Prohibited by Technical Specifications due to an Instrument Tunnel Sump Level Indication Transmitter Incompatible with the Containment Environment</strong><br /><i>Abstract:&nbsp;</i>On June 2, 2014, investigation of the erratic operation of the instrument tunnel sump level indication identified that the level indication had been inoperable from July 13, 2013 until November 20, 2013. As such, the Required Actions of Limiting Condition for Operation (LCO) 3.4.15, "RCS Leakage Detection Instrumentation," were not met. The event that led to this investigation was the identification that the instrument tunnel sump unidentified leak rate computer point was coming in and out of alarm high on May 28, 2014.<br /><br /> The apparent cause of the instrument tunnel sump level indication failure is the digital level transmitter design is not suitable for the instrument tunnel sump application. Compensatory measures were taken to maintain the capability of the instrument sump level indication to perform its specified function. Restoration of the instrument tunnel sump level transmitter from the degraded condition is being accomplished under the corrective action program.
4832014002 | Callaway | 01/14/2014 | 03/10/2014 | ML14069A49 | <strong>Operation Outside of Pressure and Temperature Limit Report Curve Required by Technical Specification 3.4.3</strong><br /><i>Abstract:&nbsp;</i>On January 14, 2014, with the plant operating in Mode 1 at 100 percent power, Callaway Energy Center (Callaway) discovered that on two occasions during the previous three years Condition C of Technical Specification (TS) 3.4.3, "RCS Pressure and Temperature (P/T) Limits," was not entered when the Reactor Coolant System (RCS) pressure was below zero pounds per square inch gage (psig). This occurred while the RCS was vacuum filled during both of the refuel outages at Callaway in the last three years. The Reactor Pressure/Temperature curves in the Callaway Pressure and Temperature Limits Report (PTLR) have a minimum pressure value of 0 psig referenced on the curve. Non-compliance with this limit, along with the failure to enter Condition C and meet its associated Required Actions, constitutes an operation or condition prohibited by the TS. <br /><br /> All systems performed as designed during the time that RCS pressure was below 0 psig over the previous three years. The cause for not entering TS 3.4.3 Condition C was the inaccurate perception that the PTLR curves only applied during RCS heatup or cooldown, and the reliance on an engineering evaluation of the RCS under vacuum conditions to allow continued operation.
4832014003 | Callaway | 06/09/2014 | 08/06/2015 | ML15218A56 | <strong>Inverter NN11 Inadvertantly Transferred to its Alternate AC Source</strong><br /><i>Abstract:&nbsp;</i>On 6/9/2014, during a maintenance activity, inverter NN11 unexpectedly transferred from its normal direct current (DC) source to its bypass alternating current (AC) source. This inverter provides power to the NN01 bus which is one of four vital 120-VAC instrument buses at Callaway Plant. In addition to other vital instrumentation, the bus provides power to cabinet SB038 which supports instrumentation and controls for systems such as the Reactor Trip System (RTS) and the Engineered Safety Feature Actuation System (ESFAS). <br /><br /> Investigation identified a loose mounting screw that secures disconnect switch NN01-11 to bus NN01. Maintenance work in the area of the loose termination led to a momentary interruption of power to cabinet SB038, which appeared as a fault condition to the inverter, thus causing the inverter to transfer to its alternate power source. The cabinet, bus, and inverter are seismically qualified and are required to be capable of performing their design basis accident mitigation functions following a Safe Shutdown Earthquake (SSE). Per Callaway's licensing basis, this capability is an Operability requirement. With the degraded electrical termination, which existed for an extended period of time before discovery and repair, the inverter and SB038 loads would not have been capable of performing their design basis function following an SSE, thus rendering the components inoperable. <br /><br /> The direct cause of this event was inadequate thread engagement of the screw securing the switch to the NN01 bus. Corrective actions include changes to job planning aids and maintenance procedures.
4832014005 | Callaway | 11/18/2014 | 08/06/2015 | ML15218A55 | <strong>All ECCS Accumulator Isolation Valve Operator Breakers Closed in Mode 3 With RCS Pressure Greater Than 1000 PSIG</strong><br /><i>Abstract:&nbsp;</i>On 11/18/2014, leak testing was being performed on the Emergency Core Cooling System (ECCS) Accumulator isolation valves (EPHV8878A, EPHV8878B, EPHV8878C and EPHV8878D) while the plant was in Mode 3 with Reactor Coolant System (RCS) pressure above 1000 psig. During the testing, the supply breakers for all four of the isolation valve motor operators were closed at 1734. This action had the unintended result of rendering the four ECCS Accumulators inoperable. The condition was identified at 1900, and Condition D under the Limiting Condition for Operation (LCO) of Technical Specification (TS) 3.5.1 was immediately entered. Per Required Action D.1, TS LCO 3.0.3 was immediately entered. By 1930, three ECCS Accumulators had been restored Operable with their isolation valves open and power removed from the isolation valve motor operators, and TS LCO 3.0.3 was exited. <br /><br /> The cause of this event was the failure of Operations personnel to comply verbatim with the leak testing procedure. Requirements for verbatim compliance with Continuous Use procedures have been reinforced within the Operations Department. The leak testing procedure has been revised to clearly specify that removal of power from the isolation valve motor operator is required for Operability of each ECCS Accumulator during the Modes of applicability for TS LCO 3.5.1.
4832014006 | Callaway | 12/03/2014 | 02/01/2015 | ML15033A21 | <strong>Main Generator Excitation Transformer Faulted to Ground, Causing Turbine and Reactor Trip</strong><br /><i>Abstract:&nbsp;</i>At 00:22 hours on December 3, 2014, during normal power operations, A turbine and reactor trip occurred, when the main generator excitation transformer faulted to ground. The reactor trip was classified as "uncomplicated." Safety systems performed as designed. During recovery the valve providing flow from Motor Driven Auxiliary Feedwater Pump "B" to Steam Generator "D" failed to throttle closed afterwards. Repair of the excitation transformer was completed and the plant returned to power operations on December 6, 2014.<br /><br /> The construction of the excitation transformer includes high voltage jumper cables between termination points inside its protective enclosure and the winding taps of the transformer coils. These jumper cables are routed above the iron core of the transformer and are supported by insulating boards as well as restrained by nylon cable ties. The fault to ground was caused when a jumper cable dropped onto the iron transformer core after failure of the nylon cable ties. These cable ties were an original part of the transformer installed in 2007.<br /><br /> The root cause of the transformer failure was inadequate design (routing cables above the transformer core) and material selection (use of nylon cable ties) during the manufacture of the transformer.
4982014001 | South Texas 1 | 01/23/2014 | 04/30/2014 | ML14135A19 | <strong>South Texas Project (STP) Unit 1 Overpower Condition Relating to the Ultrasonic Flow Measurement System</strong><br /><i>Abstract:&nbsp;</i>This LER Supplement is being submitted to provide an update regarding the evaluations being performed pertaining the overpower event, and to inform the Nuclear Regulatory Commission (NRC) that a second supplement will be submitted June 24, 2014.<br /><br /> The initial LER reported an event that occurred in South Texas Project (STP) Unit 1. It was discovered that the ultrasonic flow Feedwater correction factors had been trending in a non-conservative direction since installation resulting in an overpower of approximately 1.8% (max) for the period of 2.5 years. Pipe wall thickness measurements were then taken in the Unit 1 Feedwater piping in the vicinity of the Ultrasonic Flow Measurement System (UTF), and it was determined that pipe wall thicknesses were less than the original values resulting in increased flow diameters. The overpower condition in Unit 1 resulted in reactor trip instrumentation being inoperable longer than allowed by Technical Specifications (TS), thus reportable under 50.73(a)(2)(i)(B) Condition prohibited by TS. The Root Cause for this event is that the STP License Amendment Request implementation process did not require a formal, documented review of plant specific requirements and recommendations from vendor supplied documents that are used as a basis for a license amendments. The corrective action to prevent recurrence of this event is to develop or revise a Licensing procedure accordingly to require a formalized, documented review.
4992014001 | South Texas 2 | 12/31/2013 | 03/17/2014 | ML14086A38 | <strong>Standby Diesel Generator 23 Essential Cooling Water Leak through the Wall of Aluminum-Bronze Pipe Nipple</strong><br /><i>Abstract:&nbsp;</i>On December 31, 2013, an approximately three gallon per minute Essential Cooling Water (ECW) leak was discovered on Standby Diesel Generator (SDG) 23 at a one-half inch aluminum-bronze threaded connection. The leak was first identified as a 60 drop per minute leak on November 6, 2013. A reportability review completed on January 16, 2014 determined that SDG 23 had been inoperable since the initial leak was discovered, resulting in a safety system inoperability duration of approximately 55 days, 12 hours, and 27 minutes.<br /><br /> This event is reportable under 10 CFR 50.73(a)(2)(i)(B) as a prohibited by Technical Specifications and under 10 CFR 50.73(a)(2)(v) as a condition that could have prevented the fulfillment of a safety function.<br /><br /> The risk significance of the event is considered to be very small. The leaking aluminum-bronze tee and nipple assembly for SDG 23 was replaced on December 31, 2013 and there was no additional damage to any safety-related equipment associated with this event. The event did not have an adverse effect on the health and safety of the public.<br /><br /> The cause of the failure was erosion of the aluminum-bronze nipple and tee assembly that led to a through-wall ECW leak. Corrective actions include the replacement of the remaining aluminum-bronze nipple and tee assemblies on the SDGs with stainless steel components.
5292014001 | Palo Verde 2 | 06/11/2014 | 12/19/2014 | ML14364A02 | <strong>Inoperable Essential Spray Pond Train due to Corrosion on the Diesel Generator Fuel Oil Cooler Cover</strong><br /><i>Abstract:&nbsp;</i>On June 6, 2014, following planned maintenance on the train A emergency diesel generator (EDG) fuel oil (FO) cooler, essential spray pond (ESP) system water leakage was found on the FO cooler upper cover. The FO cooler upper cover was replaced with a new cover and the EDG and ESP systems were returned to service. A visual inspection of the removed cover identified corrosion related degradation of the cast iron cover. On June 11, 2014, an engineering analysis was completed to determine the required minimum wall thickness for the pressure boundary of the FO cooler upper cover. Measurements of the FO cooler upper cover wall thickness were found to be below the minimum wall thickness needed to maintain structural integrity for the full range of its design basis requirements. Consequently, it was determined the train A ESP system had been inoperable in excess of the completion time allowed by TS LCO 3.7.8. On June 28 and 29, 2014, the remaining five FO cooler upper covers (trains A and B for Units 1 and 3 and train B for Unit 2) were replaced with new covers.<br /><br /> The root cause of this event was latent design characteristics of the EDG FO cooler that resulted in a localized area in the cooler cover that was susceptible to galvanic corrosion. To prevent recurrence, a design modification will be implemented to remove the EDG FO cooler design function and isolate or remove the related ESP supply piping for the FO cooler.<br /><br /> No previous similar events have been reported to the NRC by PVNGS in the prior three years.
5292014002 | Palo Verde 2 | 11/06/2014 | 04/21/2015 | ML15117A01 | <strong>Technical Specification (TS) Required Plant Shutdown due to a Dropped Control Element Assembly</strong><br /><i>Abstract:&nbsp;</i>On November 6, 2014, at approximately 1116 Mountain Standard Time, Unit 2 was in Mode 1, 100 percent power, when control element assembly (CEA) 15 dropped fully into the core while the 88 other CEAs remained fully withdrawn. Operations entered Technical Specification (TS) Limiting Condition for Operation (LCO) 3.1.5, Condition A, for one CEA misaligned from its group which requires a power reduction and restoration of CEA alignment. An initial power reduction was performed in accordance with TSs and attempts to repair the problem were initiated. The CEA could not be aligned within the 2 hour TS time limit and TS LCO 3.1.5, Condition C was entered at 1316 which required entry into Mode 3 within 6 hours. The power reduction was continued and the reactor was manually shutdown at 1636 to comply with TSs.<br /><br /> The direct cause of the event was a failed upper gripper coil on the control element drive mechanism (CEDM) for CEA 15. The failed coil was replaced and Unit 2 was restarted and entered Mode 1 at 0332 on November 13, 2014. Operation of the coil at elevated temperatures accelerated thermal degradation of the coil insulation. A preventive maintenance strategy for establishing coil voltages and online CEDM coil monitoring, and adjustment, if necessary, was implemented.<br /><br /> In the previous 3 years, similar events related to malfunctions of control element drive mechanism control system equipment that resulted in a plant shutdown were reported in LERs 50-528/2011-004, 50-528/2011-005 and 50-530/2012-001.