## Sheet1
LER Number | Plant Name | Event Date | Report Date | Accession # | Title
2192018001 | Oyster Creek | 06/05/2018 | 07/31/2018 | ML18220A87 | <strong>EMRV Pressure Sensor As-Found Setting Exceeded Limiting Safety System Settings</strong><br /><i>Abstract:&nbsp;</i>While at full power steady state conditions, during calibration surveillance testing on 06/05/18, the 'A' Electromatic Relief Valve (EMRV) Pressure Switch (PS-IA0083A) as-found setpoint was at 1095 pounds per square inch, gauge (psig), which is above the Technical Specification (TS) Limiting Safety System Settings (LSSS) requirement of 1085 psig. The setpoint was immediately adjusted within an acceptable as-left band (within 38 minutes) using guidance in the surveillance test procedure. The cause of the condition was setpoint drift. <br /><br /> The TS Section 2.3.D LSSS values for Relief Valve Initiation are set to stagger relief valve opening for protection of the primary containment. The 'A' and 'C' EMRV LSSS are set at </= 1085 psig and 'B', 'D' and 'E' EMRV LSSS are set at </=1105 psig.<br /><br /> This occurrence is considered to have minimal safety significance as the primary containment structural integrity is bounded by Mark 1 Containment Long Term Program analyses and modifications which assume that all relief valves actuate simultaneously at 1105 psig. The Automatic Depressurization System (ADS) function of the EMRV is not affected by this pressure switch. None of the pressure switches for the remaining 4 EMRVs were affected, and manual operation of the EMRV was not affected.<br /><br /> This issue is reportable under 10 CFR 50.36(c)(1)(ii)(A) for Limiting Safety System Settings where an automatic safety system does not function as required (setting out of range) and 10 CFR 50.73(a)(2)(i)(B) as an operation or condition which was prohibited by the plant's TS.
2372018001 | Dresden 2, Dresden 3 | 02/12/2018 | 04/13/2018 | ML18107A21 | <strong>Non-conformances to Design for Tornado Missile Protection</strong><br /><i>Abstract:&nbsp;</i>On February 12, 2018, Dresden Nuclear Power Station identified a non-conforming condition with the three Emergency Diesel Generator Main Fuel Oil Storage Tank Vents with respect to tornado missile protection. All three Emergency Diesel Generators were declared inoperable. Compensatory measures were implemented and verified in accordance with the NRC Enforcement Guidance Memorandum (EGM) 15-002. All three Emergency Diesel Generators were returned to an operable but non-conforming status, and an eight-hour Event Notification was made to the NRC. This condition has been in existence since original plant design. It is not known if it was overlooked or considered acceptable at the time of the original licensing process. This event is reportable under 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by Technical Specifications, under 10 CFR 50.73(a)(2)(ii)(B) as an event that resulted in the plant being in an unanalyzed condition that significantly degraded plant safety, 10 CFR 50.73(a)(2)(v)(D) as an event or condition that could have prevented the fulfillment of a safety function of a system that is needed to mitigate the consequences of an accident; and 10 CFR 50.73(a)(2)(vii)(D) as an event where a single condition caused at least two independent trains to become inoperable in a single system designed to mitigate the consequences of an accident.
2442018001 | Ginna | 01/23/2018 | 03/23/2018 | ML18086A03 | <strong>Leakage in Reactor Coolant System Pressure Boundary Through an Existing Weld in Original Installation Equipment due to Orifice Wear/Erosion Resulting in Progressively Increasing System Vibrations</strong><br /><i>Abstract:&nbsp;</i>On January 23, 2018 a 0.015 gallon per minute (gpm) increase in unidentified Reactor Coolant System (RCS) Leakage was identified. A containment entry was performed on January 26, 2018 to identify the source of the leakage. A through-wall pinhole leak was identified in the Chemical and Volume Control System (CVCS) Normal Letdown line between AOV-200A (Letdown Orifice AOV-200A), and LCH01 (40 GPM Letdown Orifice Upstream of AOV-200A). The leak was found on the downstream weld of a socket welded elbow at the 10 o'clock position. CVCS Letdown was realigned to Excess Letdown and valve 543 was closed, isolating the leak. At that time, the leak was determined to be RCS pressure boundary leakage. The defective weld was subsequently removed and rewelding was performed to repair the pinhole leak. All repairs were done while the plant was on-line. The most probable cause was determined to be orifice wear/erosion from cavitation resulting in increasing system vibrations.<br /><br /> This event is reportable under 10CFR50.73(a)(2)(ii)(A) as a condition of the nuclear power plant, including its principal safety barriers, being seriously degraded; and under 10CFR50.73(a)(2)(i)(B) as any operation or condition which was prohibited by the plant's TS.
2442018002 | Ginna | 10/26/2018 | 12/20/2018 | ML18361A56 | <strong>Loss of Offsite Power to Vital Bus due to Human Error Causes Automatic Actuation of Emergency Diesel Generator "A"</strong><br /><i>Abstract:&nbsp;</i>On 10/26/2018 while in Mode 6, the 4160V 12A bus was manually deenergized during troubleshooting of the 52/12BY alternate supply breaker by Station Electricians. While racking out the 52/12BY breaker, an Electrician inadvertently pressed the close push button for 52/12BY instead of the trip push button. The 52/12BY breaker closed and the 52/12AY normal supply breaker opened through interlock. The Electrician did not hear the 52/12AY breaker open so thought it remained closed and that the potential for damage by paralleling power supplies out of phase existed. Intending to put the plant into a safe condition, the Electrician opened the 52/12BY breaker, deenergizing the 12A bus which was supplying 480V vital Busses 14 and 18. As designed, the "A" Emergency Diesel Generator started and supplied associated vital loads. The cause of the event was a human performance error by the Electrician. The electrical lineup was subsequently restored to its normal configuration by Station Operators.<br /><br /> This event is reportable under 10 CFR 50.73(a)(2)(iv)(A) as an event or condition that resulted in manual or automatic actuation of any of the systems listed in paragraph (a)(2)(iv)(B), specifically the "A" Emergency Diesel Generator.
2472018001 | Indian Point 2 | 03/31/2018 | 05/21/2018 | ML18149A12 | <strong>Penetration Indications Discovered During Reactor Pressure Vessel Head Inspection</strong><br /><i>Abstract:&nbsp;</i>On March 28, 2018, during the Indian Point Unit 2 Spring 2018 refueling outage (2R23), a white substance, indicative of reactor coolant leakage, was observed on the annulus region of reactor pressure vessel (RPV) head Penetration No. 3 while performing the visual testing (VT)-2 bare metal examination of the RPV head as required by American Society of Mechanical Engineering (ASME) Code Case N-729-4, as amended by the Nuclear Regulatory Commission (NRC) in 10 CFR 50.55a(g)(6)(ii)(D). No base material wastage was identified. <br /><br /> On March 31, 2018, liquid penetrant testing and eddy current testing of the partial penetration J-groove weld of RPV head Penetration No. 3 confirmed the presence of two relevant indications on the inside wetted surface of the J-groove weld. Both identified indications were determined to have lengths of approximately 0.085 inches. One of the two indications was characterized as being axially oriented with a measurable through-weld component, and it was concluded that this was the source of the reactor coolant leakage. The cause of the Penetration No. 3 indications was attributed to Primary Water Stress Corrosion Cracking (PWSCC) of the original Alloy 600 (Alloy 82/182) partial penetration J-groove weld. Penetration No. 3 was repaired in accordance with the NRC approved Westinghouse embedded flaw weld overlay method (WCAP-15987-P, Revision 2-P-A) and relief request IP2-ISI-RR-06. <br /><br /> This event had no effect on the public health and safety. The event was reported to the NRC on March 31, 2018 under 10 CFR 50.72(b)(3)(ii)(A) as a condition of the nuclear power plant, including its principal safety barriers, being degraded.
2472018002 | Indian Point 2 | 04/19/2018 | 06/18/2018 | ML18173A12 | <strong>Manual Reactor Trip due to Trip of Both Main Boiler Feedwater Pumps</strong><br /><i>Abstract:&nbsp;</i>On April 19, 2018, at 2100 hours, during initial plant startup following the Spring 2018 refueling outage (2R23), Indian Point Unit 2 commenced performance of the main turbine generator startup procedure to conduct turbine overspeed testing. At 2107 hours, the control room received main feedwater supervisory and panel alarms, and the main turbine control valves were observed to have opened rapidly. The unexpected rapid opening of the turbine control valves caused steam flow to increase, which in turn, caused all four steam generator water levels to swell. The high steam generator levels initiated an automatic main feedwater isolation and main turbine trip, with both Main Boiler Feedwater Pumps (MBFPs) tripping on closure of their discharge valves as part of the main feedwater isolation actuation. At 2108 hours, with reactor power at 8 percent and no MBFPs running, a manual reactor trip was inserted by the control board operators in accordance with the abnormal operating procedure for loss of main feedwater. All control rods fully inserted and all required safety systems functioned properly. The plant was stabilized in hot standby with decay heat being removed by the main condenser. The Auxiliary Feedwater System (AFWS) automatically started as expected on the tripping of the MBFPs to maintain steam generator inventory. The direct cause of the event was main turbine control oil stop valve LO-Z being out of its required position (closed instead of open). The root cause was main turbine generator startup procedure (2-SOP-26.4) provided a weak barrier to maintain the proper configuration of the main turbine control oil system. Corrective actions primarily involved the resolution of configuration control and management vulnerabilities. <br /><br /> This event had no effect on the public health and safety. The event was reported to the Nuclear Regulatory Commission on April 19, 2018 under 10 CFR 50.72(b)(2)(iv)(B) and 50.72(b)(3)(iv)(A).
2472018003 | Indian Point 2 | 10/28/2018 | 02/07/2020 | ML20050C99 | <strong>Loss of Safety Function due to Valve SWN-6 Actuator Failure During Service Water Header Swap</strong><br /><i>Abstract:&nbsp;</i>On October 28, 2018, Operations personnel were unable to fully close valve SWN-6 causing the Service Water System to be declared inoperable, and as a result, Operations entered Technical Specification (TS) Limiting Condition for Operation (LCO) 3.0.3. <br /><br /> This event occurred on October 28, 2018 at approximately 0930 Eastern Time with Unit 2 on-line at 100 percent power (Mode 1) and was identified by Operations personnel during a scheduled Essential Service Water header swap. TS LCO 3.0.3 was entered for a unit shutdown since the Service Water System (SWS) TS LCO 3.7.8 was not met during the header swap as the result of valve SWN-6 (Service Water 4-5-6 Header Supply to Turbine Building Oil Coolers) not stroking full closed. Valve SWN-7 (Service Water 1-2-3 Header Supply to Turbine Building Oil Coolers) had been successfully stroked full open as required. <br /><br /> Immediate removal of the valve SWN-6 actuator cover plate identified the worm gear roll/shear pin to be broken, which was the direct cause. The pin was replaced, allowing the valve to be cycled full closed and TS LCO 3.0.3 to be exited. A loss of SWS safety function was declared. This required an 8-hour report per 10 CFR 50.72(b)(3}(v}(B} and 10 CFR 50.72(b}(3}(v)(D). The root cause remains indeterminate due to the roll/shear pin being misplaced and lost and no interior valve inspection, but three possible causes have been identified: backed out roll/shear pin, binding in components, or inadequate preventive maintenance frequency.<br /><br /> There were no radiological or industrial safety impacts. The event had no effect on public health and safety. There were no human performance contributors to the event.
2502018001 | Turkey Point 3 | 09/28/2018 | 11/21/2018 | ML18325A20 | <strong>Inoperable Containment Purge Exhaust Penetration</strong><br /><i>Abstract:&nbsp;</i>On September 30, 2018, Turkey Point Unit 3 was in Mode 1 at 44% power, preparing for the Unit 3 Cycle 30 refueling outage. While performing the Technical Specification surveillance on the containment purge exhaust penetration, PEN 36, failed the as-found local leak rate test (LLRT) with a measurement of 21,000 standard cubic centimeters per minute (sccm), which exceeded the Technical Specification (TS) limit of 13,860 sccm. Review of maintenance history indicates evidence of a similar condition on 9/28/2018, with Unit 3 at 100% power, when a planned LLRT was aborted because of excessive time to achieve a stable test pressure. The containment purge exhaust penetration was inoperable from 9/28/18 at 0920 until 10/01/18 at 1425. Since PEN 36 was not isolated within 24 hours, TS 3.6.1.7, Action b was not met.<br /><br /> Corrective actions include seat adjustment for POV-3-2602, and seat replacement of POV-3-2603. This event is considered of very minor safety significance since the overall system capability was well within acceptable TS limits.
2502018002 | Turkey Point 3 | 09/30/2018 | 11/21/2018 | ML18325A20 | <strong>As-Found Cycle 29 Main Steam Safety Valve Setpoints Outside Technical Specification Limits</strong><br /><i>Abstract:&nbsp;</i>On September 30, 2018 Turkey Point Unit 3 was in Mode 1 and holding at approximately 44 percent reactor power while performing Technical Specification surveillance testing on the Main Steam Safety Valves (MSSVs) setpoints, just prior to the Unit 3 Cycle 30 Refueling Outage. <br /><br /> The Unit 3 C steam generator MSSV RV-3-1410 and B steam generator MSSV RV-3-1406 as found setpoints were below the Technical Specification allowable setpoint pressure of +/- 3% design pressure. All remaining MSSVs were tested as part of the required sample expansion. The as-found setpoint pressure of the B steam generator MSSVs RV-3-1407 and RV-3-1408, and C steam generator MSSV RV-3-1412 exceeded the +/- 3% design pressure. <br /><br /> The cause of the failure to meet TS allowable setpoints for RV-3-1410 and RV-3-1406 was attributed to setpoint drift due to minor spring relaxation. The cause of the failure to meet TS allowable setpoints for RV-3-1407, and RV-3-1408 was attributed to some form of friction or binding. RV-3-1410 and RV-3-1406 were adjusted to within +/-1% design pressure and returned to operable status. The cause of the failure to meet TS allowable setpoints for RV-3-1412 was attributed to setpoint variance. RV-3-1407, RV-3-1408, and RV-3-1412 were sent offsite for overhaul and replaced with four spares with as-left setpoints verified to be within the +/- 1% of design pressure as required by TS 3.7.1.1. <br /><br /> Operation of the facility with the MSSVs as-found settings was within analytical bounds; therefore, this event had no impact on the health and safety of the public.
2512018001 | Turkey Point 4 | 05/07/2018 | 06/27/2018 | ML18191B12 | <strong>Inoperable Auxiliary Feedwater Steam Supply Flowpath</strong><br /><i>Abstract:&nbsp;</i>On May 7, 2018 at 0049 while operating in Mode 1 at 100% power, Turkey Point Unit 4 experienced a failure of the steam generator A auxiliary feedwater (AFW) steam supply valve during preplanned surveillance testing. A review of the failure identified that it likely existed since the prior surveillance test on April 11, 2018. The resulting inoperability period of 26 days exceeded the seven-day allowed out of service time for an inoperable steam supply flowpath in Turkey Point Unit 4 Technical Specification (TS) 3.7.1.2, Auxiliary Feedwater System, resulting in a condition prohibited by TS. No adverse consequences resulted from this event. <br /><br /> The cause of the failure of the steam supply valve was disengagement of the torque arm from the stem key. With the torque arm disengaged from the key, the valve stem rotated and caused the geared limit switch settings for the motor operator to become out of sync with the valve travel. As a .result, the limit switches did not actuate at the expected set points. Corrective actions included repairing the torque arm, overhauling the motor-operator, resetting the limit switches, installing a set screw as a secondary restraint on the torque arm, and revising maintenance procedures to verify position and tightness of the torque arm or anti-rotation device during preventative maintenance activities.
2542018002 | Quad Cities 1, Quad Cities 2 | 03/01/2018 | 04/30/2018 | ML18120A15 | <strong>Tornado Missile Protection Non-Conformance in Association with EGM 15-002</strong><br /><i>Abstract:&nbsp;</i>On March 1, 2018, Quad Cities Nuclear Power Station (QCNPS) conservatively identified a non-conforming condition with the three Emergency Diesel Generators (EDG) intake stacks, exhaust stacks, and related fuel oil tank vents, with respect to tornado missile protection. Compensatory measures were implemented and verified in accordance with the NRC Enforcement Guidance Memorandum (EGM) 15-002, "Enforcement Discretion for Tornado-Generated Missile Protection Noncompliance," and DSS-ISG-2016-01, Revision 1, "Enforcement Discretion for Tornado-Generated Missile Protection Noncompliance." All three EDGs were returned to operable but non-conforming status in accordance with EGM 15-002 and DSS-ISG-2016-01 guidance, and an eight-hour Event Notification was made to the NRC. This condition is reportable under multiple reporting criteria in accordance with 10CFR50.73 requirements indicated above. This condition is a legacy issue that has existed since the original licensing of the plant. Due to the historic nature of this issue, a specific cause of the identified vulnerabilities was not determined. No actual consequences resulted from the nonconforming condition.
2542018003 | Quad Cities 1 | 06/09/2018 | 11/06/2018 | ML18313A03 | <strong>Two Reactor Protection System Channels Impacted by Single Main Stop Valve Limit Switch Failure</strong><br /><i>Abstract:&nbsp;</i>On June 9, 2018, at 1240 hours, Quad Cities Nuclear Power Station (QCNPS) main turbine Main Stop Valve number 1 (MSV1) failed to provide the appropriate Reactor Protection System (RPS) relay actuations during periodic surveillance activities. The associated limit switch failed to properly actuate relays in subchannels of both the A and B RPS Trip System channels. Operations entered Technical Specification (TS) 3.3.1.1. Condition B due to one inoperable channel in each trip system. <br /><br /> Fuses associated with the subchannels in both the A and B RPS channels were removed to meet the TS Action Statement. The limit switch was replaced on June 10, 2018, and associated RPS channels were tested satisfactory at 0538 hours. The cause of the switch failure was occasional binding due to inadequate lubrication during assembly by the manufacturer. <br /><br /> The safety significance of this event was minimal. The associated RPS logic requires signals from 3 of 4 valves, and the other 3 valves were providing proper signals per surveillance results. All other RPS inputs were functional. This report is submitted in accordance with the requirements of 10 CFR 50.73(a)(2)(vii) for a single condition that caused two independent channels to become inoperable in a single system designed to shut down the reactor and maintain it in a safe shutdown condition.
2542018004 | Quad Cities 1 | 09/26/2018 | 02/28/2019 | ML19059A03 | <strong>Reactor Scram due to Turbine-Generator Load Reject</strong><br /><i>Abstract:&nbsp;</i>On September 26, 2018 at 19:08, Quad Cities Unit 1 received an automatic Reactor SCRAM from 100% power. The SCRAM was the result of a Turbine-Generator Load Reject Trip that occurred when the status of the load reject contacts on one Unit Output Breaker was being tested while the other Unit Output Breaker was open. <br /><br /> The cause of the Turbine-Generator load reject trip was ineffective procedural controls for ensuring both unit output breakers were closed prior to performing contacts status verifications. The immediate corrective actions include procedure revisions to provide enhanced guidance for performing contact checks. <br /><br /> The issue is reportable under 10 CFR 50.73(a)(2)(iv)(A), any event or condition that resulted in manual or automatic actuation of any of the systems listed in paragraph (a)(2)(iv)(B).
2542018005 | Quad Cities 1 | 10/24/2018 | 11/21/2019 | ML19325C26 | <strong>Loss of Safety Bus and Automatic Actuation of a Safety System During Undervoltage Relay Surveillance</strong><br /><i>Abstract:&nbsp;</i>On 10/24/18 at 0901 CDT, during performance of the "Functional Test of Unit 1 Second Level Undervoltage," a loss of Bus 13-1 and Bus 18 occurred. The 1/2 Emergency Diesel Generator (EDG) automatically started due to a valid actuation on loss of power to Bus 13-1, but did not load due to surveillance test alignments. The loss of Bus 13-1 caused the loss Bus 18, resulting in a loss of logic power to both loops of Low Pressure Coolant Injection (LPCI). Additional equipment was also lost. <br /><br /> This notification is being made in accordance with 10 CFR 50.73(a)(2)(iv)(A), "Any event or condition that results in manual or automatic actuation of any of the systems listed in paragraph (a)(2)(iv)(B)," because the 1/2 EDG auto started due to the loss of power condition. This notification is also being made in accordance with 10 CFR 50.73(a)(2)(v)(B), "Any event or condition that could have prevented fulfillment of the safety function of structures or systems that are needed to remove residual heat," because both loops of LPCI were inoperable for a short time period.<br /><br /> The most probable cause is concurrent direct current (DC) grounds resulting in actuation of relay logic to trip Bus 13-1 and start the 1/2 EDG. Additional Q1R25 refuel outage troubleshooting was completed and did not reveal any additional causes.
2552018001 | Palisades | 05/03/2018 | 06/28/2018 | ML18180A02 | <strong>Safety Injection Inoperable for Longer Than Allowed by Technical Specifications due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On May 3, 2018, with the plant at 100% power, Entergy Nuclear Operations, Inc. (ENO) personnel were performing troubleshooting activities on the right train safety injection actuation indicating light. It was identified that wire 13 was not landed on the safety injection initiation relay circuit-2 (SIS-2) relay as required. This rendered the automatic initiation of right train safety injection inoperable and caused an entry into a 48-hour shutdown action statement. It was determined that the wire had been lifted, but not properly landed, during testing in the refueling outage eleven months prior. Consequently, the required actions and associated completion times of Technical Specification 3.3.4 were not met. <br /><br /> The wire was subsequently landed and operability restored. Additionally, during the period the right train was inoperable, the left train was inoperable on four occasions during the performance of quarterly surveillance testing, thus rendering both trains inoperable briefly. The root cause of this event was that post-test restoration of the electrical circuit on a safety significant system relied only on an administrative barrier and did not include a circuit check. <br /><br /> During the time of the right train automatic initiation inoperability, the components could have been manually actuated. Therefore, there were no consequences to the general safety of the public, nuclear safety, industrial safety or radiological safety for this event.
2552018003 | Palisades | 11/10/2018 | 07/29/2019 | ML19210D34 | <strong>Indications Identified in Reactor Pressure Vessel Head Nozzle Penetrations</strong><br /><i>Abstract:&nbsp;</i>On November 10, 2018, with the plant in Mode 6, during bare metal visual inspections of the reactor pressure vessel head (RPVH), dried boric acid was identified in the area of reactor head nozzle 25, indicative of a through-wall flaw. The flaw had not been identified during review of the original ultrasonic test (UT) data. During re-evaluation of the ultrasonic test (UT) data, analysts identified a leak-path indication and an axially oriented flaw characteristic of primary water stress corrosion cracking (PWSCC). As a result of the discovery in the UT data re-evaluation for reactor head nozzle 25, Framatome extended the UT characteristics to a re-evaluation of the data for the other relevant RPVH nozzles. This extent-of-condition review identified an additional four nozzles, 33, 34, 35, and 36, that required further review. UT analysis determined that reactor head nozzle 33 contained an indication consistent with PWSCC and that reactor head penetration 35 was acceptable. Supplemental eddy current testing (ECT) was performed on reactor head nozzles 34 and 36. ECT inspection of nozzle 34 did not reveal any PWSCC indications and was determined to be acceptable. ECT inspection of nozzle 36 revealed surface breaking PWSCC-type indications. <br /><br /> The plant was in cold shutdown at 0% power and Mode 6 for a refueling outage at the time of discovery. Reactor head nozzles 25, 33 and 36 were repaired and the RPVH was returned to service. The safety significance of this event was minimal. This event is reportable in accordance with 10 CFR 50.73(a)(2)(ii)(A) as a condition that resulted in a principle safety barrier being seriously degraded and 10 CFR 50.73(a)(2)(i)(B) for operation in a condition prohibited by Technical Specifications.
2592018002 | Browns Ferry 1 | 03/18/2018 | 05/17/2018 | ML18137A11 | <strong>Automatic Reactor Scram due to an Unanticipated Electro-Hydraulic Control Logic Condition</strong><br /><i>Abstract:&nbsp;</i>On March 18, 2018, at 1158 CDT the Brown Ferry Nuclear Plant Unit 1 reactor automatically scrammed due to a Reactor Protection System signal generated from an Average Power Range Monitor High Flux Trip in response to Turbine Control Valves (TCVs) closing to approximately 10 percent. Both megawatt input transducers on Unit 1 had been non-functional since January 22, 2018, which resulted in a "no generator load" input existing in the Electro-Hydraulic Control (EHC) system logic. On March 11, 2018, Operations personnel received an alarm which revealed that Battery Board 2 had a +230 V ground. The opening and subsequent closing of the Generator 1 Relay 250 V DC Supply breaker in support of the ground location activities resulted in a Generator Output breaker closed input. The combination of "no generator load" and "Generator Output breaker closed" signals resulted in the Initial Load Pickup Logic being met. The TCVs began to close to satisfy startup power limits, which resulted in a reactor trip. All safety systems functioned as designed. <br /><br /> The root cause investigation determined there was inadequate procedural guidance to assess operational impact(s) for digital logic inputs at the time equipment failures or faults occur (prior to entering the work management process). Both EHC megawatt input transducers were replaced prior to Unit 1 restart. The corrective action to prevent recurrence is to clarify operator responsibilities for the performance of operational impact review in procedures, including the development of a tool or checklist for operational impact reviews. As an interim action, a communication was issued to other TVA nuclear sites establishing that existing Operational Risk Review "Red Sheets" are to be utilized to evaluate operational impact prior to work activities.
2592018003 | Browns Ferry 1, Browns Ferry 2, Browns Ferry 3 | 03/29/2018 | 05/29/2018 | ML18149A49 | <strong>Unanalyzed Condition due to an Incorrectly Wired Breaker on Emergency Equipment Cooling Water Pump</strong><br /><i>Abstract:&nbsp;</i>On March 8, 2018, at 0130 Central Standard Time (CST), during a relay functional test of the C3 Emergency Equipment Cooling Water (EECW) Pump trip circuit, incorrect wiring was discovered on the C3 EECW Pump breaker. This condition would have prevented the breaker closing springs from recharging while the transfer switch was in the emergency position. On March 10, 2018, at 2042 CST, Maintenance personnel completed work to correct the wiring for the pump breaker. <br /><br /> On March 29, 2018, at 1344 Central Daylight Time (CDT), BFN Engineering determined that an unanalyzed condition, which significantly affected plant safety, had existed from October 28, 2015 to March 10, 2018. For postulated fire scenarios that could cause a Loss of Offsite Power and also result in Main Control Room Abandonment, the required EECW pumps utilized in the Fire Safe Shutdown procedure may not have been available. On March 29, 2018, at 2128 CDT, Event Notification # 53300 was made to the NRC. <br /><br /> The cause of this condition was a legacy human performance (HU) error involving a failure to properly utilize HU tools. Corrective actions were to correctly rewire the circuitry for the C3 EECW Pump breaker, and to revise plant procedures in order to add HU tools which verify, during testing, that the breaker springs will recharge while the transfer switch is in the emergency position.
2592018004 | Browns Ferry 1 | 07/09/2018 | 01/15/2019 | ML19015A07 | <strong>High Pressure Coolant Injection Declared Inoperable due to Steam Supply Valve Isolation</strong><br /><i>Abstract:&nbsp;</i>On July 9, 2018, during performance of surveillance procedure 1-SR-3.3.6.1.2(3B), High Pressure Coolant Injection System Steam Supply Low Pressure Functional Test, an unexpected High Pressure Coolant Injection (HPCI) isolation occurred. The isolation was discovered at 1111 Central Daylight Time (CDT) during a walkdown of the Unit 1 Control Room when the Unit Operator identified that the inboard and outboard HPCI steam supply valves were closed.<br /><br /> It was determined that the valves had closed at approximately 0958 CDT during performance of 1-SR-3.3.6.1.2(3B). Unit 1 entered Technical Specifications (TS) Limiting Condition for Operation (LCO) 3.5.1, ECCS - Operating, Condition C, at approximately 1111 CDT, which required restoring HPCI to operable status within 14 days and verification that Reactor Core Isolation Cooling (RCIC) is operable by administrative means. Following successful completion of the functional test, HPCI was placed in standby readiness lineup. The HPCI system was declared operable on July 10, 2018, at 1342 CDT. During the period of Primary Containment Isolation, the HPCI system was unable to perform its safety function. However, in an emergency, sufficient systems were available to provide the required safety functions. <br /><br /> The most likely cause of the unexpected HPCI isolation during performance of the HPCI test was determined to be past operation of the HPCI steam supply low pressure switches at an electrical current level near the manufacturer's rating, which resulted in degradation of the switch electrical contacts. The degradation eventually resulted in momentary arcing during functional testing of an adjacent switch, which energized the downstream logic relays causing Unit 1 HPCI to isolate. The corrective action for this event is to revise procedures 1/2/3-SR-3.3.6.1.2(3B) to lift a wire for the pressure switch under test and then re-land the wire prior to moving to the next pressure switch.
2592018005 | Browns Ferry 1, Browns Ferry 2 | 07/02/2018 | 08/31/2018 | ML18243A11 | <strong>Inoperability of Unit 1 and 2 Emergency Diesel Generators Results in Condition Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On July 2, 2018, at 1122 Central Daylight Time, it was discovered that the last performed surveillance on the C Emergency Diesel Generator (DG) Battery had recorded the specific gravity of Battery Cell 20 at 1.204. This was 0.025 less than the average battery cell specific gravity of 1.229. The difference in specific gravity between the individual cell and the average cell was more than the BFN Unit 1 and Unit 2 Technical Specifications (TS) Limiting Conditions for Operation (LCO) 3.8.6, Table 3.8.6-1, Category C, limit of 0.020. <br /><br /> On August 3, 2018, a past operability evaluation determined that, because of this condition, the C DG had been inoperable for longer than the LCO 3.8.1 Condition B, 14 day allowed outage time. Also, during this time, there were two periods where a second Unit 1 and 2 DG was inoperable for longer than the two hours allowed by TS LCO 3.8.1 Condition H for two or more concurrently inoperable Unit 1 and 2 DGs. This condition resulted in a violation of both Unit 1 and 2 TS. <br /><br /> The cause of this event is that the TS 3.8.6 Surveillance Requirement (SR) is non-conservative in regard to checking Category C limits. No SR is specified in TS 3.8.6 to check Category C limits. Corrective actions are to replace the battery cell, to issue an Operations Standing Order ensuring TS 3.8.6 Category C limits are met when quarterly SRs are performed on DG batteries, to revise battery SR procedures, and to revise Unit 1, 2, and 3 TS 3.8 to address the discrepancy between the SR and the TS 3.8.6 LCO Condition B required action.
2592018006 | Browns Ferry 1, Browns Ferry 2, Browns Ferry 3 | 10/06/2018 | 12/06/2018 | ML18340A15 | <strong>Standby Gas Treatment System Train C Inoperable Longer Than Allowed by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On October 6, 2018, at approximately 0001 Central Standard Time (CST), Standby Gas Treatment (SGT) System train C failed to automatically start in response to a Primary Containment Isolation signal which was received after Unit 3 was manually scrammed in support of the Unit 3 Cycle 6 forced outage. SGT train C was manually started. SGT trains A and B started automatically as expected. <br /><br /> On October 18, 2018, a Past Operability Evaluation determined that SGT Train C was inoperable for longer than the Unit 1, 2, and 3 Technical Specifications (TS) Limiting Condition of Operation (LCO) 3.6.4.3 seven day allowed outage time for a single inoperable SGT subsystem. The apparent cause of this event was the failure of a handswitch contact to close because of a loose cracked phenolic barrier plate inside the switch which impeded switch rotation. This crack was most likely the result of external forces on the switch and existed prior to the failure. <br /><br /> Corrective actions for this condition are to replace the failed handswitch, to replace all other handswitches affected by this condition, and to add a log note to the switch’s catalog ID to inspect new switches for barrier plate damage prior to installation.
2592018007 | Browns Ferry 1 | 12/12/2018 | 02/11/2019 | ML19042A15 | <strong>Main Steam Relief Valves Lift Settings Outside of Technical Specifications Required Setpoints</strong><br /><i>Abstract:&nbsp;</i>On December 12, 2018, the Tennessee Valley Authority was presented with as-found testing results indicating that two of the thirteen Main Steam Relief Valves (MSRVs) from Browns Ferry Nuclear Plant, Unit 1, were outside the +/- 3 percent setpoint band required for their operability. MSRV Line B failed 4.37 percent above its setpoint band and MSRV Line C failed 3.96 percent below its setpoint band. Troubleshooting determined that MSRV Line B disc failed above its setpoint band due to corrosion bonding to the valve seat as a result of its platinum anti corrosion coating flaking off. The valve discs were previously platinum coated to prevent this, and this was the first Unit 1 MSRV service interval to implement an improved surface treatment to prevent coating delamination. MSRV Line C failed below its setpoint band due to relaxation of the setpoint spring over time. <br /><br /> These two MSRVs were found to have been inoperable for an indeterminate period of time between November 2, 2016, and October 14, 2018, and longer than permitted by Technical Specifications. The affected valves remained capable of maintaining reactor pressure within American Society of Mechanical Engineers code limits. Additionally, the valves' ability to open under remote-manual operation, activation through the Automatic Depressurization System, or MSRV Automatic Actuation Logics was not affected. The valves remained capable of performing their required safety function. <br /><br /> All thirteen of the Unit 1 MSRV pilot valves were replaced with refurbished valves during the Unit 1 Refueling Outage 12. The corrective actions to preclude recurrence were to prepare the pilot discs for platinum coating in accordance with the revised procedure which required nitrogen pressure testing to verify valve seal functionality prior to coating. Additionally, the discs will be platinum coated, the setpoint spring for Pilot 1069 will be replaced, and the remaining springs will be tested and replaced, if necessary.
2612018001 | Robinson 2 | 11/19/2018 | 01/16/2019 | ML19016A08 | <strong>Valid Actuation of Emergency Diesel Generator</strong><br /><i>Abstract:&nbsp;</i>At 1916 hours eastern daylight time on 11/19/2018 with the plant in Mode 5, H. B. Robinson Steam Electric Plant, Unit No. 2 (HBRSEP2), experienced a valid actuation of the 'B' Emergency Diesel Generator (EDG) due to low voltage on the E2 Emergency Bus. <br /><br /> Subsequent investigation determined that during activities associated with a work order task, an E2 supply breaker tripped resulting in the automatic actuation of the 'B' EDG. Consequently, the 'B' Motor-Driven Auxiliary Feedwater pump (MDAFW) actuated due to logic associated with the E2 undervoltage signal. Normal E2 bus voltage supply was restored and 'B' EDG and 'B' MDAFW pump were secured. The direct cause of the EDG actuation was inadequate procedure adherence during maintenance activities. <br /><br /> The automatic actuations of the 'B' EDG and 'B' MDAFW pump are valid system actuations and are reportable in accordance with 10 CFR 50.73(a)(2)(iv)(A). There was no impact to the health and safety of the public as a result of this event.
2632018002 | Monticello | 12/20/2018 | 02/14/2019 | ML19046A00 | <strong>C Outboard Main Steam Isolation Valve Delayed Closure due to Foreign Material in the Air Valve</strong><br /><i>Abstract:&nbsp;</i>On November 16, 2018 at approximately 20:34 hours while operating in Mode 1 at 25% power, the plant was performing a functional test to demonstrate fast-closure of “C” Outboard Main Steam Isolation Valve (MSIV) AO-2-86C. The delay of the valve closure was caused by silicone based foreign material intrusion in the air solenoid valve body attributed to manufacturing of the air control assembly. The Monticello Nuclear Generating Plant (MNGP) Technical Specifications (TS) Surveillance Requirement (SR) 3.6.1.3.6 requires that the isolation time of each MSIV is >/= 3 seconds and </= 9.9 seconds. The “C” Outboard MSIV failed to close on the first attempt and failed stroke time acceptance criteria on the second closure attempt. During the second functional test the stroke time was measured at approximately 16 seconds. The valve was declared inoperable and subsequently repaired.<br /><br /> The component failure is reportable in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by TS 3.6.1.3 “Primary Containment Isolation Valves,” since “C” Outboard MSIV was inoperable for greater then the TS 3.6.1.3 Required Action A.1, Completion Time of 8 hours to isolate a main steam line, and the Completion Time for TS 3.6.1.3 Require Action F, to be in Mode 3 in 12 hours and Mode 4 in 36 hours when the completion time of A.1 is not met. There were no actual safety consequences that affect public health and safety associated with this condition since the primary containment isolation function was maintained. Additionally, this report also constitutes a 10 CFR Part 21 notification.
2652018001 | Quad Cities 2 | 03/19/2018 | 04/25/2019 | ML19115A14 | <strong>Two Main Steam Isolation Valves (MSIVs) Closure Times Exceeded</strong><br /><i>Abstract:&nbsp;</i>On March 19, 2018, during refueling outage Q2R24 at 0745 hours, the Unit 2 Main Steam Isolation Valve (MSIV) as-found closure time test results indicated that the closure time for two MSIVs exceeded the Technical Specification (TS) upper limit of less than or equal to five seconds. These two MSIVs were the inboard valves on the A and C Main Steam Lines. The safety significance of this event was minimal. <br /><br /> The cause of the slow closure timing events was due to an inadequate procedure on how to apply Super O-Lube to the valve stem bottom O-ring of the airpack manifold. <br /><br /> Corrective actions include replacement of the two air pack manifolds and revising the MSIV airpack manifold maintenance procedure regarding the amount of Super O-Lube to be applied. <br /><br /> This condition is being reported in accordance with 10 CFR 50.73(a)(2)(i)(B), which requires reporting of any operation or condition that was prohibited by the plant's TS.
2662018001 | Point Beach 1, Point Beach 2 | 03/01/2018 | 04/26/2018 | ML18116A14 | <strong>Inadequate Protection from Tornado Missiles Identified due to Nonconforming Conditions</strong><br /><i>Abstract:&nbsp;</i>On March 1, 2018, with Units 1 and 2 operating at 100% power, during evaluation of safe shutdown equipment for protection from the damaging effects of tornado missiles, Point Beach personnel initiated a condition report documenting a potential vulnerability for the turbine driven auxiliary feedwater pumps due to steam supply piping that is not routed through a Class I structure. Operations declared the affected equipment inoperable, implemented Enforcement Guidance Memorandum (EGM) 15-002, Enforcement Discretion for Tornado-Generated Missile Protection Noncompliance, Revision 1, and the required compensatory measures; and, returned the equipment to an operable-but-nonconforming status. <br /><br /> Subsequent to the condition identified on March 1, 2018, an extent of condition review documented additional equipment not fully protected by Class I structures, that are potentially vulnerable to tornado missiles. The additional equipment was declared inoperable, and returned to an operable-but-nonconforming status using EGM 15-002, Revision 1. <br /><br /> The identified nonconformances are legacy issues associated with the original plant design. Point Beach is pursuing a license amendment request to address tornado missile protection adequacy.
2692018001 | Oconee 1 | 04/13/2018 | 06/07/2018 | ML18165A14 | <strong>Unit 1 Manual Reactor Trip due to Main Feedwater Flow Control Valve E/P Converter Failures</strong><br /><i>Abstract:&nbsp;</i>On April 13, 2018 at 0227 hours, Oconee Unit 1 was manually tripped from 24% power. At the time of the trip, Unit 1 was in the process of a planned shutdown to repair a rod control cable connector and recover a dropped rod. The turbine was offline. While reducing power, problems were encountered such that power would no longer decrease. The main feedwater control valves (MFCVs) would not respond to automatic or manual control to close the MFCVs. An investigation revealed that the MFCVs would not go fully closed with a full closed demand signal from the Integrated Control System (ICS). The valves were subsequently tested and their electric to pneumatic (E/P) converters were found to be failed on the low end of calibration. The E/P converters failing in this manner caused the MFCVs to not go full closed despite the full closed demand signal from ICS. <br /><br /> This event was reported as a 4-hour notification to the NRC on April 13, 2018, in Event Notification (EN) number 53329 under 10 CFR 50.72(b)(2)(iv)(B) - Reactor Protection System (RPS) Actuation - Critical. The event is also reportable under 10 CFR 50.73(a)(2)(iv)(A) as an actuation of the RPS.
2692018002 | Oconee 1 | 10/19/2018 | 12/18/2018 | ML18362A14 | <strong>Loss of Condenser Vacuum Results in a Main Turbine Trip and a Manual Reactor Trip</strong><br /><i>Abstract:&nbsp;</i>On October 19, 2018, Oconee Unit 1 was in the process of shutting down to begin a scheduled refueling outage when auxiliary steam control valve 1AS-10 failed to open. At the time this occurred Unit 1 was at approximately 19% Rated Thermal Power (RTP) with the turbine-generator online. The failure of 1AS-10 caused a loss of Steam Seal Header (SSH) pressure which resulted in a decrease in condenser vacuum and a subsequent automatic turbine trip. Operators anticipated a loss of the operating Main Feedwater (MFW) pump and manually started both Motor Driven Emergency Feedwater (EFW) pumps (MDEFWPs). The cooler EFW flow entering both steam generators led to a 5.8% increase in reactor power. Operators manually tripped the reactor at approximately 25% RTP based on approaching the automatic trip of the last MFW pump at 19" Hg condenser vacuum which would have resulted in an automatic reactor trip.<br /><br /> The event was reported on October 19, 2018, via NRC Event Number 53677. This Licensee Event Report (LER) is required pursuant to 10 CFR 50.73(a)(2)(iv)(A) as a valid actuation of the Reactor Protection System (RPS) and EFW. <br /><br /> 1AS-10 failed to open because of age-related degradation of the positioner relay. It was determined that the Preventive Maintenance (PM) scope was inadequate. The positioner relay was replaced to correct the failure.
2722018001 | Salem 1, Salem 2 | 06/01/2018 | 07/26/2018 | ML18207A19 | <strong>Inadequate Protection from Tornado Missiles due to Nonconforming Design Conditions</strong><br /><i>Abstract:&nbsp;</i>On June 1, 2018, Unit 2 identified a nonconformance associated with tornado missile protection during development of a design change to minimize rainwater entry. Equipment required to be operable by Unit 2 technical specifications (TS) was affected and declared inoperable. Enforcement Guidance Memorandum (EGM) 15-002, "Enforcement Discretion for Tornado-Generated Missile Protection Noncompliance" was used to reclassify the affected equipment as operable but nonconforming. On June 18, 2018, Unit 1 identified a nonconformance associated with tornado missile protection during response to NRC Regulatory Issue Summary (RIS) 2015-06, "Tornado Missile Protection". Equipment required to be operable by Unit 1 TS was affected and declared inoperable. EGM 15-002 was again used to reclassify the affected equipment as operable but nonconforming. These were reported to the NRC within 8 hours. Additional nonconformances on both units have been identified and entered into the station corrective action process (CAP). The nonconformances will be resolved by license amendment or plant modification per EGM 15-002.
2772018001 | Peach Bottom 2, Peach Bottom 3 | 03/14/2018 | 05/11/2018 | ML18131A27 | <strong>Fire Safe Shutdown Requirements Not Met for Spurious Operation of Valves at a High-Low Pressure Interface</strong><br /><i>Abstract:&nbsp;</i>On 3/14/18, during a review of the Fire Protection Program Safe Shutdown Analyses, station personnel identified two valves that establish the boundary between a high pressure system and a low pressure system did not meet requirements contained in 10 CFR 50, Appendix R, Section III.G for protection against spurious operation during a fire. A flow path exists through the Reactor Water Cleanup (RWCU) System into the Reactor Core Isolation Cooling (RCIC) pump discharge line into the 'B' feedwater line and into the low-pressure piping for the feedwater recirculation line back to the main condenser. During a fire, the cables could be damaged in such a way that the power cable to the outermost valve could be reenergized and the valve could open. The second valve is also normally closed but could spuriously open. If the fire also caused three other isolation valves in the RWCU system to not close, a flow path to the main condenser could exist, resulting in a loss of reactor vessel water inventory. <br /><br /> This condition was not identified during the original analysis in the 1980's. There were no actual safety consequences as a result of this condition.
2772018002 | Peach Bottom 2, Peach Bottom 3 | 06/13/2018 | 03/04/2019 | ML19064B34 | <strong>Emergency Diesel Generator Air Inlet Check Valve Failure Results in a Condition Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On 6/13/18, during a surveillance test of the E-3 Emergency Diesel Generator, higher than normal engine temperatures were noted and abnormal noises were heard while running the engine at full load. The engine was shut down and troubleshooting initiated. Inspection of the turbocharger air inlet check valve discovered a pin used to hold the check valve disc in place was missing. The pin had become dislodged and had traveled to the turbocharger, where it caused damage to the rotating blades of the turbocharger. Repairs were performed and the diesel generator was placed back in service on 6/23/18. <br /><br /> Investigation of the failure determined that inadequate repairs during maintenance in April 2017 resulted in the pin loosening at certain engine loads. This event is being reported as required by 10CFR 50.73(a)(2)(i)(B). <br /><br /> There were no actual safety consequences as a result of this event.
2782018001 | Peach Bottom 3 | 04/22/2018 | 06/21/2018 | ML18172A26 | <strong>Reactor Core Isolation Cooling System Pressure Switch Failure Results in Condition Prohibited by TS</strong><br /><i>Abstract:&nbsp;</i>On 4/22/18, during a routine surveillance test of the Reactor Core Isolation Cooling (RCIC) system, the RCIC pump turbine tripped shortly after startup. The trip was the result of an indication of high pressure in the RCIC turbine discharge line. Troubleshooting determined that a pressure switch that monitors turbine exhaust pressure had failed. Actual exhaust pressure during the test was at the expected pressure of approximately 12 psig. <br /><br /> The pressure switch was replaced and the RCIC system was restored to an operable status on 4/23/18. There were no actual safety consequences as a result of this condition.
2782018002 | Peach Bottom 3 | 09/21/2018 | 12/21/2018 | ML19010A03 | <strong>Reactor Coolant System Pressure Boundary Leakage Resulting in Technical Specification Required Shutdown</strong><br /><i>Abstract:&nbsp;</i>On 9/21/18, the High Pressure Coolant Injection (HPCI) system was declared inoperable due to two inoperable differential pressure indicating switches that are used for isolating HPCI in the event of a break in the HPCI turbine steam line. A containment entry was made and it was determined that the instruments were incapable of performing their design function due to a leak on a one-inch diameter pressure sensing line. The line is a reactor coolant system pressure boundary, resulting in a Technical Specification required shutdown in order to repair. <br /><br /> The cause was determined to be vibration-induced fretting of the instrument line by a support bracket. The section of the pipe with the leak was replaced. <br /><br /> There were no actual safety consequences as a result of this event.
2782018003 | Peach Bottom 3 | 09/30/2018 | 11/29/2018 | ML18333A30 | <strong>Automatic Reactor Scram due to Loss of Two Condensate Pumps</strong><br /><i>Abstract:&nbsp;</i>On 9/30/18, an automatic reactor scram of Unit 3 occurred due to low reactor vessel water level following the loss of two condensate pumps. Plant equipment responded properly. The High Pressure Coolant Injection and Reactor Core Isolation Cooling systems automatically initiated on reactor low water level and restored level, in addition to the '3C' condensate pump and feedwater system. Reactor cooldown commenced in accordance with plant procedures. <br /><br /> The cause of the event was determined to be due to an electrical fault in the power cable for `3B' condensate pump and actuation of ground protective circuitry for the '3A' condensate pump. The electrical fault in power cables for the '3B' pump caused a ground current transient that raised the ground potential of the '3A' condensate pump transformer, resulting in a trip of the '3A' pump. Subsequently, power cables for the `3B' pump were replaced and ground circuitry for the '3A' pump was corrected to prevent such interaction.<br /><br /> There were no actual safety consequences as a result of this event. The '3C' condensate pump and reactor feedwater remained available for post-scram recovery.
2782018004 | Peach Bottom 3 | 10/01/2018 | 11/30/2018 | ML18334A03 | <strong>Failure of a Main Steam Isolation Valve to Fully Close</strong><br /><i>Abstract:&nbsp;</i>On 10/1/18 at approximately 12:32 pm, Main Steam Isolation Valves (MSIVs) were stroked closed in preparation for entering Mode 4. The Unit 3 'B' inboard MSIV, AO-3-01A-080B, gave a split indication and it was determined that the valve had stopped approximately 1 inch short of full closure. <br /><br /> Turbulent steam flow had caused vibration of the MSIV poppet, causing the poppet cap guide to wear against the anti-rotation lug, resulting in a notch in the poppet cap guide. During valve closure, the poppet traveled its normal path, but the last 1 inch of stem travel did not occur because the stem anti-rotation lug was caught in the notch, which prevented the stem from reaching the pilot seating surface. The stem and the poppet cap guide were replaced, and a modification was performed to stabilize the poppet to prevent recurrence.<br /><br /> There were no actual safety consequences as a result of this event. The Unit 3 outboard MSIV was operable for performing its containment isolation function.
2802018001 | Surry 1, Surry 2 | 01/17/2018 | 03/19/2018 | ML18085A15 | <strong>Loss of 4160 Volt Emergency Bus and Start of Emergency Diesel Generator due to Opening Emergency Bus Potential Transformer Drawer</strong><br /><i>Abstract:&nbsp;</i>On January 17, 2018, at 09:52 hours, with Units 1 and 2 at 100% power, the 1J emergency bus potential transformer drawer located inside the 1J 4160 V emergency bus undervoltage (UV) relaying cubicle was opened inadvertently, generating a 1J emergency bus UV signal. The signal-caused the normal 1J emergency bus supply breaker to open and also caused the automatic start of the #3 Emergency Diesel Generator (EDG). The #3 EDG energized the 1J emergency bus, and all 1J emergency bus loads were verified to be in correct alignment. <br /><br /> After proper re-installation of the bus potential transformer drawer was verified, normal alignment of the #3 EDG and normal alignment of the primary off-site power supply to the 1J emergency bus were reestablished. Both Units 1 and 2 remained at 100% power during the event. All equipment operated as designed. <br /><br /> It was determined that the Operations team, while reviewing an electrical tag-out walkdown task, did not adequately perceive and manage the risk of opening the 1J bus potential transformer drawer. Also, the operator who opened the drawer did not understand the impact to the UV sensing circuit by opening the bus potential transformer drawer. The condition was reported as an event or condition that results in a valid actuation of an emergency electrical power system, pursuant to 10 CFR 50.72(b)(3)(iv)(A). This event is being reported as an event or condition that results in a valid actuation of an emergency electrical power system, pursuant to 50.73(a)(2)(iv)(A).
2802018002 | Surry 1, Surry 2 | 10/11/2018 | 12/10/2018 | ML18351A08 | <strong>Windblowri Debris Caused Transformer Fault Resulting in Auto-Start of Emergency Diesel Generator</strong><br /><i>Abstract:&nbsp;</i>On October 11, 2018, at 23:04 hours, with Units 1 and 2 at 100% power, 'A' Reserve Station Service Transformer pilot wire lockout signal caused an undervoltage condition of the 1J emergency bus and the subsequent automatic start of the #3 Emergency Diesel Generator (EDG). The #3 EDG energized the 1J emergency bus loads as designed. At the time of the event, the site was experiencing rain and strong winds associated with Tropical Storm Michael. <br /><br /> On October 12, 2018, after the high winds had passed, inspections and functional tests determined that no repairs to the electrical service system were required. Normal alignment of the #3 EDG and the primary off-site power supply to the 1J emergency bus were reestablished within 24 hours. Both Units 1 and 2 remained at 100% power. All equipment operated as designed. <br /><br /> An eight-hour non-emergency event notification was made to the NRC pursuant to 10 CFR 50.72(b)(3)(iv)(A) due to a valid actuation of the #3 EDG. This report is being made pursuant to 10 CFR 50.73(a)(2)(iv)(A) due to a valid actuation of the #3 EDG.
2802018003 | Surry 1, Surry 2 | 11/12/2018 | 01/08/2019 | ML19016A13 | <strong>Auto-Start of Emergency Diesel Generators due to Pilot Wire Lockout on 'C' Reserve Station Service Transformer</strong><br /><i>Abstract:&nbsp;</i>On November 12, 2018, at 16:36 hours, with Unit 1 at 100% power and Unit 2 defueled, 'C' Reserve Station Service Transformer (RSST) pilot wire lockout actuated while energizing the underground feeder cables to the 'C' RSST following transformer replacement. While 'C' RSST replacement activities were ongoing, the Surry 1'H' and 2'J' emergency busses were supplied from the dependable alternate power supply, Unit 2 station service back-feed. The 'C' RSST lockout signal resulted in a partial loss of off-site power to the Unit 1'H' emergency bus and to the Unit 2'J' emergency bus. The #1 and #3 Emergency Diesel Generators (EDG) automatically started and loaded the 1'H' and 2'J' emergency buses, respectively, as designed. The Unit 1 Main Steam Power Operated Relief Valves (PORV) momentarily opened, however the Unit 1 power level was maintained at full power. No operational issues were experienced by Unit 2. Deficient workmanship in the surface preparation of the splice connection of an underground feeder cable caused the cable fault and lockout condition. Affected cable splices were replaced prior to returning the 'C' RSST to service. <br /><br /> An eight-hour non-emergency event notification was made to the NRC pursuant to 10 CFR 50.72(b)(3)(iv)(A) due to a valid actuation of the #1 EDG and the #3 EDG. This report is being made pursuant to 10 CFR 50.73(a)(2)(iv)(A) due to a valid actuation of the #1 EDG and the #3 EDG.
2822018001 | Prairie Island 1, Prairie Island 2 | 01/08/2018 | 03/07/2018 | ML18068A02 | <strong>121 Motor Driven Cooling Water Pump Auto Start due to Smoking Packing on 11 Cooling Water Pump</strong><br /><i>Abstract:&nbsp;</i>On January 8, 2018, Prairie Island Nuclear Generating Plant (PINGP) staff were running the 11 Cooling Water (CL) pump for post-maintenance testing. At 1437 CST, operators stopped 11 CL pump following a report from Maintenance staff that the inboard pump packing was smoking. Shortly after operators secured 11 CL pump the 121 Motor Driven Cooling Water Pump (MDCLP) auto-started and supplied the CL header. This event is reportable under 10 CFR 50.73(a)(2)(iv)(A) as an event that resulted in automatic actuation of an emergency service water system. <br /><br /> The cause of the 121 MDCLP auto-start was determined to be low CL header pressure after 11 CL pump was secured. Operators secured the 11 CL pump when they received the report that the inboard pump packing was smoking. Investigation found the most likely cause of the smoking pump packing was due to inadequate procedural guidance regarding packing replacement criteria
2862018001 | Indian Point 3 | 02/16/2018 | 04/16/2018 | ML18110A08 | <strong>Reactor Trip due to Main Generator Loss of Excitation</strong><br /><i>Abstract:&nbsp;</i>On February 16, 2018, at 0201 hours, with reactor power at 100 percent, Indian Point Unit 3 experienced an automatic reactor trip on a turbine trip, which was in response to a main generator trip. The main generator trip was initiated by actuation of the Generator Protection System due to a main generator loss of excitation. <br /><br /> All control rods fully inserted and all required safety systems functioned properly. The plant was stabilized in hot standby with decay heat being removed by the main condenser. The Auxiliary Feedwater System (AFWS) automatically started as expected on steam generator low level to provide feedwater flow to the steam generators. The plant was stabilized in hot standby with decay heat being removed by the main condenser. The direct cause of the loss of main generator excitation was the failure of an auctioneering diode (D8) in the Automatic Voltage Regulator Thyristor Firing Module A drawer power supply. The root cause was an improper refurbishment of obsolete Thyristor Firing Module power supplies. Corrective actions included modification of the Automatic Voltage Regulator to replace the obsolete power supplies with a new design, and creation of a Preventive Maintenance (PM) task to periodically replace the new power supplies in accordance with vendor recommendations and the PM Template.<br /><br /> This event had no effect on the public health and safety. The event was reported to the Nuclear Regulatory Commission on February 16, 2018 under 10 CFR 50.72(b)(2)(iv)(B) and 50.72(b)(3)(iv)(A) as an event that resulted in the automatic actuation of the Reactor Protection System when the reactor is critical and a valid actuation of the AFWS.
2862018002 | Indian Point 3 | 09/07/2018 | 11/05/2018 | ML18313A12 | <strong>Manual Reactor Shutdown due to Weld Leak in Safety Injection System Tank</strong><br /><i>Abstract:&nbsp;</i>On September 7, 2018 during a walkdown, an operator identified boron accumulation on a welded joint to a thermowell located on the Boron Injection Tank, which is a retired-in-place component in the safety injection system. Since the flaw could not be characterized by any available Non-Destructive Examination techniques due to the configuration of the weld, it was conservatively assumed that the weld was structurally unacceptable. This was postulated to result in ejection of the thermowell and a subsequent potential leakage rate that would render the safety injection pumps incapable of performing their functions during applicable design basis events. Additionally, the American Society of Mechanical Engineers (ASME) Section XI Code does not allow through-weld leakage in any Class 2 components. Therefore, at 1803 hours, with reactor power at 100 percent, shutdown of the plant was commenced in accordance with Technical Specification 3.0.3. The reactor was manually tripped at 2129 hours in accordance with normal shutdown procedures. <br /><br /> The Auxiliary Feedwater System was manually initiated to provide feedwater flow to the steam generators in preparation for reactor trip, and all control rods fully inserted and all required safety systems functioned properly. The plant was stabilized in hot standby with decay heat being removed by the main condenser. A plant modification removed and plugged the thermowell and a second identical thermowell on the tank.<br /><br /> This event had no effect on the public health and safety. The event was reported to the Nuclear Regulatory Commission (NRC) on September 7, 2018 under 10CFR50.72(b)2(i), 10CFR50.72(b)(3)(ii)(A), and 10CFR50.72(b)(3)(v)(D).
2862018003 | Indian Point 3 | 09/18/2018 | 11/19/2018 | ML18341A12 | <strong>Manual Reactor Trip due to a Steam Leak on a High Pressure Feedwater Heater</strong><br /><i>Abstract:&nbsp;</i>On September 18, 2018, with the reactor at 100 percent power, at approximately 0525 hours Operators manually tripped the reactor and shut the Main Steam Isolation Valves due to a steam leak on the 6 inch elbow located upstream of the 36C Feedwater Heater. The steam leak was due to a failure of the 6 inch elbow. The cause of the failure was flow accelerated corrosion which lead to pipe wall thinning and subsequent pipe failure. Ultrasonic testing of the elbow showed flow accelerated corrosion thinning in the failed elbow and also in the adjacent upstream elbow.<br /><br /> This event was reported under 10 CFR 50.72(b)(2)(iv)(B) for any event or condition that results in actuation of the reactor protection system when the reactor is critical. This event was also reportable under 10 CFR 50.72(b)(3)(iv)(A) for any event or condition that results in valid actuation of any of the systems listed in paragraph 10 CFR 50.72(b)(3)(iv)(B). This included actuation of the Auxiliary Feedwater System as expected following manual reactor trip. Following the reactor trip, the plant was stabilized in hot standby with decay heat being removed from the steam generators via the Auxiliary Feedwater System and atmospheric steam dumps. <br /><br /> This event had no effect on the public health and safety.
2872018001 | Oconee 3 | 04/20/2018 | 06/19/2018 | ML18176A02 | <strong>Two Main Steam Relief Valve Setpoints Found Out of Tolerance</strong><br /><i>Abstract:&nbsp;</i>On 4/20/18, prior to shutdown of Unit 3 for refueling, all 16 of the Unit 3 Main Steam Safety Valves, referred to as Main Steam Relief Valves (MSRV) at Oconee, were tested to satisfy Technical Specification (TS) Surveillance Requirement (SR) 3.7.1.1. The testing found that the as-found lift pressure for two valves was higher than allowed by SR 3.7.1.1. The remaining fourteen valves met the SR. Guidance from NUREG 1022 Revision 3 states "the existence of similar discrepancies in multiple valves is an indication that the discrepancies may well have arisen over a period of time and that...the condition existed during plant operation". Thus, the event is considered an operation or condition prohibited by TS and is reportable in accordance with 10 CFR 50.73(a)(2)(i)(B). <br /><br /> The causes of the MSRV test failures were determined to be a combination of setpoint drift and binding of spindle and upper spring washer. Although the lift pressures were.above the acceptance criteria, this condition is bounded by current safety analysis limits and assumptions.
2872018002 | Oconee 3 | 05/10/2018 | 10/25/2018 | ML18309A03 | <strong>Actuation of the Keowee Hydroelectric Station due to Loss of AC Power to the Unit 3 Main Feeder Buses</strong><br /><i>Abstract:&nbsp;</i>On May 10, 2018, at 16:03, with Unit 3 in MODE 6 (refueling) with the unit's startup transformer (CT-3) carrying the unit's power loads, a CT-3 lockout occurred. With the transformer locked out, Unit 3 experienced a loss of all alternating current (AC) power to the unit's main feeder buses (MFBs) which subsequently resulted in an autostart of both Keowee Hydroelectric Station (KHS) Units. Approximately 18 seconds later, emergency AC power was restored to the MFBs via the KHS Unit 2 underground powerpath and CT-4 transformer. During the 38-second power outage, the Unit 3 decay heat removal and spent fuel cooling systems were affected; however, the MFB Monitoring Panel responded as designed to restore AC power. <br /><br /> This event was reportable pursuant to 10 CFR 50.73(a)(2)(iv)(A) as a valid actuation of one of the systems listed in 10 CFR 50.73(a)(2)(iv)(B)(8), i.e., the Keowee Hydroelectric Station. Revision 1 of this LER reports a similar invalid actuation of KHS Unit 2 that occurred on May 7, 2018, while Oconee Unit 3 was in MODE 6 and CT-3 was not carrying any station loads. <br /><br /> The cause of the CT-3 lockouts was due to transient disturbances from external voltages/currents being impressed upon the direct current (DC) system due to an internal failure of the 62GZ relay concurrent with DC grounds. Corrective actions included 62GZ relay replacement and repair of DC grounds.
2932018001 | Pilgrim | 01/04/2018 | 03/05/2018 | ML18079A10 | <strong>Manual Reactor Scram due to Loss of One Offsite Transmission Line</strong><br /><i>Abstract:&nbsp;</i>On January 4, 2018 at approximately 1400 EST, with the reactor at approximately 100 percent core thermal power, Air Circuit Breakers 103 and 104 automatically opened due to a fault condition on 345KV Line 342. The sustained loss of one incoming 345KV line due to weather related conditions requires a plant shut down. While assessing plant conditions, the operating crew reduced reactor power to approximately 81 percent core thermal power. Following these actions, it was determined that the loss of 345KV Line 342 was due to weather and a manual scram was initiated at 1409 hours. <br /><br /> This event is reportable per the requirements of Title 10 Code of Federal Regulations 50.73(a)(2)(iv)(A) due to a manual actuation of the Reactor Protection System and automatic isolation signals affecting containment isolation valves in more than one system. <br /><br /> There was no impact to public health and safety.
2932018003 | Pilgrim | 01/26/2018 | 03/27/2018 | ML18093A38 | <strong>Target Rock Relief Valve Pilot Assembly Failed As-Found Lift Test, a Condition Prohibited by Plant Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On January 26, 2018, while operating at 100 percent core thermal power, Pilgrim Nuclear Power Station was notified that one of the four Target Rock Relief Valve Pilot Assemblies removed from the plant during the 2017 Refueling Outage exceeded the Technical Specification (TS) tolerance limit of 1155 ± 34.6 psig (± 3%) during routine testing at the offsite vendor's test facility. Certified replacement relief valve pilot assemblies were installed in the plant during the Spring 2017 Refueling Outage.<br /><br /> The cause of the as-found initial lift pressure exceeding the TS tolerance limit for the pilot valve was corrosion bonding. <br /><br /> This report is submitted in accordance with the requirements of Title 10 Code of Federal Regulations 50.73(a)(2)(i)(B), any operation or condition which was prohibited by plant Technical Specifications. <br /><br /> There were no adverse consequences for this event and the condition posed no threat to public health and safety because an evaluation of the as-found set pressures of the four relief valves concluded that no design or licensing basis limits would have been exceeded had the relief valve pilot assemblies been required to operate.
2932018004 | Pilgrim | 03/13/2018 | 05/14/2018 | ML18152A86 | <strong>2018-004-00, Automatic Emergency Diesel Generator System Actuation Caused by Loss of Offsite Power</strong><br /><i>Abstract:&nbsp;</i>On March 13, 2018 at approximately 10:02 am [EDT], with the reactor in Cold Shutdown, Pilgrim Nuclear Power Station experienced a loss of offsite power. The loss of both incoming 345KV lines to the Startup Transformer and the loss of the 23KV line to the Shutdown Transformer were due to weather related conditions associated with Winter Storm Skylar. The loss of offsite power lasted long enough for the associated Startup Transformer relay to transmit a valid auto start signal to both Emergency Diesel Generators and trip the non-safety related buses A1 through A4. There was minimal impact from this occurrence as the Emergency Diesel Generators had been started manually several hours prior to the auto start signal being received. The Emergency Diesel Generators were already providing power to the A5 and A6 Emergency Buses. <br /><br /> This event is reportable per the requirements of Title 10 Code of Federal Regulations 50.73(a)(2)(iv)(A) due to the receipt of a valid automatic start signal by the Emergency Diesel Generators. <br /><br /> There was no impact to public health and safety.
2932018005 | Pilgrim | 07/17/2018 | 09/12/2018 | ML18260A08 | <strong>Condition Prohibited by Technical Specifications Involving Standby Gas Treatment System Pneumatic Leakage Rate</strong><br /><i>Abstract:&nbsp;</i>On July 17, 2018, with the Reactor in the Run Mode at approximately 100 percent power, it was determined through review of current and historical data that pneumatic leakage in the system used to operate dampers caused Train 'B' of the Standby Gas Treatment System (SGTS) to be made inoperable. Subsequent review determined that the condition existed for a period of time longer than allowed by Technical Specifications. This has been determined to be a reportable condition involving the SGTS in accordance with Title 10 Code of Federal Regulations 50.73(a)(2)(i)(B). <br /><br /> A failure modes analysis was used to identify potential pneumatic air leakage paths and specific locations within the SGTS. Field work included leak checks, replacement of solenoid operated valves, repair of a damper actuator, and post-work testing of the system. SGTS Train 'B' was functioning properly but had a reduced mission time based on the as-found pneumatic system leakage rate. SGTS Train 'A' was operable during the period of time SGTS Train 'B' was inoperable. <br /><br /> This event had no impact on the health and/or safety of the public.
2932018006 | Pilgrim | 10/05/2018 | 11/29/2018 | ML18338A10 | <strong>Automatic Reactor Scram due to Feedwater Regulating Valve Malfunction</strong><br /><i>Abstract:&nbsp;</i>On October 5, 2018 at 1209 hours, with the reactor operating at 100% power, an automatic reactor scram occurred due to a reactor water level perturbation and receipt of a low reactor water level Reactor Protection System signal caused by a malfunction of the 'A' Feedwater Regulating Valve (FRV). <br /><br /> The Failure Modes Analysis attributed the probable cause to be an intermittent signal in the stepper motor and encoder control loop, which is the system that manipulates the pneumatic spool to operate the FRV's Double- Acting Piston Actuator. The as-found condition of the stepper motor and encoder electrical connectors showed that several pin sockets were not properly seated within their connector housings. Proper seating of the FRV stepper motor and encoder electrical connections is critical in ensuring error free operation of the FRVs. <br /><br /> There were no radiological releases due to this event. All control rods inserted fully. All other plant systems responded as designed. This event had no impact on the health and/or safety of the public. <br /><br /> This report is submitted in accordance with 10 CFR 50.73(a)(2)(iv)(A).
2962018001 | Browns Ferry 3 | 01/10/2018 | 03/12/2018 | ML18071A12 | <strong>Separated Pressure Switch Sensing Line Causes Unit 3 SCRAM</strong><br /><i>Abstract:&nbsp;</i>On January 10, 2018, at approximately 0926 Central Standard Time (CST), with Unit 3 at 74 percent power, Browns Ferry Nuclear Plant (BFN) received an automatic scram on Reactor Protection System (RPS) Turbine Control Valve (TCV) fast closure trip. The support bracket for Unit 3 TCV #2 Electro- Hydraulic Control (EHC) pressure switch separated from TCV #2 allowing the mass of the pressure switch to break the hydraulic sense line. As a result, the EHC pressure switch sensed low pressure and triggered a half scram. With a half-scram previously in place due to an unrelated issue from closure of TCV #3, the additional half-scram resulted in an automatic scram on Unit 3 which is a reportable condition. Safety systems responded as designed and the reactor scram was uncomplicated. <br /><br /> The apparent cause of this event was determined to be high cycle fatigue failure of the Unit 3 TCV #2 EHC pressure switch support bracket. <br /><br /> This failure was corrected by replacing the failed mounting bracket with a newly designed mounting bracket. The corrective action to reduce the probability of recurrence is to install viscoelastic dampeners on the steam piping to reduce the overall piping vibration on the area components. The dampeners are expected to reduce overall piping vibration and the probability of future vibration induced failures of various components in the moisture separator rooms.
2962018002 | Browns Ferry 3 | 02/28/2018 | 04/30/2018 | ML18120A19 | <strong>Inoperable 250V Shutdown Board Battery Charger Results in Condition Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On December 22, 2017, the Unit 3 250V Shutdown Board (SDBD) 3EB Battery Charger failed the Surveillance for SDBD 3EB Battery Modified Performance Test. Operations personnel placed the spare battery charger in service and exited Technical Specifications (TS) Limiting Conditions for Operation (LCOs) for DC Sources 3.8.4 and 3.8.7. A work order for Maintenance troubleshooting was initiated. On February 2, 2018, the 250V SDBD 3EB Battery was declared Operable after a failed firing card was replaced in the 250V SDBD 3EB Battery Charger. Based on the results from the troubleshooting, a Past Operability Evaluation (POE) was requested on February 5, 2018. The violation of TS was first recognized on February 28, 2018, when the POE determined that the 250V SDBD 3EB Battery Charger, was functional but inoperable from April 3, 2014 until December 22, 2017, which is longer than allowed by TS. Consequently, Unit 3 was in violation of Technical Specifications LCO applicability 3.0.4 and Electrical Power Systems DC Sources LCOs 3.8.4, 3.8.5, 3.8.7, and 3.8.8. <br /><br /> The apparent cause of this event was no Preventive Maintenance (PM) strategy exists to replace or refurbish subcomponents of the SDBD Battery Chargers that are vulnerable to age degradation failures. A lack of precise and rigorous communication between Operations and Engineering personnel in regards to the operability determination of the 3EB Battery Charger in 2014 was a contributing cause. The corrective action to reduce the probability of similar events in the future is to create a PM strategy to replace or refurbish subcomponents of the SDBD Battery Chargers that are vulnerable to similar age degradation failures.
2962018003 | Browns Ferry 3 | 02/20/2018 | 04/20/2018 | ML18110A36 | <strong>Misadjusted Switch Results in Condition Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On February 20, 2018, at 1616 Central Standard Time (CST), during performance of a diesel generator (DG) emergency load acceptance surveillance test (LAT) the expected 4kV load sequencing did not occur. Specifically, the 3B Residual Heat Removal (RHR) pump, and 3B and 3D Core Spray (CS) pumps did not start. The B1 Residual Heat Removal Service Water (RHRSW) pump tripped and did not restart. The automatic start feature for these pumps was determined to be inoperable, in the event of a loss of offsite power, February 25, 2016, until February 23, 2018. This resulted in violation of Technical Specifications 3.0.4, Limiting Condition for Operation (LCO) Applicability; 3.3.5.1; Emergency Core Cooling Systems (ECCS) Instrumentation; 3.5.1, ECCS and Reactor Core Isolation Cooling (RCIC) System; and 3.7.1, RHRSW System and Ultimate Heat Sink. The automatic start function of redundant CS, RHR, and RHRSW trains were unaffected by this condition.<br /><br /> Investigation revealed that the Diesel Generator Voltage Available (DGVA) relay failed to energize as a result of open contacts due to a misadjusted breaker STA actuator arm. The switch associated with this breaker was replaced, and procedures were revised to add steps to verify proper switch alignment. The root cause was that the switch assemblies are an inadequate design for use as a breaker operated auxiliary switch. Corrective actions to prevent recurrence include completion of a partially implemented design change that utilizes the 52a switch to execute safety related functions on Browns Ferry Nuclear Plant, Units 1, 2, and 3, and common breakers with safety related functions.
2962018004 | Browns Ferry 3 | 05/17/2018 | 07/16/2018 | ML18197A30 | <strong>Main Steam Relief Valves Lift Settings Outside of Technical Specifications Required Setpoints</strong><br /><i>Abstract:&nbsp;</i>On May 17, 2018, the Tennessee Valley Authority was presented with as-found testing results indicating that three of the thirteen Main Steam Relief Valves (MSRVs) from Browns Ferry Nuclear Plant, Unit 3, were outside the +/- 3 percent setpoint band required for their operability. Troubleshooting determined that the three MSRV discs failed by corrosion bonding to their valve seats. The valve discs were previously platinum coated to prevent this, and this was the first Unit 3 MSRV service interval to implement an improved surface treatment to prevent coating delamination. <br /><br /> These three MSRVs were found to have been inoperable for an indeterminate period of time between March 26, 2016, and February 17, 2018, which is longer than permitted by Technical Specifications (TS). The affected valves remained capable of maintaining reactor pressure within American Society of Mechanical Engineers code limits. Additionally, the valves' ability to open under remote-manual operation, activation through the Automatic Depressurization System, or MSRV Automatic Actuation Logics were not affected. The valves remained capable of performing their required safety function. <br /><br /> The valves failed to open within their TS required limits due to the valve discs corrosion bonding to their seats, as a result of their platinum anti-corrosion coatings flaking off. The immediate corrective action was to replace all thirteen of the Unit 3 MSRV pilot valves with refurbished valves during the Unit 3 Refueling Outage 18. The corrective action was to ensure pilot discs are prepared for platinum coating in accordance with the revised procedure which requires nitrogen pressure testing to verify valve seal functionality prior to coating.
2982018001 | Cooper Station | 03/10/2018 | 05/08/2018 | ML18136A53 | <strong>Inadequate Packing on Motor Operated Valve Results in Unplanned High Pressure Coolant Injection Inoperability and a Loss of Safety Function</strong><br /><i>Abstract:&nbsp;</i>On March 10, 2018, while returning High Pressure Coolant Injection (HPCI) and Augmented Off-Gas to service following planned maintenance, Cooper Nuclear Station (CNS) Operations personnel observed rising pressure in the drywell. <br /><br /> During the HPCI restoration, HPCI-MOV-MO15 was cycled and left open as part of the return to service process. Shortly thereafter, drywell temperature and pressure started to slowly rise. It was determined the most likely cause of the change in drywell parameters was due to the stroking of HPCI-MOV-MO15. A decision was made to close the valve to stop the leak, resulting in an unplanned entry into Technical Specification Limiting Condition for Operation 3.5.1, due to HPCI inoperability. Following valve closure, drywell temperature and pressure, along with the unidentified leakage rate, decreased. A decision was made to perform a normal plant shutdown to make repairs. <br /><br /> CNS entered Mode 3, Hot Shutdown, on March 11, 2018. New packing was installed on HPCI-MOV-MO15 and CNS returned to Mode 1, Power Operation, on March 17, 2018.<br /><br /> The cause of the packing leak was determined to be that in effort to preserve and maximize the margin for the stroking function, packing consolidation and torquing methods were altered which impacted packing sealing performance.<br /><br /> No safety consequences were associated with this condition.
2982018002 | Cooper Station | 10/10/2018 | 12/10/2018 | ML18353A27 | <strong>Lack of Procedural Guidance Results in Work Scheduling Error Causing Breach of Secondary Containment and Condition Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>During maintenance on Residual Heat Removal Service Water piping, secondary containment was breached due to work being performed simultaneously on the piping in both the reactor building and the control building basement. Upon discovery of the breach, work was stopped and direction given to install temporary covers for each breach. Upon investigation, it was discovered that multiple work orders for work on different areas of the piping had been approved, with the assumption that the work would not be scheduled to be performed concurrently.<br /><br /> Limiting Condition for Operation (LCO) 3.5.2, Condition C, was previously entered for a planned Water Inventory Control Activity to replace Control Rod Drive Mechanisms. As directed by the LCO, a contingency plan was established to maintain a secondary containment boundary by closing door R102, if needed. It was not known during this time that pipe repairs were ongoing or planned; thus the contingency plan used to enter the LCO did not include actions to be taken if secondary containment were breached via the piping. <br /><br /> Guidance will be developed for review and approval of outage work orders. Procedures will be revised to clarify secondary containment review requirements during the work order approval process.
2982018003 | Cooper Station | 10/10/2018 | 05/06/2019 | ML19128A03 | <strong>Safety Valve Failure Results in Loss of Safety Function</strong><br /><i>Abstract:&nbsp;</i>On September 29, 2018, at 20:53, Cooper Nuclear Station (CNS) commenced Refueling Outage 30 (RE30) and subsequently entered Mode 5 on October 2, 2018, at 02:41. <br /><br /> During RE30 activities, MS-RV-70ARV (Serial Number BL-2463) was removed from service and sent off-site for as-found setpoint pressure testing per station procedure. On October 10, 2018, the as-found testing was performed at National Technical Systems Laboratories (formerly Wyle Laboratories). The valve was tested three times. Per procedure, the acceptance criterion is 1202.8 psig - 1277.2 psig. The as-found testing result for the first test was 1278.6 psig. The second and third tests were performed with the results being 1260.0 psig and 1263.2 psig, respectively. Technical Specifications Surveillance Requirement setpoint criteria for the safety valves are 1240 +/-37.2 psig. <br /><br /> The safety valve was inspected at the testing facility to determine the cause of the valve failure. It was determined that the potential cause was binding or increased friction between the disc holder/guide or spindle areas. To bound this potential cause, the spindle, disc, disc holder, disc collar, lift stop, lower adjusting ring, upper adjusting ring, and compression screw will be replaced and the CNS maintenance procedure will be revised to incorporate foreign material covers during the removal and installation steps.
3012018001 | Point Beach 2 | 10/15/2018 | 12/13/2018 | ML18347B03 | <strong>Operation or Condition Prohibited by Technical Specifications, Less than Minimum Refueling Cavity Water Level</strong><br /><i>Abstract:&nbsp;</i>On October 15, 2018 at 1405, with Unit 2 in MODE 6 for refueling activities, it was identified that the refueling cavity level did not satisfy Technical Specification (TS) Limiting Condition for Operation (LCO)s. Technical Specification Action Condition (TSAC) 3.9.6.A, for refueling cavity water level not within limit, and TSAC 3.9.5.A, for less than the required number of RHR loops OPERABLE were entered.<br /><br /> During the evaluation of the issue there was evidence that the condition existed longer than the time allowed by TS. Therefore, this event is being reported pursuant to 10 CFR 50.36(c)(2) and 10 CFR 50.73(a)(2)(i)(B).
3062018001 | Prairie Island 2 | 05/17/2018 | 09/17/2018 | ML18260A37 | <strong>Automatic Actuation of Emergency Diesel Generator D5</strong><br /><i>Abstract:&nbsp;</i>On May 17, 2018, at 11:15 Central Daylight Time (CDT), with Unit 2 in Mode 1 at 100% power, the station experienced an auto-start of Emergency Diesel Generator (EDG), D5. The Bus 25 Potential Transformer fuse drawer was opened by a supplemental worker, causing Breaker 25-16 to open and de-energize Bus 25. Operators were able to manually close the EDG D5 output breaker to reenergize Bus 25. All equipment functioned as designed. EDG D5 was restored to a normal condition on May 17, 2018, at 16:44. This event was reported in accordance with 10 CFR 50.72(b)(3)(iv)(A) as an event that results in a valid actuation of the EDG.<br /><br /> The Direct Cause of this event was that the Worker opened FU/B25 25-16 POT "BUS 25 POT TO 25 LOAD SEQ PH AB and CB FUSES" (Human Performance).The Root Cause was that the risk of performing the Prairie Island Open Phase Project online with Bus 25 energized was not recognized and understood by the organization. <br /><br /> Immediate Action taken in the field placed the equipment in a safe condition and investigation efforts were completed to identify the direct cause of the condition and restoring power to Bus 25. Corrective Actions include, develop and execute a targeted observation initiative to drive improvement in walk down rigor for Design Engineering, Maintenance Planning and Operations Planning. Tagging procedure was revised to specify the requirements of the meeting required for clearances associated with modifications. POT drawers were labeled with equipment ID. Open action to install locking device and caution to instruct operator approval prior to opening drawer and contain a physical barrier such as a lock, zip tie or screws to discourage opening.
3062018002 | Prairie Island 2 | 05/22/2018 | 07/18/2018 | ML18200A08 | <strong>RHR Flood Barriers Compensatory Measures</strong><br /><i>Abstract:&nbsp;</i>On October 19, 2017, during 2R30 refueling outage a condition occurred where 21 Residual Heat Removal (RHR) pump motor floor plug, which is a flood barrier, was removed with Unit 2 in Mode 6 and core offload in progress. 21 RHR pump was out-of-service. Had a postulated internal flood occurred, this configuration could have led to flooding of the operable 22 RHR pump resulting in a loss of all RHR cooling. For 28 hours and 40 minutes Prairie Island Unit 2 was non-compliant with Technical Specifications (TS) 3.9.5, Condition A, which requires one RHR loop to be operable and in operation. This event is reportable under 10 CFR 50.73(a)(2)(i)(B): Any operation or condition which was prohibited by the plant's TS. <br /><br /> Apparent Cause is that the Station Flooding Program, is not effectively tied to the Fleet Work Management Process to ensure adequate flooding controls are in place for the RHR system.<br /><br /> Corrective Actions are to update the Fleet Work Management Process and Walkdown Form to address Flooding/High Energy Line Break (HELB)/Critical Drainage paths at Prairie Island per Internal Flooding Drainage Controls.
3112018001 | Salem 2 | 05/07/2018 | 07/06/2018 | ML18187A24 | <strong>Manual Reactor Trip due to Elevated 21 Reactor Coolant Pump Motor Winding Temperature</strong><br /><i>Abstract:&nbsp;</i>At 0325 on May 7, 2018 Salem Unit 2 experienced a manual reactor trip from approximately 90% power when 21 Reactor Coolant Pump (RCP) motor winding temperature reached the abnormal operating procedural limit of > 302 Degrees Fahrenheit requiring the RCP to be promptly removed from service. <br /><br /> As expected, the Auxiliary Feedwater (AFW) pumps started following the unit trip. Unit 2 was stabilized in Mode 3 at normal operating pressure and temperature with the 22, 23, and 24 RCPs in-service.<br /><br /> The cause of the adverse temperature trends of 21 RCP motor winding temperature was a high resistance termination contact, due to a loose connection, at the motor stator winding Resistance Temperature Detector (RTD) terminal point where field wires connect to the control room recorder.<br /><br /> This report is being made in accordance with 10CFR50.73 (a)(2)(iv)(A), "Any event or condition that resulted in manual or automatic actuation of any of the systems listed in paragraph (a)(2)(iv)(B)," for this event actuation of the Reactor Protection System (RPS) and the Auxiliary Feedwater System (AF).
3112018002 | Salem 2 | 09/14/2018 | 11/12/2018 | ML18316A01 | <strong>Automatic Reactor Trip due to High 23 Steam Generator Water Level</strong><br /><i>Abstract:&nbsp;</i>On September 14, 2018 Salem Unit 2 tripped from 90 percent power when 23 steam generator water level reached the HI-HI setpoint. This caused a trip of the main turbine generator, both steam generator feedwater pumps and closure of feedwater isolation and control valves. The trip of the main turbine generator caused an automatic reactor trip. All systems functioned as expected and Unit 2 was stabilized in MODE 3 at normal operating pressure and temperature. <br /><br /> The cause of the high water level was failure of 23BF19 (steam generator water level control valve). 23BF19 fully opened when a positioner feedback arm failed due to cyclic fatigue due to vibration. The positioner feedback arm was replaced and the station returned to operation at a reduced power level that did not induce the vibration. The feedwater control valve or the feedwater control system will be modified to adjust system parameters to reduce vibration.<br /><br /> This event is reported per 10CFR50.73{a)(2)(iv)(A), "Any event or condition that resulted in manual or automatic actuation of any of the systems listed in paragraph (a)(2)(iv)(B)," for this event actuation of the reactor protection system and the auxiliary feedwater system. Notification of this event was provided via ENS report 53606.
3132018001 | Arkansas 1 | 05/16/2018 | 07/13/2018 | ML18194A68 | <strong>Automatic Reactor Trip due to Loss of Main Feedwater Pump</strong><br /><i>Abstract:&nbsp;</i>During the Arkansas Nuclear One, Unit 1 (ANO-1) startup from refueling outage 1R27 at ~1750 CDT on May 16, 2018, the reactor experienced an automatic reactor trip from approximately 10 percent power due to a Reactor Protection System (RPS) trip from a loss of main feedwater as a result of a trip of the “B” Main Feedwater Pump (MFP) due to operator error. The “A” MFP was not in operation at the time. The ANO-1 Control Room was in the process of raising reactor power to a band of 12 – 15% when the MFP tripped on high discharge pressure. <br /><br /> The MFP trip resulted in a RPS actuation (reactor trip) followed by an Emergency Feedwater actuation. All control rods inserted into the core and the reactor was verified shutdown.
3132018002 | Arkansas 1 | 06/12/2018 | 11/16/2018 | ML18320A23 | <strong>Leak in Class 1 Reactor Coolant System Pressure Boundary Piping due to Cyclic Fatigue Failure on a High Pressure Injection Line Drain Tap Weld</strong><br /><i>Abstract:&nbsp;</i>On June 12, 2018, while in Mode 3 and investigating leakage at Arkansas Nuclear One, Unit 1, a leak was identified on a drain line associated with one of the four High Pressure Injection lines which discharge to the Reactor Coolant System (RCS). The subject leak was identified during a walk down of Reactor Building structures, systems, and components initiated in response to an elevated RCS leak rate. The leak was a result of a cyclic fatigue failure originating from poor weld geometry and grinding marks present on the axial weld toe of the associated field weld. The leak was subsequently repaired and the unit returned to power operation. The corrective action plan addressed the causal factors associated with this event.<br /><br /> Corrective actions completed or planned include 1) similar locations were inspected for weld defects, 2) enhanced training of the specific weld type, and 3) planned mockups for future high risk / high value welds. This event had no effect on the public health and safety. The event was reported to the Nuclear Regulatory Commission on June 12, 2018, via Event Notification 53456.
3132018003 | Arkansas 1 | 06/16/2018 | 08/10/2018 | ML18222A24 | <strong>Manual Trip due to Turbine Bypass Valve Failing Open</strong><br /><i>Abstract:&nbsp;</i>On June 16, 2018, Arkansas Nuclear One, Unit 1 (ANO-1), performed a manual reactor trip due to a Turbine Bypass Valve (TBV) failing open during reactor startup. The copper instrument tubing, which connects the positioner output to the top of the TBV cylinder booster, was found broken at the tubing ferrule. The instrument tubing failure was determined to be due to high cycle fatigue and vibration. The root cause of this event was determined to be the instrument air copper tubing had less than adequate robustness for the TBV system high vibration application. Corrective actions include replacement of the tubing and fittings with stainless steel and flex-lines for the four ANO-1 TBVs during the next scheduling refueling outage. <br /><br /> This event had no effect on the public health and safety. The event was reported to the Nuclear Regulatory Commission on June 16, 2018 via Event Notification 53459.
3132018004 | Arkansas 1 | 12/18/2018 | 08/26/2019 | ML19238A05 | <strong>Reactor Trip due to the Loss of a Non-Vital 4160 Volt Bus</strong><br /><i>Abstract:&nbsp;</i>On December 18, 2018, Baker testing of the Arkansas Nuclear One, Unit 1, Main Chiller motor was being performed. Unit 1 was operating at 100%. Baker motor testing is completed to gather performance monitoring data on various motors. The testing is intended for use in detection of motor health, input power, and other dynamic electrical problems with electric motors.<br /><br /> At approximately 1120 on December 18, 2018, during restoration from the subject testing, an electrical arc was observed. The arc was observed upon the removal of the third voltage test clip from a non-vital 4160 volt (V) bus. The arc caused the two fuses in one of the electrical phases to open in order to protect the bus Control Power Transformer. The loss of the control power circuit resulted in the 4160V feed from the unit Auxiliary Transformer opening, causing the 4160V bus to de-energize. The Startup Transformer feeder breaker to the 4160V bus did not automatically close upon loss of 4160V bus voltage because its closing logic was not satisfied. The loss of the 4160V bus resulted in load shedding of the respective buses, automatic start and connection of the associated Emergency Diesel Generator to the respective vital 4160 bus, and a subsequent plant transient. The direct cause of the event was determined to be an electrical arc event when removing the test leads due to the close proximity of the test lead to ground. <br /><br /> The plant transient lead to a reactor trip on high Reactor Coolant System pressure following the loss of one of the two operating Main Feedwater pumps. After the reactor trip, the unit was stabilized in Mode 3 with feedwater being supplied to the Steam Generators by the unit Auxiliary Feedwater pump.
3152018001 | Cook 1 | 04/02/2018 | 05/31/2018 | ML18155A30 | <strong>Unit 1 East Essential Service Water Pump Inoperable Longer Than Allowed by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On April 2, 2018, at 0936 Eastern Daylight Time (EDT), with Unit 1 in Mode 1 at 100 percent power, an abnormal noise was heard coming from the Unit 1 East Essential Service Water (ESVV) Pump Motor. Vibration data was taken and determined to be acceptable. On April 4, 2018, an increase in sound level from the motor was identified and the source was investigated. The Unit 1 East ESW Train was declared inoperable on April 5, 2018, at 1230 EDT when it was determined that the station no longer had reasonable expectation that the motor would operate for its mission time due to a degraded upper motor bearing. Corrective action was taken to replace the motor and the Unit 1 East ESW Train was declared operable on April 6, 2018, at 1727 EDT. A past operability evaluation was performed and determined that the Unit 1 East ESW Train had been inoperable since April 2, 2018, at 0936 EDT. As a result, the Unit 1 East ESW Train was inoperable longer than allowed by Technical Specifications. During this time, redundant equipment in the opposite train remained operable.<br /><br /> The cause of the motor bearing degradation was determined to be sub-surface initiated fatigue of the upper bearing outer race due to a manufacturing defect. It was determined the defect was a flaw in a singular bearing and it does not impact other installed ESW pump motors. <br /><br /> This event is reportable in accordance with 10 CFR 50.73(a)(2)(i)(B).
3162018001 | Cook 2 | 04/13/2018 | 06/04/2018 | ML18157A06 | <strong>Valid Actuation of the Unit 2 CD Emergency Diesel Generator During Testing</strong><br /><i>Abstract:&nbsp;</i>On April 13, 2018, with Unit 2 defueled, at approximately 1555 Eastern Daylight Time (EDT), during performance of procedure 12-EHP-4030-056-218 (Automatic Operation of Auxiliary Feedwater Pumps), the Unit 2 CD Emergency Diesel Generator (EDG) automatically started unexpectedly and loaded to 4kV Safeguards bus T21C when test switches were closed before the technician performing the surveillance recognized that he had mistakenly skipped a page that would have prevented the CD EDG from starting.<br /><br /> The South Spent Fuel Pit (SFP) Cooling Train lost power due to the expected load shed, and was restarted on the Unit 2 CD EDG at 1614 EDT. The North SFP Cooling Train remained in-service for the duration of the event. There was no observable change in Spent Fuel Pool Temperature.<br /><br /> The valid actuation of the Unit 2 CD EDG is reportable pursuant to 10CFR50.73 (a)(2)(iv)(A) as an event or condition that resulted in the manual or automatic actuation of Emergency AC Electrical Power Systems, including Emergency Diesel Generators (EDGs).
3162018002 | Cook 2 | 04/13/2018 | 06/11/2018 | ML18164A02 | <strong>Unit 2 Component Cooling Water System Inoperable Longer Than Allowed by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On April 13, 2018, Unit 2 was in a refueling outage with the reactor defueled. A leak test of the Unit 2 Component Cooling Water (CCW) Pump Discharge Crosstie Train A Shutoff Valve failed to meet acceptance criteria and the valve was declared inoperable. The cause of the failed test was due to the as-found closed torque value being lower than the recommended minimum. The valve closed torque setting was adjusted and a subsequent leak rate test was acceptable. <br /><br /> The failed test was untimely because it is required by Section XI of the American Society of Mechanical Engineers Code, but was performed for the first time due to being excluded from the inservice testing program as identified during inspection activities in November 2015. A past operability review determined the Unit 2 Train A CCW System was inoperable prior to December 3, 2015, at which time a temporary modification was approved to add a safety related make up water supply to the Unit 2 CCW System. A review of other equipment or systems redundant to Train A indicated occurrences when opposite train equipment was declared inoperable prior to December 3, 2015. <br /><br /> The event is reportable as an Operation or Condition Prohibited by Technical Specifications in accordance with 10 CFR 50.73(a)(2)(i)(B) and a Condition that Could Have Prevented the Fulfillment of a Safety Function in accordance with 10 CFR 50.73(a)(2)(v).
3162018003 | Cook 2 | 05/07/2018 | 07/02/2018 | ML18186A32 | <strong>Unit 2 Manual Reactor Trip due to High-High Moisture Separator Drain Tank Level</strong><br /><i>Abstract:&nbsp;</i>On May 7, 2018, Unit 2 was operating at approximately thirty percent power following completion of a refueling outage. The control room staff received a high-high level alarm in a moisture separator drain tank (MSDT) and manually tripped the reactor in accordance with plant procedures. Plant systems responded as expected. The plant was stabilized in hot standby conditions. <br /><br /> An investigation discovered condensate heater level column isolation valves were inadvertently left closed and not restored following system testing activities. This condition resulted in a loss of level control in the corresponding heater. Excess condensate could not drain from the heater and eventually backfilled through a steam supply line into the MSDT. This caused the drain flow capacity of the MSDT to be exceeded which resulted in corresponding high and high-high level alarms. The level column isolation valves were later returned to the open position which restored the condensate drain flow paths and cleared the alarms.<br /><br /> The manual reactor trip caused actuation of the Reactor Protection System and an automatic actuation of the Auxiliary Feedwater System. Therefore, the event is reportable as a Licensee Event Report in accordance with 10 CFR 50.73(a)(2)(iv)(A), "Any event or condition that resulted in manual or automatic actuation of any of the systems listed in paragraph (a)(2)(iv)(B)."
3172018001 | Calvert Cliffs 1 | 02/25/2018 | 02/07/2019 | ML19043A66 | <strong>Pressurizer Safety Valve As-Found Settings Outside Technical Specification Limits due to Damaged Internals</strong><br /><i>Abstract:&nbsp;</i>During scheduled testing at the offsite testing facility, the as-found lift setting for the pressurizer safety valve previously installed in Unit 1 at the 1RV200 location was measured outside the Technical Specification allowable values (valve lifted low). The valve had been installed during the 2016 Unit 1 refueling outage and was removed during the 2018 Unit 1 refueling outage for scheduled testing and maintenance. As scheduled, a spare valve was installed in its place during the 2018 refueling outage. The failed valve was disassembled and inspected at an offsite facility. The apparent cause of the PSV failure identified that the expanded contact area between the valve's bellow nose and disc, which was caused by the presence of a bulge in the bellows nose, as a result of bellows stretch and compression, did not allow the disc to act normally which resulted in the valve lifting early. The valve will have damaged parts replaced, be rebuilt, tested, and re-certified for installation in the plant during the next Unit 1 refueling outage. Calvert Cliffs will require the vendor to employ a revised method for preparing a valve for its certification lifts whenever valve internals are replaced.
3172018002 | Calvert Cliffs 1, Calvert Cliffs 2 | 05/14/2018 | 06/07/2018 | ML18164A02 | <strong>Items Non-Conforming to Design for Tornado Missile Protection</strong><br /><i>Abstract:&nbsp;</i>On May 14, 2018, Calvert Cliffs Nuclear Power Plant determined that the Saltwater subsystems on both Units 1 and 2 do not conform with the licensing basis for protection against a tornado generated missile. The Saltwater system header is vulnerable to a tornado missile that enters the Intake Structure through the watertight door, IS-2. An extent of condition review did not identify any additional items that are nonconforming to the design basis for a tornado missile. Upon determination of the initial non-conformance for the Saltwater system subsystems, both Saltwater subsystems were declared inoperable for both Units. Compensatory measures were put in place and verified. Therefore, in accordance with the NRC Enforcement Guidance Memorandum EGM 15-002, both Saltwater system subsystems were returned to operable but nonconforming status and an 8-hour ENS Notification was made to the NRC. This condition has been in existence since original licensing of the plant. It is not known if it was overlooked or considered acceptable at the time of the original licensing process. There are no actual consequences as a result of the nonconforming condition.
3172018003 | Calvert Cliffs 1, Calvert Cliffs 2 | 07/07/2018 | 10/08/2018 | ML18283A30 | <strong>Control Room Loss of Ventilation due to Smoke Detector Failure Causing Common Supply Damper to Shut</strong><br /><i>Abstract:&nbsp;</i>On July 7, 2018, at 02:42 the main Control Room experienced a loss of ventilation due to the Control Room supply damper fully closing. This isolated ventilation flow to the Control Room which resulted in both trains of the Control Room Emergency Ventilation System and Control Room Emergency Temperature System being out of service, resulting in Technical Specification Limiting Condition for Operations 3.7.8 and 3.7.9 not being met, respectively. Field troubleshooting isolated the cause of failure to Control Room ventilation smoke detector. The smoke detector functions to shut the Control Room supply damper. Manual action was taken to open the Control Room supply damper. The Units exited the associated Technical Specifications at time 02:49. This event is reportable in accordance with 10 CFR 50.73(a)(2)(v)(D) and 10 CFR 50.73(a)(2)(vii). The apparent cause of the smoke detector failure is that no preventive maintenance activity existed to inspect and clean the Control Room ventilation smoke detector to prevent dust and dirt accumulation settling on the smoke detector head. A preventative maintenance activity is being implemented.
3182018001 | Calvert Cliffs 2, Calvert Cliffs 1 | 10/11/2018 | 01/09/2019 | ML19015A01 | <strong>Both Unit 2 Emergency Diesel Generators Inoperable due to Depressurization in Common Air Start Headers</strong><br /><i>Abstract:&nbsp;</i>On October 11, 2018, during a post maintenance start of Unit 1 Emergency Diesel Generator (EDG) 1B, its air start control valves failed to shut as designed. This caused air pressure in the common air start headers, shared with both Unit 2 EDGs, to depressurize to a point that rendered both Unit 2 EDGs inoperable. Operations isolated EDG 1B air start control valves which resulted in air start pressure returning to normal on both Unit 2 EDGs. This event resulted in a loss of safety system function for Unit 2 EDGs to exist for 30 minutes. The cause was due to a diode shorting in EDG 1B air start control circuitry which caused two fuses in the circuitry to fail, thus preventing relays to shut the air start control valves. The diode was installed in the air start circuitry during this EDG 1B maintenance period to suppress induced voltage observed with newly installed control relays. The apparent cause of the diode failure was due to an undetected manufacturing defect. This event revealed a previously unknown design vulnerability in the circuitry where failure of a single fuse, at a specific time in the EDG start interval, could cause loss of air start pressure to the other EDGs that share the common air start headers. Corrective actions taken included removal of the new diodes and relays from the control circuitry and installation of isolation valves in the common air start headers.
3212018001 | Hatch 1, Hatch 2 | 01/20/2018 | 03/21/2018 | ML18080A05 | <strong>Condition Prohibited by Tech Specs due to Secondary Containment Inoperability</strong><br /><i>Abstract:&nbsp;</i>On January 20, 2018 at 1950 EST with Unit 1 at approximately 95 percent rated thermal power and Unit 2 at approximately 100 percent rated thermal power, a Secondary Containment drawdown test was completed unsatisfactorily due to not being able to establish greater than or equal to 0.20 inches of vacuum water gauge within 10 minutes in accordance with Technical Specification (TS) Surveillance Requirement (SR) 3.6.4.1.3. This test was performed using the 1A, 1B, and 2A Standby Gas Treatment (SBGT) trains. Operations personnel entered the required action statement for an inoperable secondary containment. A subsequent secondary containment drawdown test was successfully performed at 2236 EST using the 1B, 2A, and 2B SBGT trains. The required action statement was therefore exited due to meeting the surveillance requirement. <br /><br /> Subsequent troubleshooting revealed degraded secondary containment door seals. The degraded secondary containment doors were repaired and a satisfactory secondary containment drawdown test using the 1A, 1B, and 2A SBGT trains was completed on January 25, 2018. As part of the corrective actions, the secondary containment door preventative maintenance procedure will be revised with enhanced actions to prevent recurrence of degraded components.
3212018002 | Hatch 1 | 02/09/2018 | 03/21/2018 | ML18080A05 | <strong>Performance of Operations with the Potential to Drain the Reactor Vessel (OPDRV) Without Secondary Containment</strong><br /><i>Abstract:&nbsp;</i>On February 9 through February 13, 2018, planned operations with the potential to drain the reactor vessel (OPDRV) activities were performed while Unit 1 remained in Refueling Mode (Mode 5) without an operable secondary containment. These activities are prohibited per Technical Specifications (TS) 3.6.4.1. However, recent NRC guidance provided in Enforcement Guidance Memorandum (EGM) 11-003, Revision 3 and in Regulatory Issue Summary (RIS) 2012-11 allowed the implementation of interim actions as an alternative to full compliance. These actions are contained in the operating procedure for the OPDRV activities performed during the 2018 Hatch Unit 1 Refueling Outage in February. <br /><br /> The performance of OPDRV activities were planned activities that were completed under the guidance of plant procedures and confirmed to have low safety significance based on interim actions taken. Since these actions were deliberate, a cause determination was not necessary. A license amendment request (LAR) has been submitted for the associated NRC-approved Technical Specifications Task Force (TSTF) Traveler 542, "Reactor Pressure Vessel Water Inventory Control."
3212018003 | Hatch 1 | 06/20/2018 | 08/15/2018 | ML18227A88 | <strong>Safety Relief Valves' As Found Settings Resulted in Not Meeting Tech Spec Surveillance Criteria</strong><br /><i>Abstract:&nbsp;</i>On June 20, 2018, Unit 1 was at 100 percent rated thermal power (RTP) when "as-found" testing results of the 3-stage main steam safety relief valves (SRVs) indicated two of the eleven Unit 1 SRVs had experienced a setpoint drift during the previous operating cycle which resulted in their failure to meet the Technical Specification (TS) opening setpoint pressure of 1150 +/- 34.5 psig as required by TS Surveillance Requirement (SR) 3.4.3.1. The test results showed that the two SRVs were slightly out of spec low due to setpoint drift <br /><br /> The SRV pilots were disassembled and inspected to investigate the reason for the setpoint drift. Based on inspection results. the drift in setpoint was due to low abutment gap and low abutment pressure. Due to their location, drywell ventilation blowing on these two safety relief valves caused them to undergo a cyclic heating and cooling every 12 hours during the Unit's 2-year operating cycle. These temperature gradients across the valve internals caused a relaxation of the setpoint spring and bellows assembly.
3232018001 | Diablo Canyon 2 | 12/01/2018 | 04/11/2019 | ML19101A43 | <strong>Automatic Reactor Trip of Unit 2 Following a Load Rejection</strong><br /><i>Abstract:&nbsp;</i>On December 1, 2018, at 1006 PST, with Unit 2 at 100 percent power, the reactor automatically tripped following a load rejection from the 500 kV off site electrical system. The trip was not complex; all safety systems responded as designed. Due to the Unit 2 reactor trip and the expected actuation of the Auxiliary Feedwater System, this event is being reported per 10 CFR 50.73(a)(2)(iv)(A).<br /><br /> This event was a result of an automatic operation of the Diablo Canyon Special Protection Scheme (DC-SPS) that occurred when DC-SPS sensed two out of three 500 kV lines out of service when all three lines were in service. The DC-SPS Remote Outage Detection (ROD) logic used local current, independent of breaker position, for detecting a remote-end outage to determine if 500k kV lines were in service. <br /><br /> The ROD logic portion of the DC-SPS circuitry has been disabled and mitigation measures have been implemented, including improved communications with the Grid Control Center. <br /><br /> There was no impact on the health and safety of the public or plant personnel.
3252018001 | Brunswick 1 | 03/07/2018 | 05/07/2018 | ML18127A09 | <strong>Implementation of Enforcement Guidance Memorandum (EGM) 11-003, Revision 3</strong><br /><i>Abstract:&nbsp;</i>On March 7, 2018, Unit 1 implemented the guidance of EGM 11-003, Revision 3, "Enforcement Guidance Memorandum 11-003, Revision 3, Dispositioning Boiling Water Reactor Licensee Noncompliance with Technical Specification Containment Requirements during Operations with a Potential for Draining the Reactor Vessel," dated January 15, 2016. Consistent with EGM 11-003, Revision 3, secondary containment operability was not maintained during Operations with a Potential for Draining the Reactor Vessel (OPDRV) activities, and Required Actions C.1 and C.2 of Technical Specifications (TS) 3.6.4.1, "Secondary Containment," were not completed. EGM 11-003, Revision 3, was implemented seven additional times during the 2018, Unit 1 refueling outage. These conditions are being reported in accordance with 10 CFR 50.73(a)(2)(i)(B) as operations prohibited by the plant's TS.<br /><br /> Implementation of EGM 11-003, Revision 3, during the Unit 1 refueling outage was a planned activity. As such, there was no causal evaluation of the event. Consistent with the guidance provided in EGM 11-003, Revision 3, BSEP submitted a license amendment request to the NRC on June 29, 2017, to adopt Technical Specification Task Force (TSTF)-542 associated with generic resolution of this issue.
3252018002 | Brunswick 1 | 04/07/2018 | 06/05/2018 | ML18156A56 | <strong>Automatic Reactor Trip during Stator Coolant System Realignment</strong><br /><i>Abstract:&nbsp;</i>On April 7, 2018, at 0836 Eastern Daylight Time (EDT), Unit 1 automatically tripped during realignment of the Stator Cooling System. The trip was uncomplicated with all systems responding normally. Reactor water level reached low level 1 (LL1) due to the reactor trip. Per design, the LL1 signal resulted in Group 2, Group 6, and Group 8 Primary Containment Isolation System (PCIS) actuations. The Reactor Protection System (RPS) and PCIS actuations are being reported in accordance with 10 CFR 50.73(a)(2)(iv)(A) as an event or condition that resulted in manual or automatic actuation of systems listed in 10 CFR 50.73(a)(2)(iv)(B).<br /><br /> The direct cause of this event was a design deficiency which resulted in an unanticipated Turbine Protection System actuation that caused a main turbine trip and subsequent automatic reactor trip. The root cause of the design deficiency was determined to be human performance related. Corrective actions include training and procedure revisions.
3252018003 | Brunswick 1 | 06/11/2018 | 08/09/2018 | ML18221A55 | <strong>Setpoint Drift in Main Steam Line Safety/Relief Valves Results in Two Valves Inoperable</strong><br /><i>Abstract:&nbsp;</i>On June 11, 2018, BSEP received the results of testing of eleven main steam line safety relief valves (SRVs) removed from Unit 1 during the spring 2018 refueling outage. Two of the eleven valves were found to have as-found lift setpoints of their pilot valves outside the +/-3 percent tolerance required by Technical Specification (TS) 3.4.3. TS 3.4.3 requires ten of the eleven installed SRVs to be operable. Since less than ten SRVs were operable, this event is being reported in accordance with 10 CFR 50.73(a)(2)(i)(B) as operation prohibited by the plant’s TS. All 11 of the SRV pilot valves were replaced with certified spares before the startup of Unit 1.<br /><br /> The direct cause of the out of tolerance as-found lift setpoints was corrosion bonding of the SRV pilot discs-to-the pilot seats. The root cause of the corrosion bonding was an inadequate procedure and work order instructions. Corrective actions include revising associated procedures to include sufficient detail to ensure consistent surface preparation and proper quality checks of surface condition are performed prior to platinum coating.
3272018001 | Sequoyah 1, Sequoyah 2 | 06/26/2018 | 09/18/2018 | ML18261A29 | <strong>Inadequate Post Maintenance Testing Results in Condition Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On June 26, 2018, at 0902 eastern daylight time, a flow switch electronic circuit board associated with the Strain Emergency Gas Treatment System (EGTS) Air Cleanup Subsystem relative humidity heaters was replaced due to the circuit board approaching the end of its environmentally qualified life. Following board replacement, the flow switch was calibrated and the B-train of EGTS was returned to service in the standby condition. The post maintenance testing (PMT) did not require or recommend operability testing. On July 22, 2018, Operations personnel performed a surveillance instruction for Surveillance Requirement (SR) 3.6.10.1 and identified that the B-train relative humidity heaters did not energize as required by the SR. Operators declared Limiting Condition for Operation 3.6.10, EGTS Air Cleanup Subsystem, not met and entered Condition A for one EGTS Air Cleanup Subsystem train being inoperable. On July 23, 2018, the flow switch circuit board for the B-train EGTS relative humidity heaters, that had previously been removed on June 26, was reinstalled. Following reinstallation of the board, the B-train of EGTS was able to meet SR 3.6.10.1 and was declared operable July 24, 2018, at 0115. The cause of the event was the lack of formality in determining PMTs and return to operability (RTO) tests even though the procedure provides adequate guidance for this determination. The corrective action is to conduct information sharing with each Operations Crew and the Work Planners to determine PMT and RTO requirements in accordance with the maintenance procedure.
3272018002 | Sequoyah 1, Sequoyah 2 | 11/24/2018 | 01/22/2019 | ML19022A04 | <strong>Exceeded Breach Margin Renders Both Trains of the Auxiliary Building Gas Treatment System Inoperable</strong><br /><i>Abstract:&nbsp;</i>On November 24, 2018, at 0930 eastern standard time (EST), Door A118 was breached to allow a hose to be routed from a vacuum truck outside to an ice bin inside the Unit 2 Additional Equipment Building. The auxiliary building secondary containment enclosure (ABSCE) breach permit required personnel to be stationed in the main control room (MCR) in communication with personnel responsible for closing Door A118. At 1420, it was discovered that no personnel were stationed in the MCR to perform this function. The open door created a breach of the ABSCE boundary that exceeded the allowed breach margin. As a result, both units entered Technical Specification (TS) Limiting Condition for Operation (LCO) 3.7.12, Condition E for a required train of Auxiliary Building Gas Treatment System (ABGTS) inoperable with fuel stored in the spent fuel pool and Unit 1 entered LCO 3.7.12, Condition B for two trains of the ABGTS inoperable due to an inoperable ABSCE boundary in Mode 1, 2, 3, or 4. At 1435, the door was closed and both units exited LCO 3.7.12, Condition E and Unit 1 exited LCO 3.7.12, Condition B. <br /><br /> An evaluation determined that the event was related, in part, to a failure to review the requirements of the ABSCE breach permit. Corrective actions included revising the associated work order to add a hold point to ensure the ABSCE permit is reviewed, understood, and adhered to prior to and during breach. The hold point now requires a supervisor's signature to proceed in the work order.
3312018001 | Duane Arnold | 02/06/2018 | 04/04/2018 | ML18128A19 | <strong>Loss of RPS Function During MSIV and TSV Channel Functional Testing due to Use of a Test Box</strong><br /><i>Abstract:&nbsp;</i>On February 6, 2018, at 1312 CST, while operating at 100% power, a Maintenance Supervisor determined that the use of the Reactor Protection System (RPS) test box described in site procedures would result in the loss of two RPS reactor scram functions. Technical Specifications (TS) 3.3.1.1 requires that RPS instrumentation for Table 3.3.1.1-1, Function 5, for Main Steam isolation Valves (MSIVs) and Table 3.3.1.1- 1, Function 8, for Turbine Stop Valves (TSVs) remain OPERABLE. Surveillance Test Procedure (STP) 3.3.1.1-17, Main Steam Isolation Valve Functional Test, used the RPS test box from June 2015 through July 2016. STP 3.3.1.1-19, Functional test of TSV Closure Input to RPS and RPT, had used the RPS test box from May 2006 through December 2017. The cause of this event was determined to be inadequate plant effect evaluations for revising the STPs to incorporate use of the RPS test box. This event was of low safety significance and had no impact on public health or safety. This event is reportable pursuant to 10CFR50.73(a)(2)(v) as an Event or Condition that Could Have Prevented Fulfillment of a Safety Function. <br /><br /> STP 3.3.1.1-19 was revised on February 28, 2018 to eliminate the use of the RPS test box.
3312018002 | Duane Arnold | 07/09/2018 | 08/16/2018 | ML18228A75 | <strong>Both Doors in Secondary Containment Airlock Opened Concurrently</strong><br /><i>Abstract:&nbsp;</i>On July 9, 2018, at 1334, while operating at 100% power, workers opened doors concurrently when entering a secondary containment access airlock. The individuals involved each closed their respective doors upon encountering this unexpected condition; however, the result was a brief inoperability of secondary containment integrity. This resulted in an 8 hour reportable event. The Resident Inspector was notified, and an Event Notification was made pursuant to 10 CFR 50.72(b)(3)(v)(C) due to a condition at the time of discovery that prevented the fulfillment of the Secondary Containment safety function (Reference EN#53496). Following the event, the doors were verified to be functioning properly via Surveillance Test Procedure. A Root Cause Evaluation was previously conducted and determined the root cause of this event is that the airlock door interlock is not designed to prevent more than one airlock door from opening under all possible conditions. <br /><br /> This event did not result in a safety system functional failure. There were no radiological releases associated with this event.
3312018003 | Duane Arnold | 09/09/2018 | 10/22/2018 | ML18303A29 | <strong>Combined Maximum Main Steam Line Pathway Leakage Exceeded Technical Specification Limit</strong><br /><i>Abstract:&nbsp;</i>On September 9, 2018, with the unit shutdown for a planned refueling outage (Mode 5, Refueling, 0% power), an evaluation of data from the scheduled Main Steam System valve penetration Local Leak Rate Testing (LLRT) determined the 'as found' maximum pathway leakage for the Main Steam System to be in excess of the Technical Specification (TS) 3.6.1.3 leakage limit of <=200 scfh for combined maximum pathway leakage. The largest contributor to the leakage was through the main steam line (MSL) drains. The cause was that the MSL Drain valves were not optimal for the service conditions to ensure long term performance. Corrective actions were taken to replace the main steam line drain valves with an optimal valve design. This event was of low safety significance and had no impact on public health or safety. This event is reportable pursuant to 10CFR50.73(a)(2)(i)(B). This event did not result in a safety system functional failure. There were no radiological releases associated with this event and there were no automatically or manually initiated safety system responses.
3312018004 | Duane Arnold | 10/19/2018 | 12/17/2018 | ML18355A62 | <strong>Automatic Reactor Scram due to Feedwater Regulating Valve Failure</strong><br /><i>Abstract:&nbsp;</i>On October 19, 2018, at 1725 while operating at 100% power, the 'B' Feedwater Regulating Valve (FRV; CV1621) failed closed resulting in lowering reactor level and subsequent automatic reactor scram on low level. This resulted in a 4 hour event report to the NRC under 10CFR50.72(b)(2)(iv)(B) for actuation of the Reactor Protection System. This report also included reports for emergency core cooling systems (High Pressure Coolant Injection (HPCI) and Reactor Core Isolation Cooling (RCIC)) discharge into the reactor coolant system under 10CFR50.72(b)(2)(iv)(A), and a valid actuation of the Primary Containment Isolation System under 10CFR50.72(b)(3)(iv)(A) (reference EN#53676). The FRV was subsequently repaired and the reactor was started up on October 21, 2018. The direct cause of the failure was a broken conductor within the FRV position modulator (ZM1621). The root cause of this event was the fact that design choices made by the vendor resulted in a less robust wire connection. This event was of low safety significance and had no impact on public health or safety. There were no systems, structures, or components inoperable at the time of the event and none that contributed to the event. This event is reportable pursuant to 10CFR50.73(a)(2)(iv)(A). There were no radiological releases associated with this event.
3332018001 | FitzPatrick | 12/05/2018 | 02/01/2019 | ML19032A63 | <strong>Secondary Containment Differential Pressure Exceeded the Technical Specification Surveillance Requirement</strong><br /><i>Abstract:&nbsp;</i>At 1010 on December 5, 2018, Secondary Containment differential pressure exceeded the Technical Specification Surveillance Requirement of greater than or equal to 0.25 inches of vacuum water column. The highest Secondary Containment differential pressure was measured at a positive value of 0.06 inches water column. This condition existed for approximately 3 minutes before the differential pressure was restored to normal when the Standby Gas Treatment system was manually initiated.<br /><br /> This event was caused by a trip of the service air compressor 39AC-2A. The loss of instrument air pressure caused Reactor Building ventilation to isolate and raise Secondary Containment differential pressure. The instrument air pressure was restored when 39AC-2A was isolated and the two backup air compressors started. <br /><br /> This condition did not impact the ability of the Standby Gas Treatment system to establish and maintain the required negative pressure in the containment structure. When Secondary Containment did not meet the Technical Specification Surveillance Requirement 3.6.4.1.1 for differential pressure, the Limiting Condition of Operation (LCO) was not met. Therefore, Secondary Containment was inoperable. This event was being reported under 10 CFR 50.72(b)(3)(v)(C).
3352018001 | St. Lucie 1 | 10/29/2018 | 12/26/2018 | ML18360A04 | <strong>Feedwater Heater Level Control Malfunctions Resulted in Lowering Steam Generator Water Level and Manual Reactor Trip</strong><br /><i>Abstract:&nbsp;</i>On October 29, 2018, St. Lucie Unit 1 was in Mode 1 at 100 percent reactor power. At 1258 hours the control room was alerted to abnormal water levels in the 4B feedwater heater. Troubleshooting was unable to determine the cause and at 1304 hours the 1B steam generator water level began to decrease. The operators initiated a rapid downpower at 1308 hours. At 1317 hours the operators executed a manual reactor scram due to 1B steam generator water level approaching procedural limits. <br /><br /> Malfunctioning feedwater heater system controllers caused the inadequate main feedwater flow and loss of steam generator water level. Legacy foreign material was removed from the 4B feedwater heater normal drain valve controller restoring that component to service; remaining susceptible controllers will be visually inspected for foreign material. Preventative maintenance practices allowed abnormal wear on the normally closed 4B feedwater alternate drain valve controller and the controller was replaced; preventative maintenance practices are being revised to account for this failure mechanism.<br /><br /> The operators and plant responded as trained and designed for the feedwater system failures. The resultant trip was uncomplicated and plant risk remained green. There was no adverse effect on the health and safety of the public.
3362018001 | Millstone 2 | 10/23/2018 | 12/19/2018 | ML19022A26 | <strong>Loss of Both Trains of Control Room Emergency Ventilation Resulting in the Loss of Safety Function</strong><br /><i>Abstract:&nbsp;</i>During surveillance testing on October 23, 2018, with Millstone Power Station Unit 2 in Mode 6 it was discovered that Control Room Envelope (CRE) air in-leakage exceeded the allowable limit of the Control Room Habitability Program. The test results found the air in-leakage for both trains of Control Room Emergency Ventilation did not meet the Control Room Habitability Program requirements rendering the Control Room Envelope inoperable. Technical Specification Action Statement 3.7.6.1.e was entered and the required Limiting Condition for Operation actions were completed. The condition was reported to the NRC pursuant to 10 CFR 50.72(b)(3)(v)(D) via an 8-hour prompt report (NRC Event Notice EN 53688). This is being reported pursuant to 10 CFR 50.73(a)(2)(v)(D) as an event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident. <br /><br /> The direct cause of the inoperability of the CRE was determined to be the air in-leakage through multiple degraded components, including a partially open duct access hatch, degraded door seals and latches, an open loop seal, a degraded area on the bottom of a cooler drain pan, and leaking charcoal filter canisters. Repairs were made to the CRE and subsequent testing indicated the safety function was restored.
3382018001 | North Anna 1 | 03/11/2018 | 05/09/2018 | ML18135A08 | <strong>1-SW-P-1B Failed to Trip During the 1J Blackout Test</strong><br /><i>Abstract:&nbsp;</i>On March 11, 2018, with Unit 1 at 0 percent power in mode 5 and Unit 2 at 100 percent power in mode 1, the Unit 1 "B" Service Water (SW) Pump failed to trip during 1J Emergency Bus blackout testing. The pump did not load shed and sequence back on the bus, as expected, but remained energized by the emergency bus during the auto start of the 1J Emergency Diesel Generator (EDG). This condition was the result of a disconnected wire on sequence timing relay 1-SW-62-1SWEB03 which in turn caused the relay to be inoperable. Investigation of why the wire was disconnected identified the most likely cause to be inadvertent manipulation of the wire during the implementation of an unrelated design change the previous refueling outage. With the inoperable sequence timing relay, this rendered the 1J EDG inoperable, though it was capable to perform its design function. In addition, redundant equipment was removed from service, including the 1H EDG for reasons other than normal testing, over the time period the 1J EDG was inoperable. This is a condition prohibited by Technical Specifications and is reportable in accordance with 10 CFR 50.72(a)(2)(i)(B). The health and safety of the public were not affected by this event.
3382018002 | North Anna 1 | 09/03/2018 | 10/23/2018 | ML18303A28 | <strong>1J Emergency Diesel Generator Auto-Start</strong><br /><i>Abstract:&nbsp;</i>On September 3, 2018, with Unit 1 at 100 percent power in mode 1 and Unit 2 at 100 percent power in mode 1, the Unit 1 "J" Emergency Bus de-energized due to a loss of the "A" Reserve Station Service Transformer (RSST). This resulted in the auto start of the 1J Emergency Diesel Generator (EDG). The loss of the "A" RSST was due to a bird strike on the "C" Phase Lightning Arrestor which caused a fault on the "C" phase on the High Side (34.5kV) of the transformer. Also, as a result of this event, the Unit 1 "A" Charging pump auto-started due to logic associated with the loss of the 1J emergency bus. The auto start of the 1J EDG is a valid System Actuation and thus reportable in accordance with 10 CFR 50.73(a)(2)(iv)(A). The health and safety of the public were not affected by this event.
3412018001 | Fermi 2 | 01/11/2018 | 02/23/2018 | ML18054A75 | <strong>Secondary Containment Pressure Exceeded Technical Specification due to Reactor Building HVAC System Manipulation</strong><br /><i>Abstract:&nbsp;</i>On January 11, 2018, at 1041 EST, a planned train swap of the Reactor Building Heating Ventilation and Air Conditioning (RBHVAC) system resulted in the Technical Specification (TS) for secondary containment (SC) pressure boundary not being met for less than one minute. The maximum secondary containment pressure recorded during that time was approximately 0.116 inches of vacuum water gauge. Secondary containment pressure was restored to within TS limits by starting Division 1 of the Standby Gas Treatment System (SLITS). There were no safety consequences or radiological releases associated with this event. <br /><br /> The cause of this momentary loss of SC was determined to he the effect of the RBHVAC West Exhaust Fan Modulating Damper failing to fully open. For corrective actions, Fermi 2 has repaired the damper.
3412018002 | Fermi 2 | 04/14/2018 | 06/12/2018 | ML18164A07 | <strong>Loss of Division 1 Offsite Power Causes Partial Loss of Feedwater Leading to ECCS Injection and Reactor Scram</strong><br /><i>Abstract:&nbsp;</i>On April 14, 2018 at approximately 1040 EDT, a reactor scram on low reactor water level occurred due to a partial loss of feedwater accompanied by a reactor recirculation system scoop tube lock. The High Pressure Coolant Injection (HPCI) and Reactor Core Isolation Cooling (RCIC) systems automatically started in order to restore reactor water level as designed. Reactor water level was subsequently maintained using RCIC. No Safety Relief Valves actuated and the Primary Containment Isolation System responded as expected. The partial loss of feedwater and scoop tube lock were caused by a loss of Division 1 electrical power which occurred following a trip of the normal feed to Transformer 64, the 13.8 kV Bus 11 Position D breaker. Division 1 Emergency Diesel Generators (EDGs), EDG-11 and EDG-12, automatically started and energized Division 1 buses. In addition, both Low Pressure Coolant Injection (LPCI) subsystems were declared inoperable while aligned to their alternate power source following loss of their normal power source. The LPCI subsystems were declared operable following realignment to their normal source after EDG-11 and EDG-12 were started. Investigation has determined the direct cause of this event to be moisture intrusion into the A6 cubicle of the Bus 1-2B enclosure, which caused a ground fault that tripped the Bus 11 Position D breaker. Immediate corrective actions were completed to eliminate moisture intrusion into the Bus 1-2B enclosure. The root cause evaluation determined that the organization failed to recognize the degradation of the Bus 1-2B enclosure as a failure mechanism of the A6 switchgear. Corrective actions to prevent recurrence include developing and implementing a Preventive Maintenance strategy for outdoor metal clad switchgear.
3412018003 | Fermi 2 | 05/27/2018 | 07/25/2018 | ML18206A68 | <strong>Inoperability of Reactor Water Cleanup System Isolation Differential Flow-High Function</strong><br /><i>Abstract:&nbsp;</i>On May 27, 2018 at 0630 EDT, the Reactor Water Cleanup (RWCU) System Isolation Differential Flow - High function was declared inoperable as a result of the RWCU Differential Flow Indicator reading downscale. This condition would have prevented the primary containment isolation valves for the RWCU system from automatically isolating on a high differential flow signal. The cause of the downscale reading was due to a capacitor failure within the square root converter. Corrective actions were taken to replace the capacitors within the square root converter and return the RWCU System Isolation Differential Flow - High function to operable on May 28, 2018 at 0046 EDT. The safety related function of the RWCU System is to provide primary containment isolation upon receipt of a primary containment isolation signal, or upon indication of a high-energy line break (HELB) in the RWCU System piping in response to the following signals: low reactor water level 2; high RWCU equipment temperatures; high RWCU pump room differential temperature; or high RWCU System differential flow. Due to the availability of other automatic RWCU isolation functions as well as the ability to manually isolate RWCU, the safety significance of this event is very low. There were no radiological releases associated with this event.
3412018004 | Fermi 2 | 05/31/2018 | 07/25/2018 | ML18206A68 | <strong>Inoperability of Reactor Water Cleanup System Isolation Differential Flow-High Function</strong><br /><i>Abstract:&nbsp;</i>On May 31, 2018 at 1420 EDT, the Reactor Water Cleanup (RWCU) System Isolation Differential Flow - High function was declared inoperable as a result of the RWCU Differential Flow Indicator reading downscale. This condition would have prevented the primary containment isolation valves for the RWCU system from automatically isolating on a high differential flow signal. The cause of the downscale reading was due to a capacitor failure within the square root converter. Corrective actions were taken to replace the capacitor within the square root converter and return the RWCU System Isolation Differential Flow - High function to operable on June 1, 2018 at 0947 EDT. Additional corrective actions included verification of the shelf life of the current inventory of capacitors and a 10-year preventative maintenance activity to replace the capacitor due to the 10-year service life. The safety related function of the RWCU System is to provide primary containment isolation upon receipt of a primary containment isolation signal, or upon indication of a high-energy line break (HELB) in the RWCU System piping in response to the following signals: low reactor water level 2; high RWCU equipment temperatures; high RWCU pump room differential temperature; or high RWCU System differential flow. Due to the availability of other automatic RWCU isolation functions as well as the ability to manually isolate RWCU, the safety significance of this event is very low. There were no radiological releases associated with this event.
3412018005 | Fermi 2 | 08/03/2018 | 09/29/2018 | ML18272A00 | <strong>Non-Functional Mechanical Draft Cooling Tower Fan Brakes Leads to HPCI Being Declared Inoperable and Loss of Safety Function</strong><br /><i>Abstract:&nbsp;</i>At 0940 EDT on August 3, 2018, the Division 2 Mechanical Draft Cooling Tower (MDCT) fans were declared inoperable due to loss of power to the over speed fan brake inverter. The MDCT fans are required to support operability of the Ultimate Heat Sink (UHS) and the Emergency Equipment Cooling Water (EECW) system. The Division 2 EECW system cools the High Pressure Coolant Injection (HPCI) system room cooler. As a result, the non-functionality of the fan brakes led to an unplanned HPCI inoperability. Since HPCI is a single train system designed to mitigate the consequences of a loss of coolant accident (LOCA), this event could have prevented the fulfillment of a safety function. The cause of the event was the failure of the Division 2 fan brake inverter. <br /><br /> Corrective Actions were taken to replace the blown fuse and inverter returning the MDCT fans, the UHS, EECW and HPCI to service on August 4, 2018 at 2151 EDT. The fan brake system is only required for a design basis tornado and there was no credible tornado threat during this event. The inverter was fully tested by Fermi 2 with assistance and guidance from the vendor NOVA. All testing was satisfactory. The fuse has been sent for failure analysis. The HPCI system is not required to mitigate a design basis tornado. The safety significance of this event is very low and there were no radiological releases associated with this event.
3412018006 | Fermi 2 | 10/19/2018 | 12/14/2018 | ML18348B11 | <strong>Emergency Diesel Generator Load Sequencer Inhibits Automatic Start of Residual Heat Removal Pumps Under Certain Scenarios due to Unrecognized Original Design Defect</strong><br /><i>Abstract:&nbsp;</i>On 10/19/2018, DTE Electric Company identified that the Engineered Safety Feature Bus degraded voltage relay scheme could inhibit all Residual Heat Removal (RHR) pumps from automatically starting and performing the Low-Pressure Coolant Injection (LPCI) function during a Loss of Offsite Power (LOP) with a non-simultaneous Loss of Coolant Accident (LOCA). At the time, Fermi 2 was in Mode 4 and automatic LPCI function was not required. However, since this condition was present from original plant design and construction, the result is past inoperability of the Emergency Diesel Generators and RHR pumps in certain non-simultaneous LOP/LOCA scenarios. This is a reportable, unanalyzed condition prohibited by Technical Specification, and additionally represents a loss of safety function, single cause inoperability of independent trains and single cause inoperability in multiple systems. The safety significance of this event is very low due to the capability of the RHR pumps to be manually started. There were no radiological releases associated with this event. <br /><br /> The root cause was an original plant design defect. A design modification to correct the design defect was implemented and successfully tested on all four degraded voltage circuits between 10/22/2018 and 10/24/2018.
3412018007 | Fermi 2 | 12/08/2018 | 02/04/2019 | ML19036A74 | <strong>Reactor Building to Suppression Chamber Vacuum Breaker Condition Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On 12/8/2018, an inconsistency was identified between the Updated Final Safety Analysis Report (UFSAR) and the original station design of the Reactor Building to Suppression Chamber vacuum breakers. The Reactor Building to Suppression Chamber vacuum breaker design includes two vacuum breakers, a check valve and a butterfly valve, in series in each of two lines from the Reactor Building to the Suppression Chamber. The UFSAR states that power is applied to automatically keep the butterfly valve vacuum breakers closed except when air is required to relieve a vacuum inside the primary containment and that a loss of power will cause the butterfly valve to open to prevent a negative differential pressure condition. Contrary to the UFSAR requirement, after losing power the original control circuit design prevented the butterfly valve vacuum breakers from re-closing once power was restored without manual Operator action. This original station design issue rendered the butterfly valve vacuum breakers inoperable and resulted in a condition prohibited by Technical Specifications. The butterfly valve vacuum breaker control circuits have been modified so that the valve operation meets the UFSAR requirements to open when power is lost and to automatically close when power is restored.
3462018001 | Davis-Besse | 12/16/2018 | 02/14/2019 | ML19050A16 | <strong>Borated Water Storage Tank Level Transmitter Out of Tolerance due to Reaching End of Expected Life</strong><br /><i>Abstract:&nbsp;</i>On December 16, 2018, with the Davis-Besse Nuclear Power Station operating at approximately 100 percent power, during a scheduled panel shift walkdown it was identified the Safety Features Actuation System (SFAS) Channel 3 Level Transmitter for the Borated Water Storage Tank (BWST) was reading lower than expected. The associated SFAS Bistable was tripped upon discovery in accordance with the Technical Specifications Required Actions. A review of plant computer data identified this transmitter had been reading lower than expected starting more than 7 hours prior to discovery, which resulted in the plant operating in a condition prohibited by the Technical Specifications. The transmitter was recalibrated and returned to service the following day; the transmitter was subsequently replaced on January 3, 2019, after it began to indicate a degrading trend. The cause of the degradation was determined to be the transmitter reaching the end of its expected service life, as the transmitter was installed during original plant construction. The remaining three BWST level transmitters have been or will be replaced. <br /><br /> This issue is being reported in accordance with 10 CFR 50.73(a)(2)(i)(B).
3482018001 | Farley 1 | 04/16/2018 | 06/12/2018 | ML18163A22 | <strong>Pressurizer Safety Valve Lift Pressure Outside of Technical Specifications Limits due to Spring Relaxation</strong><br /><i>Abstract:&nbsp;</i>On April 16, 2018, while at 0% power level and defueled, it was discovered that a Unit 1 pressurizer safety valve (PSV), which had been removed during the April 2018 refueling outage (1R28) and shipped off-site for testing, failed its as-found lift pressure test. The PSV lifted below the Technical Specification (TS) 3.4.10 allowable lift setting value. Spring relaxation of the PSV is the most likely cause of the failure.<br /><br /> It is likely that the PSV was outside of the TS limits longer than allowable by the Required Action Statement (15 minutes) during the previous operating cycle in all applicable modes of operation. Therefore, this condition is being reported in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by TS. <br /><br /> The PSV was replaced during the April 2018 refueling outage.
3522018001 | Limerick 1 | 12/07/2017 | 02/05/2018 | ML18036A98 | <strong>D12 EDG Inoperable for Greater than 30 Days Resulting in Condition Prohibited by TS</strong><br /><i>Abstract:&nbsp;</i>On December 7, 2017, during performance of the D12 Emergency Diesel Generator (EDG) Surveillance Test (ST), it was recognized that Scavenging Air temperatures were abnormally high. An investigation revealed a deficiency in the air pressure control valve. Because of this deficiency, the Air Cooler Temperature Indicating Controller was not performing correctly. The D12 EDG had run unloaded for approximately two hours, then fully loaded for approximately one hour when the condition was identified. This condition results in inoperability/ unavailability of the affected EDG and entry into a 30-day shutdown Limiting Condition for Operation (LCO). On December 12, 2017, the D12 EDG was declared operable and the LCO was exited. A past operability review determined that the D12 EDG was inoperable since the last D12 EDG 24-hr endurance run, which was began on November 6, 2017. The D12 EDG was inoperable for a period of greater than 30 days and the LCO 3.8.1.1.a actions were not completed in the required time frames provided in Technical Specifications (TS). Therefore, an Operation or Condition Prohibited by TS existed and is reportable under 10 CFR 50.73(a)(2)(i)(B).
3522018002 | Limerick 1 | 04/03/2018 | 06/04/2018 | ML18155A19 | <strong>Primary Containment Isolation Valve Failed to Fully Close Resulting in Condition Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>During the performance of reverse flushes of the Shutdown Cooling Piping for the refuel outage, the 1A Low Pressure Coolant Injection (LPCI) Outboard Injection Primary Containment Isolation Valve (PCIV) failed to fully close. The valve was manually closed and declared inoperable. Troubleshooting identified corrosion on the torque switch prevented the electrical and mechanical switches from closing on a demand signal.<br /><br /> It was determined that the PCIV was inoperable after 9/8/17 when moisture from a nearby steam leak penetrated the motor operator limit switch compartment causing a ground in the motor operator. After the ground was received the valve was declared inoperable, actions were taken to clear the ground, and the valve was returned to an operable status. Though the PCIV was closed from 9/8/17 to 3/27/18, the valve was not deenergized per Technical Specification (TS) and the PCIV is required to close to support Suppression Pool Spray operation during a Loss of Coolant Accident (LOCA); therefore, this is a violation of TS and reportable per the requirements of 10 CFR 50.73(a)(2)(i)(B).
3522018003 | Limerick 1 | 04/17/2018 | 06/18/2018 | ML18169A23 | <strong>High Pressure Coolant Injection (HPCI) Inoperability due to Main Pump Inboard Seal Leak</strong><br /><i>Abstract:&nbsp;</i>On April 17, 2018, the Unit 1 High Pressure Coolant Injection (HPCI) system was secured during surveillance testing due to a leak from the main pump inboard seal. Unit 1 HPCI System was isolated and declared inoperable at 1030. <br /><br /> A retaining collar setscrew was not properly secured during reassembly of the HPCI inboard pump seal. The retaining collar captures a split ring that secures the mechanical seal sleeve in position. During surveillance testing, the seal sleeve moved out of position resulting in the inboard seal leak. <br /><br /> Technicians performed a less than adequate inspection and did not ensure that the split ring was secured by the retaining collar. The individuals were coached and the procedure for a HPCI full pump rebuild was revised to include additional technical detail with technical hold points for pump seal reinstallation.
3532018001 | Limerick 2 | 12/08/2017 | 02/06/2018 | ML18037A91 | <strong>HPCI Inoperability due to Discharge Check Valve Failure to Close</strong><br /><i>Abstract:&nbsp;</i>On December 8, 2017, when the Unit 2 High Pressure Coolant Injection (HPCI) System was being secured following a quarterly surveillance test, the Main Control Room (MCR) received indications that the HPCI pump suction piping was pressurizing. The HPCI pump discharge check valve failed to fully close following turbine shutdown causing repeated cycling of the HPCI pump minimum flow bypass valve. The motor operated HPCI pump discharge valve located immediately downstream of the pump discharge check valve was closed to terminate pressurization of the pump suction piping.<br /><br /> With the pump discharge check valve in an indeterminate state and the motor operated pump discharge valve closed, the Unit 2 HPCI System was declared inoperable. This condition is reportable under 10 CFR 50.73(a)(2)(v)(D) as an event that could have prevented fulfillment of a safety function of a system that is needed to mitigate the consequences of an accident. An eight (8) hour Emergency Notification System (ENS) notification (#53108) was completed on December 8, 2017 at 1725 hours.
3542018001 | Hope Creek | 04/19/2018 | 06/18/2018 | ML18169A19 | <strong>Operations with a Potential to Drain the Reactor Vessel (OPDRV) Without Secondary Containment</strong><br /><i>Abstract:&nbsp;</i>From April 19 through April 29, 2018, with Hope Creek Generating Station (HCGS) in a planned refueling outage and the reactor cavity flooded in OPCON 5, HCGS performed operations with a potential to drain the reactor vessel (OPDRV) without an operable secondary containment. These operations are prohibited by Technical Specification (TS) 3. 6.5. 1; however, NRC guidance provided in Enforcement Guidance Memorandum (EGM) 11-003, Revision 3, allowed the implementation of interim actions as an alternative to full compliance. These actions were compiled in a plant procedure for controlling OPDRV activities performed at HCGS during Refueling Outages. <br /><br /> Three OPDRV activities were planned activities that were completed under the guidance of plant procedures and confirmed to have low safety significance based on the interim actions taken. Since these actions were deliberate, no cause determination was necessary. One OPDRV activity was not planned and occurred as a result of equipment failure. Consistent with the guidance provided in EGM 11-003, Revision 3, HCGS submitted a license amendment request on September 22, 2017, to adopt a Technical Specification Task Force (TSTF) traveler associated with generic resolution of this issue. <br /><br /> These conditions are being reported in accordance with 10 CFR 50.73{a)(2)(i)(B) as a condition prohibited by TS.
3542018002 | Hope Creek | 04/20/2018 | 10/03/2018 | ML18276A02 | <strong>Safety Relief Valve (SRV) As-Found Setpoint Failure</strong><br /><i>Abstract:&nbsp;</i>On April 20, 2018, Hope Creek Generating Station (HCGS) received results that the 'as-found' set-point tests for safety relief valve (SRV) pilot stage assemblies had exceeded the lift setting tolerance prescribed in Technical Specification (TS) 3.4.2.1. The TS requires the SRV lift settings to be within +/- 3% of the nominal set-point value. <br /><br /> During the twenty-first refueling outage (H1R21), all fourteen SRV pilot stage assemblies were removed for testing at an offsite facility. Between April 20 and May 11, 2018, HCGS received the test results for all fourteen of the SRV pilot valve assemblies. A total of eight of the fourteen SRV pilot stage assemblies experienced set-point drift outside of the TS 3.4.2.1 specified values. All of the valves failing to meet the limits were Target Rock Model 7567F two-stage SRVs. <br /><br /> This is a condition reportable under 10 CFR 50.73(a)(2)(i)(B) as an Operation or Condition Prohibited by Technical Specifications. <br /><br /> The cause of the set-point drift for the eight SRV pilot stage assemblies is attributed to corrosion bonding between the pilot disc and seating surfaces, which is consistent with industry experience. This conclusion is based on previous cause evaluations and the repetitive nature of this condition at HCGS and within the BWR industry.
3542018003 | Hope Creek | 04/18/2018 | 09/12/2018 | ML18255A23 | <strong>Feedwater Isolation Valve Leakage Exceeded Technical Specification Limit</strong><br /><i>Abstract:&nbsp;</i>On April 18, 2018, with Hope Creek Generating Station (HCGS) in a planned refueling outage, HCGS performed a required surveillance test of the long term seal of the feedwater lines. The test criteria could not be met due to leakage past feedwater isolation valve H1AE -AE-HVF032B. The valve is sealed with a water seal from the High Pressure Reactor Coolant (HPCI) system, or Reactor Core Isolation Cooling (RCIC) system, to form a long-term seal boundary of the feedwater lines. The valve is tested per Technical Specification Surveillance Requirement 4.6.1.2.g to verify a maximum leak rate of 10 gpm at a test pressure of 55.7 psig. During the test, a test pressure of 44 psig was the highest pressure that could be obtained, which does not meet the acceptance criterion.<br /><br /> This condition is being reported in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by plant Technical Specifications.
3542018004 | Hope Creek | 09/26/2018 | 11/20/2018 | ML18324A61 | <strong>High Pressure Coolant Injection System Inoperable due to Failed Fuse</strong><br /><i>Abstract:&nbsp;</i>On September 26, 2018, at 1530 the High Pressure Coolant Injection (HPCI) system became inoperable due to a failed fuse in channel 'A' of the system initiating logic. At the time of the failure Hope Creek was in Operational Condition 1 at 100% power. The failed fuse also affected the 'A' channel of the Core Spray and Low Pressure Coolant Injection (LPCI) sub-systems. The HPCI system can be initiated by either of two channels, designated as 'A' channel and 'C' channel. The 'C' channel of the HPCI system remained functional. The fault was isolated to a single component associated with the HPCI system high water level trip (level 8). With the fault isolated, power was restored to the remaining effected portions of the 'A' channel ECCS systems at 2101 on September 26, 2018. <br /><br /> With power restored to the other circuits, the 'A' Core Spray and 'A' LPCI subsystems were restored to operable. The HPCI system remained inoperable in accordance with plant Technical Specifications. HPCI was restored to operable status on September 27, 2018 at 1755, following replacement of the effected component, a trip unit, associated with the 'A' channel high water level switch.<br /><br /> These conditions are being reported in accordance with 10 CFR 50.73(a)(2)(v)(D) as a condition that could have prevented the fulfillment of a safety function.
3692018001 | McGuire 1 | 02/16/2018 | 05/17/2018 | ML18145A09 | <strong>Valid Actuation of the Unit 1 Reactor Protection System and Auxiliary Feedwater System</strong><br /><i>Abstract:&nbsp;</i>At 1014 [EST] hours on February 16, 2018, with Unit 1 in Mode 1 at approximately 100 percent power, the reactor was tripped when the 1B Reactor Auxiliary Trip Breaker was actuated during Train B Solid State Protection System (SSPS) testing. The trip was uncomplicated with all systems responding normally post-trip. Operations manually started the motor driven auxiliary feedwater pumps. The turbine driven auxiliary feedwater pump auto-started on low low steam generator level in two out of four steam generators. A Feedwater Isolation occurred as designed due to the Reactor Trip and low reactor coolant system average temperature. <br /><br /> The cause was determined to be: An improper discretionary action to perform hands on verification of the reactor trip breaker position on the part of the technician. This intrusive action was not required nor directed by the SSPS procedure. <br /><br /> The cause investigation did not identify any process, scheduling, procedural, training issues with the SSPS task, or component labeling issues at the control rod drive motor generator set output breakers, that directly influenced technician's decision to take the intrusive action resulting in the reactor trip.
3732018001 | LaSalle 1, LaSalle 2 | 02/15/2018 | 04/16/2018 | ML18106A10 | <strong>Unanalyzed Condition Affecting Accident Mitigation for Tornado Generated Missile Protection Non-conformances</strong><br /><i>Abstract:&nbsp;</i>On February 15, 2018, during evaluation of protection for Technical Specifications (TS) equipment from the damaging effects of tornado generated missiles, LaSalle County Station (LSCS) identified non-conforming conditions in the plant design such that specific TS equipment is considered inadequately protected from tornado generated missiles. Specifically, tornado generated missiles could strike the components supporting the operation of the main control room ventilation (VC) and auxiliary electric equipment room ventilation (VE) systems, and the Unit 2 Division 2 480-volt motor control center 236X-1 (2AP78E). The VCNE systems provide a protected environment for occupants to control the unit following an uncontrolled release of radioactivity, hazardous chemicals, or smoke if a tornado were to occur. This condition is a legacy design issue that has existed since the original licensing of the plant. <br /><br /> This condition is reportable under multiple reporting criteria in accordance with 10CFR50.73 requirements indicated above. This condition is being addressed in accordance with NRC enforcement guidance provided in Enforcement Guidance Memorandum (EGM) 15-002, Revision 1, "Enforcement Discretion for Tornado-Generated Missile Protection Noncompliance," and DSS-ISG- 2016-01, Revision 1, "Clarification of Licensee Actions in Receipt of Enforcement Discretion per Enforcement Guidance Memorandum EGM 15-002." Compensatory measures have been implemented in accordance with these documents.
3732018002 | LaSalle 1 | 02/17/2018 | 04/18/2018 | ML18108A02 | <strong>Damaged Bus Bar Identified Potentially Affecting High Pressure Core Spray System</strong><br /><i>Abstract:&nbsp;</i>On February 17, 2018, during troubleshooting for an issue with the Unit 1 "B" diesel generator (DG) oil circulating pump, station personnel identified damage of a bus bar at the breaker that supplies the DG auxiliaries. One of the loads fed from this breaker is the Division 3 DC Battery Charger. Station personnel determined that the degradation of the bus bar may have prevented the Division 3 DC battery charger from performing its function, which could have prevented the High Pressure Core Spray (HPCS) system, which is a single-train safety system, from performing its design safety function. This condition is reportable in accordance with 10 CFR 50.73(a)(2)(v)(D) as a condition that could have prevented the fulfillment of the safety function of structures or systems that are required to mitigate the consequences of an accident. Based on a subsequent review of the loads powered by the 2B cubicle, loss of any of those loads would not have prevented the 1B DG from being able to start and perform its design function. The condition of the motor control center (MCC) 143-1 (1AP79E) bus-bar was the result of a degraded connection between the "A" phase bus bar and the "A" phase bus clip (stab) associated with the breaker cubicle 2B. The apparent cause of the degraded bus bar to clip connection is due to relaxation of the bucket clip over time. The condition was exacerbated by long-term continuous ohmic heating caused by the normal currents of the loads supplied by this molded case circuit breaker. Corrective actions included replacement of the degraded clip assembly with one obtained from a spare cubicle, relocating loads to alternative spare cubicles in the affected MCC, visual inspection of all bucket-to-bus connections and repairs as necessary, and performance of a causal investigation including component failure analysis. This model of MCC used at the station is limited to Division 3 on both operating units; therefore, the extent of condition does not apply to other safety-related divisions.
3732018003 | LaSalle 1 | 02/27/2018 | 07/25/2018 | ML18206A39 | <strong>Two Main Steam Safety Relief Valves Failed Inservice Lift Inspection Pressure Test</strong><br /><i>Abstract:&nbsp;</i>During the February 2018 Unit 1 refueling outage, two main steam safety relief valves (SRV) did not pass Technical Specification (TS) Surveillance Requirement 3.4.4.1 and Inservice Testing (IST) Program lift pressure requirements. Both SRVs lifted below their expected lift pressures. On February 27, 2018, SRV 1B21-F013R was required to lift within plus or minus three percent of 1205 psi (i.e., 1205 psi plus or minus 36.1 psi), but lifted at 1167 psi. On February 27, 2018, SRV 1B21-F013U was required to lift within plus or minus three percent of 1150 psi (i.e., 1150 psi plus or minus 34.5 psi), but lifted at 1109 psi.<br /><br /> Multiple test failures are reportable under 10 CFR 50.73(a)(2)(i)(B) as an operation or condition prohibited by the plant's TS. Both SRVs lifted prior to their expected lift pressures, which is conservative regarding maintaining reactor pressure vessel over-pressure limits. Both SRVs were replaced during the outage. A failure analysis was conducted; however, it did not identify a cause for the valves lifting below their expected lift set-points.
3732018004 | LaSalle 1 | 03/22/2018 | 05/21/2018 | ML18141A63 | <strong>Technical Specification Required Shutdown due to Reactor Pressure Boundary Leakage</strong><br /><i>Abstract:&nbsp;</i>On March 22, 2018, a through-wall pipe leak was identified on a three-fourths inch vent line coming off the bonnet on a reactor recirculation pump discharge valve. This condition was reactor coolant system (RCS) pressure boundary leakage. which required entry into technical specifications (TS) actions for required shutdown. The leakage was significantly less than the 10 gallons per minute emergency action threshold. At the time of discovery, Unit 1 was in Mode 1. A controlled shutdown of Unit 1 was performed, having all necessary shutdown equipment available; and, there was no impact to Unit 2. This condition was reported on March 22. 2018 (ENS 53276) in accordance with 10 CFR 50.72(b)(2)(i) for plant shutdown required by Technical Specifications and 10 CFR 50.72(b)(3)(ii)A for the pressure boundary leakage as a principal safety barrier being in a degraded condition. <br /><br /> The cause for the steam leak on the vent line was determined to be fatigue cracking that initiated on the external surface of the pipe at the toe of the socket fillet weld. Crack propagation occurred under low cycle fatigue conditions. In addition, the fracture surface contained deformation features which were indicative of a potential high nominal stress. Actions were taken to repair the vent line after plant shutdown and perform failure analysis on the degraded component. This condition is reportable in accordance with 10 CFR 50.73(a)(2)(i)A as a condition that required a plant shutdown in accordance with TS and 10 CFR 50 73(a)(2)(ii)A as a principal safety barrier being in a degraded condition.
3742018001 | LaSalle 2 | 08/31/2018 | 01/15/2019 | ML19015A07 | <strong>Manual Reactor Scram due to Main Condenser Vacuum Degradation</strong><br /><i>Abstract:&nbsp;</i>On August 31, 2018, while operating at approximately 29 percent power, a reactor manual scram signal was inserted on Unit 2 due to main condenser vacuum degrading. The turbine was tripped following the scram. During the scram, one control rod did not fully insert but was manually fully inserted. The plant was in a stable condition, with reactor pressure being maintained by the turbine bypass valves, and reactor water level was controlled using feedwater. Except for the single control rod insertion, required safety systems and shutdown equipment performed as expected, and there was no impact to Unit 1. This condition was reported on August 31, 2018 (ENS 53576) in accordance with 10 CFR 50.72(b)(2)(iv)(B) for a reactor protection system (RPS) actuation. This condition is reportable in accordance with 10 CFR 50.73(a)(2)(iv)(A) as a condition that resulted in a valid actuation of the RPS. <br /><br /> The condition was attributed to localized impingement degradation of a turbine building miscellaneous equipment drain header resulting in through-wall failure. Corrective actions were taken to install a robust welded temporary patch on the drain header, with a header replacement scheduled for the upcoming Unit 2 refueling outage L2R17 (2019), and revise procedures to incorporate lessons learned. <br /><br /> A root cause investigation identified additional corrective actions necessary to address weaknesses in the original design of the header susceptibility to localized impingement (on both units), revisions to training materials and procedures, and training and communications to engineering staff regarding piping failure mechanisms.
3822018001 | Waterford 3 | 12/20/2017 | 02/20/2018 | ML18051B50 | <strong>Failure to Enter Limiting Condition of Operation Action Statement due to Lack of Procedure Guidance Results in a Condition Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On December 8, 2017, at 1112 CST, Waterford 3 declared Containment Purge and Exhaust Isolation Area Radiation Monitor (ARM) ARM-IRE-5026 inoperable. Redundant instrument ARM-IRE-5025 was already inoperable and Technical Specification (TS) 3.3.3.1, “Radiation Monitoring Instrumentation,” action b. was entered due to the minimum instrumentation requirements of the TS were not met. On December 11, 2017 at 1907 CST, ARM-IRE-5025 was returned to service and TS 3.3.3.1 action b. was exited. During the time that ARM-IRE-5025 and -5026 were inoperable (79 hours and 55 minutes), plant personnel believed that they were complying with the appropriate actions per TS 3.3.3.1; however, it was determined on December 20, 2017 that the actions of TS 3.6.3, “Containment Isolation Valves,” should also have been complied with, resulting in a condition prohibited by TS. <br /><br /> The cause of this event was personnel failed to realize that TS 3.6.3 actions needed to be applied for the condition. Surveillance Requirement (SR) 4.6.3.2 could not be met with the inoperable instrumentation, requiring application of the TS 3.6.3 actions. Guidance that is included in the TS basis was not incorporated into the plant procedure that exists to assist with applying TS actions. Corrective action to add clarification to plant procedures to comply with TS 3.6.3 actions if the instrument requirements are not met has been completed.
3822018002 | Waterford 3 | 04/10/2018 | 07/02/2018 | ML18183A56 | <strong>Unplanned Loss of a Train of Control Room Outside Air Intake Radiation Monitors Results in a Condition Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>From 2015 to 2018 there have been four instances where a train of Control Room Emergency Air Filtration was inoperable due to a failure to meet a Technical Specification (TS) Surveillance Requirement (SR). In each instance, operators failed to take the required actions of TS 3.7.6.1, “Control Room Emergency Air Filtration System,” while a train of Control Room Outside Air Intake (CROAI) Radiation Monitors was inoperable. Plant personnel failed to recognize that SR 4.7.6.1.d.2 was no longer met during a CROAI radiation monitor train outage. This resulted in four instances of failure to meet the actions of TS 3.7.6.1 resulting in four instances of a condition prohibited by Technical Specifications. <br /><br /> The cause of this condition is that plant personnel were unaware that SR 4.7.6.1.d.2 was no longer met when a train of CROAI Radiation Monitors were inoperable. A contributing cause is that guidance was lacking in the application and intent of SR 4.0.1. Plant operators believed that the only applicable TS to the CROAI Radiation Monitors was TS 3.3.3.1, “Radiation Monitoring Instrumentation,” which Waterford 3 was in compliance with at the time of these instances. Corrective actions for this condition include changes to Operations department procedures to provide operators clear guidance on SR 4.0.1.
3872018001 | Susquehanna 1 | 04/02/2018 | 05/24/2018 | ML18144A81 | <strong>Implementation of Enforcement Guidance Memorandum (EGM) 11-003, Revision 3, During Unit 1 Refueling</strong><br /><i>Abstract:&nbsp;</i>The condition reported by this Licensee Event Report (LER) was an expected condition, which was the result of planned activities in support of a routine refueling outage. As described in the LER, the United States (U.S.) Nuclear Regulatory Commission (NRC) provided enforcement guidance, applicable to boiling water reactor licensees, that allows the reported condition. Although this allowance is provided by the NRC's enforcement guidance, the planned activities are still considered reportable in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by Technical Specifications (TS). <br /><br /> Between 04/02/2018 and 04/24/2018, Susquehanna Steam Electric Station (SSES) performed Operations with the Potential for Draining the Reactor Vessel (OPDRV) activities on Unit 1 while in Mode 5 without an operable secondary containment, as expected and allowed by the enforcement guidance. Although NRC Enforcement Guidance Memorandum (EGM) 11-003, Revision 3 allows the implementation of interim actions as an alternative to full compliance, this condition is still considered a condition prohibited by TS 3.6.4.1, Secondary Containment. The OPDRV activities were planned activities that were completed under the guidance of plant procedures and are considered to have low safety significance based on interim actions taken. Since these actions were deliberate, no cause determination was necessary. <br /><br /> There were no actual consequences to the health and safety of the public as a result of this event.
3872018002 | Susquehanna 1, Susquehanna 2 | 04/03/2018 | 05/30/2018 | ML18150A63 | <strong>Loss of Secondary Containment Differential Pressure Following Surveillance Testing</strong><br /><i>Abstract:&nbsp;</i>On April 03, 2018 at approximately 00:19, the Susquehanna control room received indication of a loss of Secondary Containment Zone 3 differential pressure, noting differential pressure less than 0.25 inches water gauge (WG). As a result, Technical Specification 3.6.4.1 Surveillance Requirement 3.6.4.1.1 was not met. The alarm came in during Unit 1 surveillance testing. <br /><br /> The condition is being reported in accordance with 10 CFR 50.73(a)(2)(v)(C) as an event or condition that could have prevented fulfillment of a safety function. The condition was previously reported on April 03, 2018, at 02:53 in accordance with 10 CFR 50.72(b)(3)(v)(C) in EN #53310.<br /><br /> The direct cause of this event was due to vendor workmanship resulting in a missing cotter pin that prevented the Unit 2, Zone 3 Supply Fan breaker from closing and remaining closed. <br /><br /> Corrective actions include installation of cotter pin on the Unit 2, Zone 3 Supply Fan breaker, replacement of electronic control device, and addition of step to identified plant procedures to ensure a retaining pin is installed prior to installation of refurbished breakers. <br /><br /> There were no actual consequences to the health and safety of the public as a result of this event.
3872018003 | Susquehanna 1 | 04/05/2018 | 09/05/2018 | ML18248A05 | <strong>Main Steam Isolation Valve Leakage due to Pilot Poppet and Pilot Poppet Seat Wear/Degradation</strong><br /><i>Abstract:&nbsp;</i>During Local Leak Rate Testing (LLRT) conducted during the recent Unit 1 refueling outage, combined as-found leakage through the inboard Main Steam Isolation Valve (MSIV) (HV141F022D) and outboard MSIV (HV141F028D) in the "D" Main Steam Line was 78,782 standard cubic centimeters per minute (sccm). Subsequent testing on April 5, 2018, measured the leakage through HV141F028D as 54,623 sccm, which exceeded the Technical Specification (TS) 3.6.1.3 limit of 100 scfh (47,194 sccm) for individual valve leakage. <br /><br /> Based on cause and history, there is firm evidence that the condition existed during the last operating cycle for longer than allowed by TS 3.6.1.3. The condition is being reported in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by Technical Specifications. <br /><br /> The cause of the leakage was identified as pilot poppet and pilot poppet seat wear/degradation. Repairs to the valve were made resulting in an acceptable as-left LLRT.<br /><br /> There were no actual safety consequences associated with the condition.
3872018005 | Susquehanna 1, Susquehanna 2 | 06/05/2018 | 12/16/2019 | ML19350A28 | <strong>Condition Prohibited by Technical Specifications due to Drift of Reactor Pressure Switches</strong><br /><i>Abstract:&nbsp;</i>On June 5, 2018, the Unit 1 "B" Reactor Steam Dome Pressure - Low permissive pressure switch, Microswitch 2 (SW2) was found outside of the Technical Specification (TS) 3.3.5.1 allowable value during testing. Subsequently, on June 6, 2018, the Unit 2 "C" Reactor Steam Dome Pressure - Low permissive pressure switch, SW2, was found outside of the TS 3.3.5.1 allowable value during testing. Both drifted outside of the lower allowable value which is intended to ensure that the Emergency Core Cooling System (ECCS) injection prevents the fuel peak cladding temperature from exceeding the limits of 10 CFR 50.46. <br /><br /> Based on the information available, the condition existed for longer than allowed by Units 1 and 2, TS 3.3.5.1 and TS 3.5.1. As such, this is a condition prohibited by TS and is being reported in accordance with 10 CFR 50.73(a)(2)(i)(B). This is also considered a common cause inoperability of independent trains or channels (10 CFR 50.73(a)(2)(vii)), a condition that could have prevented fulfillment of a safety function (10 CFR 50.73(a)(2)(v)(D)), and a single cause that could have prevented fulfillment of safety functions of trains or channels in different systems (10 CFR 50.73(a)(2)(ix)(A)). <br /><br /> The direct cause was determined to be instrument setpoint drift resulting from an over-ranged condition and the effects of the movement assembly on the torque tube. Interim compensatory actions include performing calibration using the quarterly calibration procedures every 45 days on Unit 1 and every 30 days on Unit 2. Final corrective actions will include installing Cameron-Barton 288A instruments that have been modified to remove the over-range condition and the movement assembly/associated linkages that were determined to be affecting instrument drift.<br /><br /> There were no actual consequences to the health and safety of the public as a result of this event.
3872018006 | Susquehanna 1 | 09/26/2018 | 12/19/2018 | ML18353A43 | <strong>Standby Liquid Control Valve Failed Surveillance Test</strong><br /><i>Abstract:&nbsp;</i>During the performance of the quarterly flow verification, the 1A Standby Liquid Control (SBLC) Pump could not obtain the Technical Specification required flow of 40 gallons per minute due to the SBLC Injection Pump 'A' Discharge Pressure Relief Valve (PSV148F029A) lifting and being unable to reseat itself. This failed to meet the requirements of Technical Specification Surveillance Requirement 3.1.7.7 and consequently, the 1A SBLC pump was declared inoperable. <br /><br /> This condition is being reported in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by technical specifications and 10 CFR 50.73(a)(2)(v)(A) as a condition that could have prevented fulfillment of a safety function. The 'B' train of Standby Liquid Control had been unavailable during the time the 'A' was inoperable.<br /><br /> The cause of the event was determined to be inadequate work instructions for installing the insulation on the associated relief valves. Corrective actions include additional guidance for installing insulation around the relief valves.<br /><br /> There were no actual safety consequences associated with this event.
3882018001 | Susquehanna 2, Susquehanna 1 | 02/11/2018 | 04/11/2018 | ML18101A26 | <strong>Loss of Secondary Containment Differential Pressure During Entry into Unit 2 Zone 3 Exhaust Plenum</strong><br /><i>Abstract:&nbsp;</i>On February 11, 2018 at 22:03, the Susquehanna control room received indication of a loss of Secondary Containment Zone 2 differential pressure and noted differential pressure less than 0.25 inches water gauge (WG) for several seconds. As a result, Technical Specification 3.6.4.1 Surveillance Requirement 3.6.4.1.1 was not met due to loss of Secondary Containment differential pressure and Technical Specification 3.6.4.1 was entered. The alarm came in during an entry into the Unit 2 Zone 3 exhaust plenum for plenum checks. This event is similar to the event that occurred on November 30, 2017 (LER 50-387(388)/2017-007-00). <br /><br /> The condition is being reported in accordance with 10 CFR 50.73(a)(2)(v)(C) as an event or condition that could have prevented fulfillment of a safety function. The condition was previously reported on February 11, 2018, at 23:36 in accordance with 10 CFR 50.72(b)(3)(v)(C) in EN #53202. <br /><br /> This event was unable to be replicated under various scenarios and no obvious equipment issues were identified. A sign was installed on the Unit 2 Zone 3 exhaust plenum door that states: "Entry into the plenum may impact secondary containment, notify control room prior to entry to evaluate LCO requirements." <br /><br /> There were no actual consequences to the health and safety of the public as a result of this event.
3892018001 | St. Lucie 2 | 09/11/2018 | 12/17/2018 | ML18351A24 | <strong>Pressurizer Instrument Nozzle Leak due to Primary Water Stress Corrosion Cracking</strong><br /><i>Abstract:&nbsp;</i>On September 11, 2018, during Unit 2 refueling outage augmented ISI bare metal visual inspection activities, a through wall flaw was discovered on a Class 1 pressurizer level instrument nozzle. <br /><br /> The flaw was most likely caused by primary water stress corrosion cracking (PWSCC), a known failure mechanism for Alloy 600/82 weld material. The affected small bore pressurizer nozzle was replaced prior to startup from the refueling outage. The lower temperature service conditions for the remaining Alloy 600 components support continued operation through the end of licensed life for St. Lucie Unit 2. <br /><br /> The flaw was found as part of the Alloy 600 Management Program and within the ISI augmented inspection frequency. <br /><br /> This LER Revision adds reporting criterion 50.73(a)(2)(i)(B) and discusses the nature of the through wall flaw.
3892018002 | St. Lucie 2 | 10/12/2018 | 12/10/2018 | ML18344A42 | <strong>Automatic Reactor Trip due to a Breaker Failure on the 2A1 6.9kV Bus</strong><br /><i>Abstract:&nbsp;</i>On October 12, 2018 at 1353 EDT with St. Lucie Unit 2 in Mode 1 at 100% Reactor power, an unplanned automatic Reactor trip occurred due to a failure of a supply breaker to the non-safety related 2A1 6.9kv bus during a transfer of the bus power supply from the 2A Auxiliary Transformer to the 2A Startup Transformer. The breaker failure caused a fire in the cubicle that was extinguished by onsite personnel. <br /><br /> The initial breaker problem developed after it was placed in service. However, there was no viable option to unload the breaker before opening. A team was formed to determine the options for resolving the condition. The option chosen was to use normal procedures with contingencies in place. The failure occurred as the damaged breaker was removed from service. The fault inside the breaker was the result of a ruptured SF6 gas vessel due to an inadequate design. <br /><br /> The failed breaker has been removed from service, and similar breakers susceptible to interrupter vessel failures are being evaluated for replacement. Additionally, action plans are being developed that will allow similar beakers to be unloaded in the event of future interrupter vessel failures. <br /><br /> Following the uncomplicated trip, the plant was maintained in Mode 3. Therefore, this event had no safety significance.
3902018001 | Watts Bar 1 | 01/10/2018 | 03/12/2018 | ML18071A19 | <strong>Failure to Replace Capacitors Results in Inoperable 120 VAC Vital Inverter</strong><br /><i>Abstract:&nbsp;</i>On January 10, 2018, Watts Bar Nuclear Plant (WBN) personnel identified a concern related to the timeliness of preventative maintenance performed on the 120 VAC Vital Inverter 1-11, which was installed in March of 2005. A capacitor replacement is required by the vendor every ten years to maintain its Class 1-E qualification. or by March 13, 2015. A past operability evaluation performed on this component determined that it was inoperable from April 9, 2017 until January 10, 2018. While an installed spare inverter was available for most of this time period, there was an occasion when the spare inverter was unavailable for about 13 days. This would have exceeded the allowable out of service time for an inverter of 24 hours. and is therefore a condition prohibited by the Technical Specifications. <br /><br /> The cause of this issue is attributed to two human performance errors, one during creation of the preventative maintenance (PM) work order for the capacitor replacement and a second where an individual improperly closed the PM work order for the capacitor replacement. Upon discovery of the failure to replace the capacitors, vital inverter 1-11 was removed from service and a capacitor replacement performed. The process related to PM work order closure changed subsequent to this event such that a single individual cannot close a PM work order with no work performed without an additional review.
3902018002 | Watts Bar 1 | 01/17/2018 | 06/26/2018 | ML18177A33 | <strong>Shield Building Inoperability due to Annulus Vacuum Transient</strong><br /><i>Abstract:&nbsp;</i>At 2002 Eastern Standard Time (EST) on January 17, 2018. Watts Bar Nuclear Plant Unit 1 annulus differential pressure went outside its pressure limit. At that time, the Shield Building was declared inoperable requiring entry into Technical Specification 3.6.15 Limiting Condition for Operation (LCO), Conditions A and B. Action was taken by field operators to swap annulus vacuum control dampers due to slow system response to restore annulus differential pressure. At 2024 EST, annulus differential pressure was restored to required limits, the Shield Building was declared operable, and TS 3.6.15 LCO. Conditions A and B were exited. This is being reported as an event or condition that could have prevented fulfillment of a safety function.<br /><br /> Investigation revealed that an Emergency Gas Treatment System (EGTS) operational test on January 12, 2018, resulted in an abnormal damper configuration which contributed to this event. Following the event, tuning was performed on the actuator for control damper 1-PCO-65-49, however an equipment cause could not be confirmed. After a pressure transient on April 3, 2018 additional corrective actions were completed for 1-PCO-65-49 which included replacement of the actuator pneumatic relay and controller. The procedure for performance of the EGTS operational test will be revised to include restoration steps. Lessons learned from this event will be addressed in licensed operator training.
3902018003 | Watts Bar 1, Watts Bar 2 | 03/26/2018 | 05/24/2018 | ML18144A99 | <strong>Control Room Emergency Ventilation System Inoperable due to Main Control Room Door Being Left Open</strong><br /><i>Abstract:&nbsp;</i>At 1058 Eastern Daylight Time (EDT) on March 26, 2018, a Main Control Room (MCR) alarm was received for low control room positive pressure. At 1100 EDT, a Control Room Envelope (CRE) door was found ajar and immediately closed. Technical Specification Limiting Condition for Operation (LCO) 3.7.10, Control Room Emergency Ventilation System (CREVS), was declared not met for both trains and Condition B entered. At 1100 EDT on March 26, 2018, the alarm cleared, CREVS was declared operable and LCO 3.7.10, Condition B was exited. <br /><br /> Later that day at 1839 EDT, a MCR alarm was received for low control room positive pressure. At 1840 EDT, a CRE door was found ajar and immediately closed. Technical Specification LCO 3.7.10 for CREVS, was declared not met for both trains and Condition B entered. At 1840 EDT on March 26, 2018, the alarm cleared, CREVS was declared operable and LCO 3.7.10, Condition B was exited. <br /><br /> These events were caused by human performance errors when individuals traversing the control building complex failed to confirm the MCR envelope boundary door was properly latched. A worn latching component of the MCR envelope door contributed to this event, and was replaced. A site stand-down was conducted to brief and reaffirm to site personnel on the requirements for door closure throughout the plant. An engineering change is in development to magnetically lock the MCR door and to provide indication when the door is not fully shut and latched.
3902018004 | Watts Bar 1, Watts Bar 2 | 09/11/2018 | 11/13/2018 | ML18317A03 | <strong>Control Room Emergency Ventilation System Inoperable due to Main Control Room Door Being Left Open</strong><br /><i>Abstract:&nbsp;</i>At 0113 Eastern Daylight Time (EDT) on September 11, 2018, a Main Control Room (MCR) alarm was received for low control room positive pressure. At 0114 EDT, a Control Room Envelope (CRE) door was found ajar and immediately closed. Technical Specification Limiting Condition for Operation (LCO) 3.7.10, Control Room Emergency Ventilation System (CREVS), was declared not met for both trains and Condition B entered. At 0114 EDT on September 11, 2018, the alarm cleared, CREVS was declared operable and LCO 3.7.10, Condition B was exited.<br /><br /> This event was caused by a human performance error when an individual traversing the control building complex failed to confirm the MCR envelope boundary door was properly latched. The open control room door was identified and promptly closed. Stand-downs were conducted to brief and reaffirm to site personnel with MCR access on the requirements for door closure. A work order to install engineering features on MCR doors to ensure they are closed after opening is scheduled to be performed in January 2019.<br /><br /> This condition is being reported as an event or condition that could have prevented fulfillment of a safety function needed to mitigate the consequences of an accident in accordance with 10 CFR 50.73(a)(2)(v)(D).
3902018005 | Watts Bar 1 | 10/27/2018 | 12/19/2018 | ML18353A74 | <strong>Manual Reactor Trip due to Failure of Reactor Coolant Pump to Transfer to Normal Power</strong><br /><i>Abstract:&nbsp;</i>On October 27, 2018, at 1533 Eastern Daylight Time (EDT), Watts Bar Nuclear Plant Unit 1 reactor was manually tripped due to the number 3 Reactor Coolant Pump (RCP) normal feeder breaker failing to close during the planned power transfer to unit power following startup. Concurrent with the reactor trip, the Auxiliary Feedwater (AFW) system actuated as designed. All safety systems responded as designed. <br /><br /> During the post trip investigation, it was discovered that the normal feeder breaker for the number 3 RCP was left in the racked down (disconnected) position. The apparent cause of this event was operations personnel failed to properly implement the requirements of system status control procedures. Corrective actions include revising the system operating instructions controlling the RCP normal feeder breaker position and implementing additional training on system status control. <br /><br /> This event is being reported in accordance with 10 CFR 50.73(a)(2)(iv)(A), as a manual actuation of the Reactor Protection System (RPS) and the automatic actuation of the AFW system.
3902018006 | Watts Bar 1 | 12/11/2018 | 02/11/2019 | ML19042A00 | <strong>Containment Air Return Fan Inoperable for a Time Period Longer than Allowed by Technical Specifications due to an Inadequate Post Maintenance Test</strong><br /><i>Abstract:&nbsp;</i>At 1642 Eastern Standard Time (EST) on December 20, 2018, it was determined that both trains of Containment Air Return Fans (CARF) were simultaneously inoperable from 0817 EST to 1129 EST on November 20, 2018. This condition was reported as an unanalyzed condition that significantly degrades plant safety. It is also reportable as a condition prohibited by Technical Specifications and as a condition that could have prevented fulfillment of a safety function. <br /><br /> During the Unit 1 outage in the Fall of 2018, maintenance to replace damper seals associated with the Containment Air Return Fan system was performed. During leak testing following this maintenance, it is likely that a counterweight associated with the 1B-B CARF backdraft dampers was inadvertently moved, which resulted in an opening force greater than allowed by the design. A damper push test was not performed following the leak test to confirm that proper operation of the 1B-B CARF backdraft damper was within acceptance limits. Between the time Unit 1 entered Mode 4 and the condition was discovered, the 1A-A CARF was removed from service for testing, resulting in both trains of CARF being inoperable. Corrective actions to prevent recurrence include revising the Preventative Maintenance activity for these damper replacements to require additional post maintenance testing related to the CARF backdraft damper operation.
3912018001 | Watts Bar 2 | 04/12/2018 | 06/11/2018 | ML18162A22 | <strong>Reactor Trip on Low Reactor Coolant System Flow due to Maintenance on Flow Instrumentation</strong><br /><i>Abstract:&nbsp;</i>At 0920 Eastern Daylight Time (EDT) on April 12, 2018, the Watts Bar Unit 2 reactor automatically tripped on Reactor Coolant System (RCS) low flow in Loop 1 while operating at 100 percent power. All control and shutdown bank rods inserted properly in response to the automatic reactor trip. All safety systems including Auxiliary Feedwater actuated as designed. <br /><br /> The apparent cause of the plant trip was the failure to recognize the aggregate risk of minor maintenance being performed on the common drain line for the RCS Loop 1 flow transmitters. This maintenance caused a pressure perturbation on the common high side RCS reference leg, resulting in low flow on all three RCS loop 1 flow transmitters. The maintenance on the common drain line was not identified as work involving trip sensitive equipment during the planning process. Corrective actions include briefing affected personnel on this event, labeling the equipment as trip sensitive and revising the procedure on control of sensitive equipment.
3912018002 | Watts Bar 2 | 05/11/2018 | 07/09/2018 | ML18190A20 | <strong>Loss of Shield Building Vacuum due to Equipment Failure</strong><br /><i>Abstract:&nbsp;</i>At 1011 Eastern Daylight Time (EDT) on May 11, 2018, Containment Shield Building Annulus differential pressure exceeded the required limit. The Shield Building was declared INOPERABLE requiring entry into Technical Specification (TS) Limiting Condition for Operation (LCO) 3.6.15 Conditions A and B. The event was initiated by failure of the operating annulus vacuum fan. Main Control Room Operators manually started the stand-by annulus vacuum fan to recover pressure. The required Shield Building Annulus differential pressure was restored to the required value at 1016 (EDT) and TS LCO 3.6.15 Condition A and B were exited May 11, 2018 at 1016 (EDT). <br /><br /> The shield building transient was caused by the failure of the fan belts associated with annulus vacuum fan 2A. In addition, the hand switch for the 2B annulus vacuum fan had not been reset after actuation during a previous surveillance to permit the fan to auto start on lowering annulus vacuum. Corrective actions included replacing the fan belts for the 2A annulus vacuum fans and completing a revision of the operating procedure for the containment annulus vacuum fans to ensure the auto start feature for the vacuum fans is enabled. A preventative maintenance change request is being processed to increase the frequency for inspection and replacement, as necessary, of the annulus vacuum fans belts.
3912018003 | Watts Bar 2 | 06/22/2018 | 08/21/2018 | ML18233A32 | <strong>Reactor Trip due to Main Generator Differential Relay Actuation</strong><br /><i>Abstract:&nbsp;</i>At 0841 Eastern Daylight Time (EDT) on June 22, 2018, the Watts Bar Unit 2 reactor automatically tripped while operating at 96 percent power. All control and shutdown bank rods inserted properly in response to the automatic reactor trip. All safety systems including Auxiliary Feedwater actuated as designed. The reactor automatically tripped due to a main turbine trip. The turbine trip was caused by an electrical issue with the main generator differential current trip signal. No actual fault occurred. <br /><br /> The most probable cause of the event was an intermittent equipment failure in the A phase signal loop between the neutral side current transformer of the main generator and the digital protection relays which led to actuation of the A phase main transformer differential current relay. Initial corrective actions implemented a temporary modification to relocate the neutral side differential trip signal to a different neutral side current transformer, thus providing equivalent protection while preventing a trip from the identified likely cause of the June 22, 2018 trip. Additional work will be performed during the next Unit 2 refueling outage to correct and determine the cause of the identified intermittent equipment failure.
3912018004 | Watts Bar 2 | 07/27/2018 | 09/21/2018 | ML18264A19 | <strong>Failure to Implement Annunciator Response Process Results in a Condition Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On July 27, 2018, at 1040 Eastern Daylight Time (EDT), it was discovered that one of two purge air exhaust radiation monitors was inoperable. Technical Specification (TS) Limiting Conditions for Operation (LCO) 3.3.6, Containment Vent Isolation Instrumentation, Condition B, and TS LCO 3.6.3, Containment Isolation Valves, Condition A were entered. A review of plant data revealed that on July 26, 2018, at 1007 EDT, an unrecognized instrument malfunction alarm for Train A, Purge Air Exhaust Radiation Monitor (RM) was received in the main control room. Consequently, operations personnel did not comply with TS 3.3.6 Required Action B.1 or TS 3.6.3 Required Action A.1, resulting in a condition prohibited by TS. <br /><br /> This event was the result of Human Performance errors in implementing the annunciator response process. Corrective actions to address these human performance errors include the implementation of shift orders focused on operator standards for annunciator response and the logging of active annunciators for shift turnover. Personnel accountability actions related to this event have also been taken. <br /><br /> This event is being reported in accordance with 10 CFR 50.73(a)(2)(i)(B), as any operation or condition which was prohibited by the plant's TS.
3912018005 | Watts Bar 2 | 08/22/2018 | 10/22/2018 | ML18295A21 | <strong>Automatic Reactor Trip due to Turbine Control System Card Failure and Throttle Valve Closure</strong><br /><i>Abstract:&nbsp;</i>On August 22, 2018, at 0943 Eastern Daylight Time (EDT), the Watts Bar Nuclear Plant (WBN) Unit 2 reactor automatically tripped while operating at 100 percent power when operators changed the turbine control system from Operator Auto to Turbine Manual. All control and shutdown bank rods inserted properly in response to the reactor trip. All safety systems including the Auxiliary Feedwater (AFW) System actuated as expected. The reactor automatically tripped with a follow-on turbine trip in response to throttle valve closure. Throttle valve closure was caused by a turbine control system throttle valve manual up/down (U/D) counter card failure. <br /><br /> The card failure resulted in the closure of throttle valves which caused an initiation of a reactor trip with a follow-on turbine trip. Initial corrective actions included replacing the failed card. The main turbine analog electro-hydraulic (AEH) control system is scheduled to be replaced with a modern fault tolerant digital turbine control system. Installation is scheduled for the Unit 2 Cycle 2 refueling outage in April 2019. <br /><br /> This event is being reported in accordance with 10 CFR 50.73(a)(2)(iv)(A), as an automatic actuation of the Reactor Protection System (RPS) and the AFW system.
3952018001 | Summer 1 | 01/18/2018 | 05/07/2018 | ML18127B70 | <strong>Valid Actuation of Emergency Diesel Generator</strong><br /><i>Abstract:&nbsp;</i>On January 18, 2018 at 1202 [EST], V.C. Summer Nuclear Station (VCSNS) lost one of its two redundant offsite power supplies. The loss of the 115 kV offsite power supply created an undervoltage condition on the normal incoming Engineered Safety Features (ESF) power supply to the safety related bus 1DA. The 'A' Emergency Diesel Generator (EDG) started and loads sequenced as designed. All plant equipment and systems responded as expected. All loads were transferred back to the offsite 115 kV power supply at 1318 [EST]. The EDG was secured at 1321 [EST], and reset for auto start. Reactor power remained at 100% throughout the event.
3972018001 | Columbia | 05/18/2018 | 01/29/2019 | ML19030B26 | <strong>Automatic Reactor Scram due to Main Transformer Trip</strong><br /><i>Abstract:&nbsp;</i>On May 18, 2018, at 0651 PDT, Columbia Generating Station experienced a Main Transformer lockout relay trip. Coincident with the unplanned trip, an external line to ground fault occurred. A Reactor scram was automatically initiated by the plant in response to the transient. <br /><br /> All rods fully inserted as expected; no Emergency Core Cooling Systems actuated or injected. Plant Operators effectively maintained Reactor power, pressure and level. This event did not pose a threat to the health and safety of the public.<br /><br /> This event was reported via Event Notification #53410 under 10 CFR 50.72(b)(2)(iv)(B) as an event that resulted in actuation of the Reactor Protection System when the Reactor was critical. <br /><br /> The root cause of the Main Transformer lockout and Reactor scram was that the vendor-supplied Buchholz relay did not meet the standard performance requirements to be insensitive to external faults.
4002018001 | Harris | 04/07/2018 | 06/05/2018 | ML18156A43 | <strong>Automatic Actuation of Auxiliary Feedwater System</strong><br /><i>Abstract:&nbsp;</i>On April 7, 2018, at 0451 EDT, Shearon Harris Nuclear Power Plant, Unit 1 (HNP), was in Mode 3 following a manual shutdown for a planned refueling outage. With the "A" main feedwater pump (MFP) secured and the "B" MFP in service, the "A" and "B" motor driven auxiliary feedwater (MDAFW) pumps unexpectedly auto-started after a clearance was hung on a control power breaker circuit. The removal of power to this circuit simulated a loss of the "B" MFP, which in turn actuated the MDAFW pumps on a "Loss of Last Running MFP" auto-start signal. The "B" MFP discharge valve concurrently went in the closed direction. Operations subsequently secured the "B" MFP. <br /><br /> This event is being reported in accordance with 10 CFR 50.73(a)(2)(iv)(A) as an event that resulted in an automatic actuation of the Auxiliary Feedwater (AFW) system. The actuation of the AFW system was valid, and the system responded to plant conditions as designed. There is no safety consequence as a result of this event. The cause was attributed to a less than adequate evaluation of plant conditions required for the clearance hang and not due to any equipment failures. All plant systems responded as designed. This event did not impact the health and safety of the public.
4002018002 | Harris | 04/11/2018 | 06/07/2018 | ML18158A29 | <strong>Reactor Pressure Vessel Closure Head Penetration Nozzle Indications Attributed to Primary Water Stress Corrosion Cracking</strong><br /><i>Abstract:&nbsp;</i>On April 11, 2018, while the Shearon Harris Nuclear Power Plant was shut down for a scheduled refueling outage, the reactor vessel head was being examined in accordance with the Inservice Inspection Program. Ultrasonic examinations identified two rejectable indications in head penetration nozzle 33. <br /><br /> The two indications associated with nozzle 33 were attributed to primary water stress corrosion cracking (PWSCC), with the indications having an axial extent of 0.223 in. and 0.260 in. with a through-wall extent of 0.100 in. (16%) and 0.095 in. (15%), respectively. The indications were located on the downhill side of the nozzle at the lower toe of the J-groove weld.<br /><br /> A leak path assessment and a bare metal visual examination of the reactor vessel head was completed, with no leakage identified. The two PWSCC indications were repaired using the inside diameter temper bead weld method. The repair was completed prior to exiting the refueling outage.
4002018003 | Harris | 07/03/2018 | 08/29/2018 | ML18241A39 | <strong>Turbine Control System Auto-Stop Trip Solenoid Operated Valves Response Times Impacted</strong><br /><i>Abstract:&nbsp;</i>On June 29, 2018, the Shearon Harris Nuclear Power Plant, Unit 1, attempted to perform turbine trip testing of each individual solenoid operated valve (SOV) within the Auto-Stop Trip (AST) and Overspeed Protection Control (OPC) Quadvoter Trip Block assemblies. The response received for the first AST Quadvoter SOV was not as prescribed by procedure and the remainder of the test was aborted. Initial evaluation of the SOV response indicated that valve operation was not the cause of the test failure. Troubleshooting performed on July 3rd determined that mechanical binding (sticking) was the cause of the original test failure and impacted at least three of the four AST SOVs overall. The behavior observed constituted a vulnerability common to all four of the AST SOVs mounted on the AST Quadvoter assembly. With both AST channels rendered non-functional, the system was incapable of depressurizing the AST hydraulic header to trip the main turbine within the time response requirements of Technical Specifications. <br /><br /> The direct cause of this event was that periodic cycling of the AST SOVs was not performed at a periodicity which would prevent a common mode failure mechanism from rendering the turbine trip system non-functional. <br /><br /> Immediate action was taken to exercise the AST valves and restore functionality. The frequency for performance of AST and OPC valve testing was adjusted to a weekly periodicity, consistent with vendor recommendations.
4002018004 | Harris | 07/26/2018 | 09/20/2018 | ML18263A02 | <strong>Independent Trains of the Emergency Core Cooling System Inoperable During Testing</strong><br /><i>Abstract:&nbsp;</i>On July 26, 2018, the site was preparing to perform testing on the interlocks for isolation valves used in the residual heat removal system to isolate the suction source from the reactor coolant system. The testing was historically performed during a refueling outage, but was moved to online testing procedures prior to the previous operating cycle. Prior to performing the test, it was identified that testing per the online test procedures would result in impact on both trains of the emergency core cooling system (ECCS), rendering two independent trains inoperable simultaneously.<br /><br /> The online testing procedures were performed on three previous occasions, twice on October 6, 2016 and once on June 26, 2018. The potential for impacting both trains of ECCS was not recognized when the testing was moved to online procedures, resulting in a procedural deficiency in the online test procedures. Performance of these tests resulted in an inoperability of independent trains due to a common cause, a reportable condition per 10 CFR 50.73(a)(2)(vii). The condition lasted for less than an hour for each test performed. The resulting cross-train impact caused a train of low head safety injection (LHSI) to be inoperable simultaneously with the alternate train of high head safety injection (HHSI). For the duration of all events, a train of both LHSI and HHSI were operable. The testing procedures have since been revised to impact a single train of ECCS only.
4102018001 | Nine Mile Point 2 | 05/10/2018 | 07/09/2018 | ML18192B98 | <strong>Auto Start of Division II Emergency Diesel Generator due to Loss of Line 6</strong><br /><i>Abstract:&nbsp;</i>At approximately 0248 on May 10, 2018, while at 0% power and in Cold Shutdown (mode 4) in support of the Nine Mile Point Unit 2 (NMP2) refueling outage, NMP2 experienced a partial loss of off-site power (Line 6) during relay testing that resulted in an automatic start of the Division 2 Emergency Diesel Generator (EDG). All systems responded per design during the event. The station responded in accordance with appropriate Special Operating Procedures and restored impacted systems. <br /><br /> The condition was reported in Event Notification #53395 as an event or condition that results in a valid actuation of an emergency electrical power system, pursuant to 10 CFR.50.72(b)(3)(iv)(A). This-event is being reported as an event or condition that results in a valid actuation of an emergency electrical power system, pursuant to 50.73(a)(2)(iv)(A).
4102018002 | Nine Mile Point 2 | 08/27/2018 | 10/25/2018 | ML18306A48 | <strong>NMP2 Turbine Trip and Scram due to Unit Differential Relay Trip</strong><br /><i>Abstract:&nbsp;</i>At 0033 on August 27, 2018, Nine Mile Unit 2 (NMP2) experienced an automatic reactor scram on turbine control valve fast closure due to a turbine trip. All control rods inserted. There were no safety system actuations. In response to the turbine trip and reactor scram all systems responded per design. The station responded in accordance with appropriate procedures and restored impacted systems. The condition was reported in Event Notification #53565 as an event or condition that results in a valid RPS actuation (scram) pursuant to 10CFR.50.72(b)(2)(iv)(B). This event is being reported as an event or condition that results in a valid RPS actuation pursuant to 10CFR50.73(a)(2)(iv)(A). <br /><br /> The direct cause of this event is an actuation of the 'A' phase Unit Differential Relay, 87-2SPUY02(1) due to a grid disturbance on the 'A' phase of the 2-15 Clay - Edic transmission line. The root cause of the event is a failure of Relay & Control technicians to hold themselves accountable for use of the HU tools in preventing errors while removing grounding screws from the Unit Differential Relaying Circuitry. Corrective actions included: removal of the identified shorting screws and qualifications for those involved with the event.
4122018001 | Beaver Valley 2 | 08/12/2018 | 09/26/2018 | ML18274A08 | <strong>Technical Specification Required Shutdown due to Loss of 2P 480 Volt Emergency Bus</strong><br /><i>Abstract:&nbsp;</i>At 0158 on August 12, 2018 Beaver Valley Power Station (BVPS) Unit 2 experienced a loss of the 2P 480 Volt Emergency Bus. The loss of the bus was due to a failed over current relay on the "C" phase of the incoming power supply. Per operating procedures this was considered a Loss of Safety Function. The same procedure directed entry into Technical Specification (TS) 3.0.3. At 0358, TS 3.8.4, DC Sources-Operating, Condition D was entered due to the inoperability of the "B" train battery chargers. This required a shutdown to Mode 3 in 6 hours and Mode 5 in 36 hours if not corrected. A reactor shutdown was commenced at 0410. Unit 2 entered Mode 3 at 0843. Unit 2 entered Mode 4 at 1445. At 1824, the affected relay had been replaced. The 2P Emergency bus was tested and returned to service by 2011. At 0212, on August 13, 2018, the normal battery chargers were placed in service to restore the batteries to their required parameters. It was determined that the complete charging of the batteries would take longer than the allowed TS completion time of 36 hours to be in Mode 5. At 1130 on August 13, a Notice of Enforcement Discretion (NOED) to allow Unit 2 to remain in Mode 4 for an additional 18 hours was requested. At 1203, the NOED was verbally granted. The "B" train of batteries was restored by 2253 on August 13, at which time the NOED was terminated. This was just under 7 hours into the extension period granted by the NRC per NOED 18-1-01. <br /><br /> This event is being reported as: the completion of a plant shutdown required by the plant's Technical Specifications, 10 CFR 50.73(a)(2)(i)(A) and a condition prohibited by Technical Specifications, 10 CFR 50.73(a)(2)(i)(B).
4122018002 | Beaver Valley 2 | 10/09/2018 | 12/05/2018 | ML18341A11 | <strong>Inadvertent Automatic Actuation Signal to the Unit 2 Standby Service Water System</strong><br /><i>Abstract:&nbsp;</i>On 10/7/2018 clearances were posted that removed both trains of the Beaver Valley Power Station (BVPS) Unit 2 Standby Service Water System (SWE) from service. Per procedure, both SWE pumps were placed in Pull-To-Lock to perform inspection and testing of the Train "A" SWE Pump Discharge Isolation Valve (2SWE-MOV116A). At 1020 on 10/9/2018 valve 2SWE-MOV116A was stroked open using a locally operated switch, resulting in both trains of the Service Water System (SWS) header pressure to drop below the automatic actuation setpoint of the SWE system. As the SWE pumps were on clearance they did not respond to the actuation signal. The safety related Service Water pumps recovered the header pressure without the assistance of the SWE pumps.<br /><br /> Although this system was properly removed from service, a valid actuation signal was generated. This signal was not part of a preplanned sequence. This event is reportable per 10 CFR 50.73(a)(2)(iv)(A) as an event that resulted in the automatic actuation of an emergency service water system that does not normally run and that serves as an ultimate heat sink even though the standby service water system is non-safety related.<br /><br /> Causes were identified as a failure to perform the verbal communication prior to stroking the Train "A" SWE Pump Discharge Isolation Valve and the Operations Work Order reviews did not address the system impact that would have ensured adequate instructions were included in the Work Order to mitigate any impact on the system.
4122018003 | Beaver Valley 2 | 11/01/2018 | 12/19/2018 | ML18355A62 | <strong>Unacceptable Indication Identified During Reactor Vessel Head Inspection</strong><br /><i>Abstract:&nbsp;</i>On November 1, 2018 during the Beaver Valley Power Station, Unit No. 2 (BVPS-2) twentieth refueling outage (2R20), the results of ultrasonic examinations performed on Penetration No. 27 of the reactor vessel head did not meet the applicable acceptance criteria. The indication was not through wall and there was no evidence of leakage at this penetration based on inspections performed on top of the reactor vessel head. Because this indication could not be dispositioned as acceptable per ASME Code Section XI in a Reactor Coolant System pressure boundary it is being reported under 10 CFR 50.72(b)(3)(ii)(A) (EN 53711) and 50.73(a)(2)(ii)(A). <br /><br /> Primary Water Stress Corrosion Cracking (PWSCC) of the Alloy 600 penetration tube material was determined to be the apparent cause of the identified flaw. Reactor vessel head Penetration No. 27 was repaired in accordance with the applicable embedded flaw repair methodology which was approved by the Nuclear Regulatory Commission for use at BVPS-2. The safety significance of this indication was very low. A weld overlay of PWSCC resistant material was performed to isolate the indication.
4142018001 | Catawba 2 | 03/19/2018 | 05/16/2018 | ML18138A31 | <strong>Auxiliary Feedwater System Auto-Start due to a Loss of Both Feedwater Pumps Signal</strong><br /><i>Abstract:&nbsp;</i>On March 19, 2018, Unit 2 experienced an Auxiliary Feedwater system (CA) auto-start due to "Loss of both Feedwater (CF) Pumps" signal while the unit was in Mode 5. Maintenance was supporting restoration of an Operations clearance which was closing the sliding links associated with the hydraulic oil pressure switches for the 2B Feedwater Pump Turbine (CFPT). At the time, 2A CFPT indicated TRIPPED on the main control board and Operator Aid Computer (OAC), and 2B CFPT indicated TRIPPED on the main control board, but indicated RESET on the OAC. Once 2 out of 3 hydraulic oil pressure switches were restored, 2B CFPT logic went to a TRIPPED condition. The 2B CA Pump then started due to a valid "Loss of both CF Pumps" signal. The Control Room then secured the 2B CA Pump. The actuation occurred as designed and there was no adverse impact to plant operation. <br /><br /> The cause of this event was determined to be that the clearance on the logic circuit was not sufficiently evaluated to prevent an undesired system response between the CF and CA Systems, resulting in an auto start of the 2B CA Pump. Corrective actions include ensuring that work on the CA pump logic is not scheduled during other logic-impacting work, issue a crew learning to reinforce the responsibilities with assessing and understanding plant impacts and the standards associated with logic circuits, and performing an analysis to determine if clearance preparers, reviewers, and approvers are able to consistently and effectively apply the standards associated with understanding the impact of clearances on logic circuits.
4142018002 | Catawba 2 | 06/11/2018 | 08/13/2018 | ML18226A05 | <strong>Condition Prohibited by Technical Specifications (TS) due to Failure of the 2A Diesel Generator (DG)</strong><br /><i>Abstract:&nbsp;</i>On June 11, 2018, at 0408 hours Eastern Daylight Time (EDT) the 2A Diesel Generator (DG) was declared inoperable for planned maintenance. At 2111 EDT, during a scheduled surveillance test of the 2A DG, the output breaker ZETA-18 tripped open, caused by the actuation of the Lockout Relay 86D. The failure of the surveillance test required additional troubleshooting and maintenance. During troubleshooting, two disconnected cables were identified in the Voltage Regulator circuitry. These two cables connect the current transformer to the linear reactor. The two cables were left disconnected from the linear reactor terminal during the current maintenance activities. The cause of the disconnected cables is a failure to properly reassemble the connection after maintenance. As a result of the disconnected cables. damage occurred during the subsequent post-maintenance run that required corrective work for a duration beyond the Technical Specification (TS) required Completion Time. <br /><br /> This event is being reported under 10 CFR 50.73(a)(2)(i)(B) as an operation or condition which was prohibited by the plant's Technical Specification due to 2A EDG repair and testing exceeding the 72-hour completion time as mandated by TS 3.8.1, TS 3.7.8, TS 3.7.5, and TS 3.6.6. <br /><br /> On June 14, 2018, Catawba Unit 2 requested a Notice of Enforcement Discretion (NOED) in anticipation of exceeding TS 3.8.1, TS 3.7.8, TS 3.7.5, and TS 3.6.6. The NOED was granted by the NRC on the same day.
4162018001 | Grand Gulf 1 | 01/30/2018 | 08/07/2019 | ML19219B32 | <strong>Reactor Manual Shutdown due to Turbine Pressure Control Valve Position Changes</strong><br /><i>Abstract:&nbsp;</i>On January 30, 2018, Grand Gulf Nuclear Station (GGNS) was operating in Mode 1 at 91% power and was in the process of increasing power. At 1739 hours CST on January 30, 2018, GGNS experienced main turbine control valve (TCV) position changes of between 3 and 5 percent and main generator output load changes of approximately 20 megawatts with a periodicity of approximately 3 seconds.<br /><br /> At 1822 on January 30, 2018, operators performed a manual shut down of the reactor by moving the reactor mode switch from RUN to SHUTDOWN to place the unit in Mode 3. Upon reactor shutdown all systems performed as designed and no subsequent safety system actuations occurred. The TCV position changes were caused by an inappropriately high gain setting in one channel of the TCVs resonance compensator circuit. Corrective actions include adjustments to the control circuit, and revision of work task documents for adjustment of the control circuits. <br /><br /> There were no consequences to the general safety of the public, nuclear safety, industrial safety and radiological safety for this event.
4162018002 | Grand Gulf 1 | 02/10/2018 | 04/04/2018 | ML18094A17 | <strong>Both 208 Containment Air Lock Doors Simultaneously Inoperable</strong><br /><i>Abstract:&nbsp;</i>On February 10, 2018, at 1835 hours, while in MODE 1 at 68 percent power, the Grand Gulf Nuclear Station entered Technical Specification (TS) 3.6.1.2 Condition C for both 208 foot upper containment air lock doors being inoperable. The upper containment inner door was determined to be inoperable while the air lock outer door was tagged-out for planned maintenance. A seal air system leak test performed on the air lock inner door on February 6, 2018, had been deemed satisfactory. The outer door was subsequently taken out of service for planned maintenance and, while the outer door was out of service, an additional review of the paperwork determined that the test on the inner door was actually unsatisfactory. TS 3.6.1.2 Condition C was entered at that time. Maintenance of the outer door was completed, the air lock was returned to operable status, and ACTION C was exited at 0835 on February 11, 2018, prior to exceeding the TS action completion time of 24 hours. The cause was determined to be human error in transcribing data and interpreting test results. Analyses of test results for inner doors demonstrated that in all cases the doors and air locks remained functional and capable of maintaining containment integrity in the event of an accident. The inner doors and the air locks remained functional, containment integrity was assured throughout the events, and there was no significant impact on the health and safety of the public.
4162018003 | Grand Gulf 1 | 03/06/2018 | 04/27/2018 | ML18117A48 | <strong>Inoperable Reactor Protection Functions During Main Steam Isolation Valve and Turbine Stop Valve Channel Functional Tests due to Use of a Test Box</strong><br /><i>Abstract:&nbsp;</i>On March 6, 2018, during a review of industry operating experience, it was determined that use of the Reactor Protection System (RPS) test box described in station procedures would potentially result in the loss of two RPS reactor scram safety functions. Technical Specification (TS) 3:3.1.1 requires that RPS instrumentation for Table 3:3.1.1-1 Function 6 for Main Steam Isolation Valve - Closure (MSIV) and Function 9 for Turbine Stop Valves Closure (TSV) remain OPERABLE. It was concluded that an isolation of three of four Main Steam Lines or Turbine Stop Valves would not necessarily have resulted in a full Scram during testing, as required the TS bases, depending on the combination of closed valves occurring while the test box was in use. Modifications were approved in 2014 to accommodate the test box and surveillance procedures were revised to incorporate the use of the test box in May and June of 2016. Between May 2016 and February 2018, the MSIV Closure and TSV Closure procedures were each performed 6 times using the test box. While it did not meet the TS bases, the RPS remained functional at all times. The failure to recognize the impact of the modification and procedure revisions is considered a human performance error by engineering personnel.
4162018004 | Grand Gulf 1 | 02/18/2018 | 04/17/2018 | ML18107A15 | <strong>Potential Loss of Safety Function due to Concurrent Inoperability of Two Diesel Generators</strong><br /><i>Abstract:&nbsp;</i>On February 14, 2018, the Grand Gulf Nuclear Station Division 2 diesel generator (DG) was removed from service for maintenance. On February 18, 2018, at 0006 hours, while in Mode 1 at 97 percent power, the Division 3 DG experienced a lockout and was declared inoperable. Technical Specification 3.8.1 Condition E was entered for two DGs inoperable at that time. On February 18, 2018, at 0355 hours, Division 2 DG maintenance was completed, the diesel was returned to-service, and Condition E was exited. Division 3 DG was restored to operable status on February 18, 2018, at 1257 hours. <br /><br /> The Division 3 DG lockout was caused by inadequate operation procedures, which failed to detect an elevated jacket water temperature condition. The elevated jacket water temperature was caused by a malfunctioning jacket water temperature control switch. Corrective actions include replacement of the temperature control switch, and revision of the operation procedures.<br /><br /> Division 1 DG, which powers one low pressure core injection pump and one low pressure core spray pump, remained operable. An evaluation of Chapter 15 accident analyses demonstrated that, with just Division 1, peak cladding temperatures and cladding oxidation remained within the Cycle 21 licensing basis of <1730 degrees F and <3%, respectively.
4162018005 | Grand Gulf 1 | 03/30/2018 | 05/25/2018 | ML18145A29 | <strong>Secondary Containment Door Misaligned, due to Inadequate Criteria, Could Have Prevented Fulfillment of a Safety Function</strong><br /><i>Abstract:&nbsp;</i>On March 31, 2018, at approximately 0200, Grand Gulf Nuclear Station (GGNS) Operations personnel performed Technical Specification Surveillance Requirement (SR) 3.6.4.1.4, Secondary Containment Drawdown. During the surveillance, secondary containment pressure was unable to be maintained, as required by SR 3.6.4.1.4, and Operators in the field identified air leakage from the Auxiliary Building Rail-Bay Door. The door had been operated the previous day by supplemental personnel, who improperly seated the door, causing excessive air flow across the seals. <br /><br /> The cause of the door misalignment was a lack of criteria for determining proper door seating. The procedure has a step to inspect the door for misalignment; however, there are no match marks or quantitative metrics to compare the performance against a standard. Corrective actions include restoring door alignment and satisfactorily performing the previously failed surveillance. In addition, match marks or alignment aids will be added to the door, and referenced in the relevant procedures. <br /><br /> Engineering analyzed the results of the failed Surveillance, and determined that the GGNS dose analysis would have been preserved and the Secondary Containment safety function would have still been met. In addition, no other component or system failures contributed to this event.
4162018006 | Grand Gulf 1 | 04/05/2018 | 05/25/2018 | ML18145A29 | <strong>Secondary Containment Roof Hatch Left Open due to Inadequate Corrective Actions</strong><br /><i>Abstract:&nbsp;</i>On April 5, 2018, while at 100 percent reactor thermal power, members of the Grand Gulf Nuclear Station Unit 1 staff were assigned to perform a routine inspection of the secondary containment roof surfaces and roof drain scuppers and screens. The purpose of this inspection was to verify the materials were in good working order and to identify any condition requiring maintenance/repair. To perform this activity the station personnel accessed the roof through a normally closed access hatch. The hatch was left open during the inspection activity. The failure to close the hatch resulted a breach of the secondary containment boundary and an event/condition that could have prevent the fulfillment of a safety function.<br /><br /> The cause for roof hatch being left open has been determined to be inadequate corrective actions developed and implemented in response to a similar event (Licensee Event Report 2016-003). Specifically, the causes were inadequate work instructions and incomplete/ineffective communications between the assigned workers and control room personnel. Corrective actions for this error include closure of the hatch, establishment of interim guidance, and enhancement of the existing model work order to provide the appropriate guidance on controlling the roof hatch. <br /><br /> There were no actual nuclear safety consequences or radiological consequences during the event.
4162018007 | Grand Gulf 1 | 05/01/2018 | 06/26/2018 | ML18177A32 | <strong>Potential Loss of Safety Function (Residual Heat Removal) and System Actuation Caused by Inadvertent Valve Opening</strong><br /><i>Abstract:&nbsp;</i>On May 1, 2018, Grand Gulf Nuclear Station Instrument & Control technicians started a Reactor Vessel Water Level Transmitter Calibration Surveillance. At 1551, the technicians inadvertently opened the low pressure isolation valve instead of the equalization valve. This resulted in a decrease in sensing line pressure, which appeared as a low water level signal to the transmitters. As a result, Division 1 Emergency Core Cooling System initiated, and Shutdown Cooling was isolated. All systems responded as expected. After a 5 degree F rise in local Reactor Coolant System (RCS) temperature, Operations restored Shutdown Cooling. <br /><br /> The technicians inadvertently opened the wrong valve because of a failure to use human performance tools. In addition, Operations did not implement an adequate risk mitigation strategy for the surveillance. Both of these causes will be corrected by revising surveillances which involve replacement, calibration, or maintenance on consequential transmitters, to include hardened barriers. <br /><br /> The safety consequences of this event were low, as Shutdown Cooling was restored after only a slight rise in local RCS temperature.
4162018008 | Grand Gulf 1 | 05/11/2018 | 07/06/2018 | ML18187A40 | <strong>Unplanned System Actuation (Diesel Generator) Caused by Inadvertently Opening the Wrong Fuse Drawer</strong><br /><i>Abstract:&nbsp;</i>On May 11 2018, at 2327 with the plant in Mode 5, a Grand Gulf Nuclear Station electrical technician inadvertently opened the fuse drawer for the Bus 15AA Potential Transformer (PT) fuse instead of the Line PT fuse drawer. This resulted in an under voltage condition on the 15AA Bus, and an unplanned auto start of the Division 1 Diesel Generator. All systems responded as designed, including Standby Service Water (SSW) Pump "A", which failed to start due to the open Bus 15AA PT fuse drawer preventing the Load Shedding and Sequencing panel from sensing power restoration to the 15AA Bus. Operations secured the Diesel Generator, since SSW was not able to provide cooling.<br /><br /> The incorrect fuse drawer was opened due to a failure to use human performance tools. The technicians lacked the fundamental knowledge of, and sensitivity to, the impact of the evolution on plant operation. A Maintenance Organization Standing Order was implemented, including requirements for field walkdowns, flagging, peer checks, procedure use, and placekeeping. <br /><br /> The actual consequence of this event was an unplanned automatic start of the Division 1 Diesel Generator. There were no other actual consequences to the general safety of the public, nuclear safety, industrial safety and radiological safety for this event.
4162018009 | Grand Gulf 1 | 09/14/2018 | 08/07/2019 | ML19219B10 | <strong>Reactor Manual Shutdown due to Feedwater Level Control Changes</strong><br /><i>Abstract:&nbsp;</i>On September 14, 2018, Grand Gulf Nuclear Station (GGNS) was operating in Mode 1 at 100 percent power and performing a backfill of a 6A feedwater heater level transmitter. At 1638 hours technicians began backfilling operations of the transmitter. During the activity, GGNS experienced the 6A feedwater heater drain valve going full open and subsequent heater drain tank level control valve oscillations, which resulted in automatic condensate booster pump and feedwater pump trips on low suction pressure. The feedwater pump trip was followed by a reactor recirculation flow control valve runback. At 1644 hours operators performed a manual reactor protection system shut down of the reactor to place the unit in Mode 3. Upon reactor shutdown all systems performed as designed and no subsequent safety system actuations occurred. The root cause of the event was that test instructions did not include dynamic tuning of Air Operated Valves. The cause of the manual shutdown was operator response in anticipation of reactor water level lowering to the 11.4 inch automatic scram setpoint. Corrective actions included adjustments to the heater drain tank level control circuit. There were no consequences to the general safety of the public, nuclear safety, industrial safety or radiological safety for this event.
4162018010 | Grand Gulf 1 | 12/12/2018 | 07/11/2019 | ML19192A06 | <strong>Reactor Manual Scram due to Main Steam Bypass Stop and Control Valve A Drifting Open</strong><br /><i>Abstract:&nbsp;</i>At approximately 1351 hours on Wednesday, December 12, 2018, while operating in MODE 1 at approximately 100 percent power, the Grand Gulf Nuclear Station was manually shutdown in response to Main Steam Bypass Stop and Control Valve A drifting open. The Main Steam Line Isolation Valves were manually closed as a mitigating action to control reactor pressure vessel rate of depressurization and cooldown. During the scram recovery, the Reactor Core Isolation Cooling (RCIC) System injection was delayed. During preparation to initiate High Pressure Core Spray (HPCS) System the operator noted that RCIC had started to inject but due to the water level and the rate of change the operator started HPCS. HPCS was secured once water level was trending higher. RCIC was utilized for reactor water level control until RCIC was placed in standby at 1645 hours. There were no consequences to the general safety of the public, nuclear safety, industrial safety and radiological safety for this event. <br /><br /> The direct cause of the condition is a failed linear variable differential transformer (LVDT) in the actuator for the Main Steam Bypass Stop and Control Valve A. The cause of the event was the existing operating guidance for the turbine electro hydraulic control (EHC) did not provide procedural steps to manually swap from a faulty controller to an auxiliary controller, which would have allowed the operators to close the valve. Corrective actions included swapping wiring from the failed LVDT to an installed spare LVDT and enhancement of the procedural guidance to ensure operators have the tools to manually swap from a faulty controller to an auxiliary controller. This report is made pursuant to 10 CFR 50.73(a)(2)(iv)(A) for any event or condition that resulted in manual or automatic actuation of systems as listed in 10 CFR50.73(a)(2)(iv)(B), specifically the Reactor Protection System, HPCS, and RCIC systems were actuated.
4242018001 | Vogtle 1 | 07/03/2018 | 08/30/2018 | ML18242A36 | <strong>Manual Reactor Trip due to High Steam Generator Water Level</strong><br /><i>Abstract:&nbsp;</i>At 0954 EDT on July 3, 2018, with Unit 1 in Mode 1, 100 percent power, the reactor was manually tripped due to high steam generator water level. The high steam generator water level was caused by a controller failure on Heater Drain Tank B which led to a feedwater oscillation on the secondary side of the plant. This oscillation caused steam generator water levels to increase. Control Room operators monitored this increase and manually tripped the plant prior to reaching the automatic trip setpoint. <br /><br /> The unit was stabilized in Mode 3 with decay heat removed through the main steam lines through the steam dumps and into the condenser. <br /><br /> This event had no adverse effects on the health and safety of the public and is of very low safety significance. This event is reportable under 10CFR50.73(a)(2)(iv)(A) due to manual actuation of systems listed in 10CFR50.73(a)(2)(iv)(B). Unit 2 was not affected.
4242018002 | Vogtle 1 | 10/04/2018 | 12/03/2018 | ML18337A18 | <strong>Manual Reactor Trip due to Receiving Rod Control Urgent Failure Alarm During Low Power Physics Testing</strong><br /><i>Abstract:&nbsp;</i>At 0544 EDT on October 4, 2018, with Unit 1 in Mode 2 with reactor power in the intermediate range performing Low Power Physics Testing, the reactor was manually tripped due to a Rod Control Urgent Failure alarm. The trip was not complex, with all systems responding normally. Operations stabilized the plant in Mode 3. Decay heat was removed through the main steam system through the steam dumps and into the condenser. <br /><br /> This event had no adverse effects on the health and safety of the public and is of very low safety significance. This event is reportable under 10CFR50.73(a)(2)(iv)(A) due to manual actuation of systems listed in 10CFR50.73(a)(2)(iv)(B). <br /><br /> Unit 2 was not affected.
4402018001 | Perry | 11/06/2016 | 03/28/2018 | ML18088A06 | <strong>Loss of Safety Function and Violation of Technical Specifications due to Diode Failure</strong><br /><i>Abstract:&nbsp;</i>On November 6, 2016, while the plant was at 100 percent rated thermal power, during logic system testing of the Division 2 Diesel Generator (DG), the DG control power breakers tripped. This resulted in loss of control power to the Division 2 DG. It was later discovered that a shorted diode, in parallel with a control circuitry relay, had caused the control power breakers to trip.<br /><br /> The NRC later determined that due to the degradation of the diode, the Division 2 DG had been inoperable since April of 2015 when this particular portion of the control circuitry was last energized. This resulted in an operation or condition prohibited by the plants technical specifications as the DG was inoperable for longer than its 14 day allowed outage time. In addition, during this time period, the Division 1 DG was inoperable at various times for surveillance testing and maintenance, resulting in a loss of safety function for both DG's being inoperable at the same time. The cause of this event was a manufacturing defect in the diode and inadequate design controls over the DG control circuitry. Corrective actions included removal of the diodes from both Division 1 and 2 DG control power circuit and a review of past design changes to verify failure modes have been considered for any new components. The safety significance of this event was determined to be of low to moderate safety significance. This event is being reported under 50.73(a)(2)(i)(B) for an Operations or Condition Prohibited by Technical Specifications and under 50.73(a)(2)(v)(D) for a Loss of Safety Function.
4402018002 | Perry | 07/01/2018 | 08/23/2018 | ML18236A29 | <strong>Failed Fuse Leads to Loss of Safety Function</strong><br /><i>Abstract:&nbsp;</i>On July 1, 2018, at 0100 hours, while the plant was at 100 percent rated thermal power, a portion of the Division 1 Emergency Core Cooling System (ECCS) Loss Of Coolant Accident (LOCA) initiation logic was declared inoperable due to the discovery of a failed fuse. The fuse was replaced and the Division 1 ECCS LOCA initiation logic was declared operable at 0230 hours on July 1, 2018. The failed fuse caused the loss of a portion of the Division 1 ECCS LOCA initiation logic, which would have prevented the initiation of the Emergency Closed Cooling (ECC) A system. This resulted in ECC A and its supported systems to be declared inoperable. Low Pressure Core Spray (LPCS) is one of those supported systems and is considered a single train safety system. Inoperability of LPCS is considered an event or condition that could have prevented the fulfillment of a safety function. The failed fuse also caused the loss of a portion of the initiation logic, which would have prevented the automatic isolation of the Nuclear Closed Cooling system and Instrument Air to containment. The loss of containment isolation capability is also considered an event or condition that could have prevented the fulfillment of a safety function. <br /><br /> The cause of the Gould Shawmut TR30R fuse failure is due to a manufacturing defect. Immediate corrective actions replaced the failed fuse. The spare fuse inventory was inspected, and suspect fuses were removed. Inspections are planned for circuits that were identified that could have the suspect fuses. If a suspect fuse is found, it will be replaced.<br /><br /> The safety significance is very small. This issue is being reported in accordance with 10 CFR 50.73(a)(2)(v)(D) as a condition that could have prevented the fulfillment of a safety function. This LER satisfies the evaluation, notification, and reporting obligation to report defects under 10 CFR 21.2(c).
4402018003 | Perry | 10/04/2018 | 11/30/2018 | ML18334A36 | <strong>Unanalyzed Condition Resulting from Unfused Alternating Current Control Circuits</strong><br /><i>Abstract:&nbsp;</i>During a recent NRC inspection, it was discovered that Perry Nuclear Power Plant (PNPP) has an unfused circuit that crosses multiple safety-related fire zones. The resulting extent of condition review found an additional two components with unfused circuits also crossing multiple safety-related fire zones. Without overcurrent protection for these circuits, the potential exists that an initial fire event affecting these circuits could cause short circuits that would cause excessive current through the circuits beyond the capacity rating of the conductors. This could lead to a secondary fire in another plant area where the circuits are routed, challenging the ability to achieve and maintain safe shutdown. Compensatory fire watches have been established for the areas affected. Planned corrective actions include plant modifications to install overcurrent protection in the affected circuits. <br /><br /> These events are being reported under 10CFR50.73(a)(2)(ii)(B) as an unanalyzed condition. Notifications were made under 10CFR50.72(b)(3)(ii)(B), Unanalyzed Condition, on October 4, 2018 (EN 53644) and October 19, 2018 (EN 53675). <br /><br /> The cause of the event was due to a legacy issue stemming from the design and installation of the systems, prior to initial plant startup in 1986, that led to the vulnerability to cause a secondary fire. <br /><br /> The postulated events are considered to be of very low safety significance.
4432018001 | Seabrook | 02/06/2018 | 04/05/2018 | ML18095A68 | <strong>Pressurizer Safety Valve Outside of Technical Specification Limits Discovered During As-Found Set Point Testing</strong><br /><i>Abstract:&nbsp;</i>On February 6, 2018, with Seabrook Station at 100% power, it was determined that one of the Pressurizer Safety Valves (PSVs) had a high as-found set point pressure which was discovered during off site testing after the valve was removed from service during the previous refueling outage (04/08/17). Technical Specifications (TS) require three pressurizer safety valves to be operable, with a lift setting of +/- 3% in Modes 1, 2 & 3. One safety valve had as-found set point of +6.1%, the other two were within the +/- 3% tolerance. Although the TS limit was surpassed, the ASME code limitation of 110% design pressure was not exceeded. The contributing cause of the excessive set point pressure is attributed to set point drift. A direct cause of the excessive set point drift was not able to be determined. The Corrective Action was to replace the spring. Following that, additional testing was performed to ensure the valve meets design specifications and would be suitable for future service. The additional testing was satisfactory and within design specifications.
4432018002 | Seabrook | 07/25/2018 | 09/19/2018 | ML18262A40 | <strong>Automatic Valve in Emergency Core Cooling System Inoperable</strong><br /><i>Abstract:&nbsp;</i>On 7/25/2018, it was discovered that the A Train Centrifugal Charging Pump (CCP) Flow Loop, 1-CS-F-7325, failed low which would have prevented CS-V-196, A Train CCP miniflow isolation valve from closing during a SI signal coincident with a charging pump flow greater than 122.5 gpm. Closing CS-V-196 directs the charging pump flow to Emergency Core Cooling (ECCS) injection. Failure of CS-V-196 to close diverts flow away from core cooling during a safety injection event. At the time of the event, the alternate train CCP, 1-CS-P-2B, was tagged out of service for maintenance for 12 hours and 28 minutes. <br /><br /> Technical Specification (TS) 3/4.5.2 requires two independent Emergency Core Cooling System (ECCS) subsystems OPERABLE which includes one OPERABLE CCP in each train. On 7/25/18 from 0629 to 1857, while 1-CS-P-2B was tagged out for maintenance, both trains were inoperable. TS Surveillance Requirement (SR) 3/4.5.2 requires that each automatic valve in the flow path be verified to actuate to the correct position. Since CS-V-196 would not have been capable of closing, it was incapable of meeting SR 4.5.2.e. <br /><br /> These conditions are reportable in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by Technical Specification and 50.73(a)(2)(v)(D) as a condition that could have prevented fulfillment of a safety function.
4432018003 | Seabrook | 09/27/2018 | 11/26/2018 | ML18330A20 | <strong>Overpower Delta T Setpoint Exceeded Allowable Value for Time Longer than Permitted by the Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On September 27, 2018 with the plant operating in Mode 1, control room operators discovered spiking and elevated operation of the reactor coolant loop 4 overpower delta T (OPDT) setpoint during a computer trend review. The OPDT setpoint spike and elevated operation, which exceeded its allowable Technical Specifications (TS) value, started at approximately 0200 on September 25, 2018 and remained above the allowable value until 1600 on September 26, 2018.<br /><br /> The cause of this condition was the erratic operation of one of the four associated Westinghouse 7300 cards. The corrective action was to replace all four of the 7300 cards. <br /><br /> The condition had no impact on public health and safety because the three other redundant OPDT channels remained operable during the time the loop 4 instrument was inoperable.
4462018001 | Comanche Peak 2 | 08/13/2018 | 09/30/2019 | ML19282A38 | <strong>Automatic Reactor Trip due to Turbine Trip</strong><br /><i>Abstract:&nbsp;</i>On August 13, 2018, Comanche Peak Nuclear Power Plant, Unit 2 experienced an automatic reactor trip due to an automatic turbine trip Unit 2 was at approximately 100% reactor power when the turbine tripped. Because reactor power was greater than 50% power an automatic reactor trip was initiated. The automatic turbine trip was caused by a loss of generator excitation. The loss of generator excitation also caused a generator lockout One channel of the main generator voltage regulator failed due to a power supply failure and automatically swapped to the backup channel. The primary function of the power supply that failed was to supply power to the firing thyristor in the Thyristor Voltage Regulator (TVR). Upon loss of power, firing was not possible and excitation current fell rapidly The primary channel swapped to manual prior to changing over to the backup channel The backup channel was in manual when it assumed control due to the TVR being in manual (from the primary channel) at the time of fail over. Corrective actions include replacing the failed power supply and evaluating modification of the excitation system. <br /><br /> Analysis did not identify any changes to the original submittal of LER 2-18-001-00. The failure described was the cause of the event and main generator and main turbine protection system performed as designed in response to the failed power supply. <br /><br /> All times are in Central Daylight Time (CDT).
4462018002 | Comanche Peak 2 | 12/03/2018 | 07/11/2019 | ML19199A03 | <strong>Automatic Actuation of Auxiliary Feedwater System</strong><br /><i>Abstract:&nbsp;</i>At 0315 on December 3, 2018, Comanche Peak Nuclear Power Plant (CPNPP) experienced a loss of the 138 kV West Bus. Since the 138 kV East Bus was out of service for transmission line maintenance, this resulted in a transfer of the Unit 2 safety buses to the alternate off site power source and an actuation of both Unit 2 blackout sequencers and an automatic start of both Unit 2 Motor Driven Auxiliary Feedwater pumps (MDAFWPs) and the Unit 2 Turbine Driven Auxiliary Feedwater pump (TDAFWP). The Emergency Diesel Generators did not start since they were not required to start due to a successful bus transfer. There was no impact on Unit 1. <br /><br /> The cause of this event was a power fault on off site equipment not owned by CPNPP. The Unit 2 MDAFWPs and the TDAFWP were stopped and returned to automatic. The off site source was recovered at 0416 on December 3, 2018. All times in this report are approximate and Central Standard Time unless noted otherwise.
4552018001 | Byron 2 | 07/06/2018 | 08/29/2018 | ML18241A05 | <strong>Byron Unit 2 Automatic Safety System Actuation due to System Auxiliary Transformer 242-2 Failure and Subsequent Unit 2 Loss of Offsite Power (LOOP)</strong><br /><i>Abstract:&nbsp;</i>On July 6, 2018 at 1201 hours, with both units at Byron Station operating at approximately 100% power, Station Auxiliary Transformer (SAT) 242-1 and SAT 242-2 tripped due to a fault on SAT 242-2, causing a Loss of Offsite Power (LOOP) on Unit 2 and safety system actuation. SAT 242-2 experienced a fault and tripped on differential relay and sudden pressure relay actuation. <br /><br /> The root cause of the SAT 242-2 failure is indeterminate. The failure was the result of an aggregate contribution of multiple events, including operation with a sustained open phase in 2012 and a partial oil drain and refill to replace a degraded bushing in 2018, which degraded the dielectric qualities of the SAT 242-2 transformer insulation.<br /><br /> The corrective actions planned include installing a replacement transformer and implementing standard fleet guidance that directs the review and consideration of original equipment manufacturer (OEM) input for internal transformer maintenance and any associated oil drain and refill actions. <br /><br /> This condition is reportable as an LER in accordance with 10 CFR 50.73(a)(2)(iv)(A) for any event or condition that resulted in manual or automatic actuation of any of the systems listed in 10 CFR 50.73(a)(2)(iv)(B).
4562018001 | Braidwood 1 | 04/19/2018 | 06/18/2018 | ML18169A35 | <strong>1A Emergency Diesel Generator Lost Voltage During a Surveillance due to a Failed Exciter Diode, Which Resulted in an Unplanned Actuation of Bus 141 Undervoltage Relay</strong><br /><i>Abstract:&nbsp;</i>On April 19, 2018 at 1152 hours, during performance of a pre-planned bus undervoltage (UV) actuation surveillance, with the 1A diesel generator (DG) solely supplying electrical power to bus 141, the 1A DG lost voltage resulting in an unplanned valid actuation of Engineered Safety Feature (ESF) bus 141 UV relay. On April 19, 2018 at 1201 hours, operators restored power to ESF bus 141 via crosstie of the Unit 2 offsite power source.<br /><br /> The cause of this event was a failed exciter "Free-Wheeling" diode in the DG exciter rotor circuit due to shorting. Corrective actions taken included replacing the exciter diode on the 1A DG. <br /><br /> This event is reportable in accordance with 10 CFR 50.73(a)(2)(iv)(A) for "Any event or condition that resulted in manual or automatic actuation of any of the systems listed in paragraph (a)(2)(iv)(B) of this section ...," specifically 10 CFR 50.73(a)(2)(iv)(B)(8) for the "Emergency ac electrical power systems, including: emergency diesel generators..."
4562018002 | Braidwood 1 | 04/20/2018 | 06/18/2018 | ML18170A13 | <strong>1B Emergency Diesel Generator Tripped on Overspeed During Testing due to Broken Close-Assist Springs on the Turbocharger Inlet Butterfly Valve While the 1A Emergency Diesel Generator Was Inoperable</strong><br /><i>Abstract:&nbsp;</i>On April 20, 2018 at 1042 hours, the 1B diesel generator (DG) was being run for a normal monthly run and subsequently tripped. Operations entered Technical Specification (TS) 3.8.2, "AC Sources - Shutdown," Condition B for the required 1B DG inoperable. The cause of this event were two broken close-assist springs on the turbocharger inlet butterfly valve. The butterfly springs were replaced, and on April 20, 2018 at 1249 hours, Operations exited LCO 3.8.2, Condition B. <br /><br /> Actions taken include: The butterfly valve springs were replaced on the 1B and 1A DGs, and inspections verified the 2A and 2B DG butterfly valve springs were intact. Additional corrective actions include revising applicable DG operating procedures to visually inspect the butterfly valve springs prior to each DG run. <br /><br /> This event is reportable in accordance with 10 CFR 50.73(a)(2)(v)(B) for "any event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to remove residual heat."
4562018003 | Braidwood 1 | 04/20/2018 | 06/14/2018 | ML18165A16 | <strong>Indications on Top Head to Upper Center Disc Weld of Reactor Head Identified due to New Inspection Standards</strong><br /><i>Abstract:&nbsp;</i>On Friday, April 20, 2018 at 1730 hours, a scheduled ultrasonic test (UT) was performed on the top head to upper center disc weld of the Unit 1 reactor head. The UT identified nineteen indications, nine of which exceeded ASME Section XI, 2001 Edition, 2003 Addenda, Paragraph IWB-3510 acceptance criteria. <br /><br /> The cause of this event was the application of new inspection standards, required by 10 CFR 50.55a(b)(xv), as provided in ASME Section XI, Appendix VIII, which required the use of new procedures, personnel qualifications and equipment during the spring 2018 refueling outage reactor vessel inspection. This resulted in the identification of subsurface flaws not previously identified using techniques applicable to prior standards. <br /><br /> An evaluation concluded the nine indications met the criteria of ASME Section XI IWB-3600 and the existing indications were deemed acceptable for two additional operating cycles. A planned corrective action is to perform an evaluation to extend acceptance of the nine indications beyond the next two operating cycles. <br /><br /> This event is reportable in accordance with 10 CFR 50.73(a)(2)(ii)(A), "any event or condition that results in the condition of the nuclear power plant, including its principal safety barriers, being seriously degraded."
4562018004 | Braidwood 1 | 04/22/2018 | 06/21/2018 | ML18172A09 | <strong>1A Emergency Diesel Generator Output Breaker Opened During a Surveillance Which Resulted in Unplanned Actuations of Bus 141 Undervoltage Relay</strong><br /><i>Abstract:&nbsp;</i>On April 22, 2018, during performance of a pre-planned 1A emergency diesel generator (DG) surveillance, the 1A DG output breaker tripped open on under frequency (UF), resulting in multiple unplanned actuations of bus 141 undervoltage relay. The fuel supply was secured to the 1A DG and the engine stopped. Subsequently, operators restored power to bus 141 from the Unit 1 offsite power source. <br /><br /> The cause of the UF condition was due to a combination of 1) an improperly installed time delay relay due to incorrect wiring during initial modification installation, 2) the lack of lubrication of the fuel rack, and 3) a burr between the fuel rack lever and shaft. Corrective actions taken included correcting the 1A and 2A DG wiring errors, and repair of the1A DG manual trip lever. Actions planned include revising the DG 2-year inspection procedure to include instructions for the trip lever assembly to be entirely disassembled and lubricated, document fuel rack lever inspection results for the DGs, and evaluate for a design change to the fuel rack lever to add a grease zerk fitting. <br /><br /> This event is reportable in accordance with 10 CFR 50.73(a)(2)(iv)(A) for "Any event or condition that resulted in manual or automatic actuation of any of the systems listed in paragraph (a)(2)(iv)(B) of this section, ..."
4562018005 | Braidwood 1 | 04/30/2018 | 06/28/2018 | ML18180A26 | <strong>Unit Trip on Turbine Anti-Motoring Circuit Caused by Weld Blockage of Instrument Line with a Failed Differential Pressure Switch Assembly</strong><br /><i>Abstract:&nbsp;</i>On April 30, 2018, at 1124 hours, during power ascension from refueling outage A1R20, Unit 1 tripped from approximately 48 percent power as a result of a turbine motoring generator trip. At 1126 hours, the 1A auxiliary feedwater (AF) pump was manually started to provide feedwater flow to all four steam generators. <br /><br /> The cause of the event was due to a welded-over sensing inlet line from the turbine exhaust piping in 2015, in combination with a failed differential pressure switch assembly, which allowed pressurization of all three differential pressure sensing devices resulting in the 2-out-of-3 turbine trip logic being satisfied. Corrective actions taken included installing a temporary modification opening a test switch in the Unit 1 anti-motoring circuit, and revoking the welding qualification for the welder involved in welding over the instrument sensing line. Actions planned include repairing the sensing line in the next Unit 1 refueling outage to restore function. <br /><br /> This event is reportable in accordance with 10 CFR 50.73(a)(2)(iv)(A) for "Any event or condition that resulted in manual or automatic actuation of any of the systems listed in paragraph (a)(2)(iv)(B) of this section, ..."
4562018006 | Braidwood 1 | 06/04/2018 | 08/02/2018 | ML18214A14 | <strong>Manual Unit Trip on Low Steam Generator Level Following Trip of a Turbine Feedwater Pump due to a Design Issue</strong><br /><i>Abstract:&nbsp;</i>On June 4, 2018, at 0920 hours, Braidwood Unit 1 was manually tripped due to lowering steam generator water levels following a trip of the 1C turbine driven feedwater pump. The 1A and 1B auxiliary feedwater (AF) pumps auto started as expected due to low steam generator levels. <br /><br /> The cause of the event was due to the inclusion of a digital input module in the turbine driven feedwater pump control circuitry, which affected only the safeguards testing function of the circuit, and which was not identified as a design input per the design input and configuration change impact screening procedure. Corrective actions planned include implementing the changes to eliminate the design deficiency, and revising the design input and configuration change impact screening procedure. <br /><br /> This event is reportable in accordance with 10 CFR 50.73(a)(2)(iv)(A) for "Any event or condition that resulted in manual or automatic actuation of any of the systems listed in paragraph (a)(2)(iv)(B) of this section, ..." Specifically, for 1) 10 CFR 50.73(a)(2)(iv)(B)(1) for the "Reactor protection system (RPS) including: reactor scram or reactor trip," and 2) 10 CFR 50.73(a)(2)(iv)(B)(6) for the "PWR auxiliary or emergency feedwater system."
4572018001 | Braidwood 2 | 10/08/2018 | 12/06/2018 | ML18340A01 | <strong>Reactor Coolant System Pressure Boundary Leak on a Steam Generator Bowl Drain Line due to High Cycle Fatigue Cracking Initiated from Small Welding Defects</strong><br /><i>Abstract:&nbsp;</i>On October 8, 2018 at 0000 hours, Braidwood Unit 2 was shut down for refueling outage A2R20. While performing leak inspections during the Mode 3 descending walkdown, a through-weld leak on the bowl drain line of the 2D steam generator (SG) was identified. <br /><br /> The cause of the leakage was high cycle fatigue cracking that initiated from small welding defects at the root of the socket fillet weld. Corrective actions included the replacement of the failed 2D SG bowl drain line as well as the drain lines for the remaining three SGs, using more robust socket welds and smaller weld filler rods. <br /><br /> This event is reportable in accordance with 10 CFR 50.73(a)(2)(ii)(A) for "Any event or condition that resulted in the condition of the nuclear power plant, including its principal safety barriers, being seriously degraded." This event is also reportable in accordance with 10 CFR 50.73(a)(2)(i)(B) for "Any operation or condition which was prohibited by the plant's Technical Specifications."
4582018001 | River Bend | 04/10/2018 | 06/07/2018 | ML18164A21 | <strong>Potential Loss of Safety Function of Control Building HVAC due to Legacy Design Flaw</strong><br /><i>Abstract:&nbsp;</i>On April 10, 2018, at 05:38 p.m. CDT, with the plant operating at 100 percent power, a design vulnerability in the Control Building Chill Water (HVK) logic was identified during a review of HVK Chiller and Chill Water Pump control logic. This design vulnerability could prevent the auto start of the HVK Chillers upon restoration of safety related power by emergency diesel generators following a Loss of Offsite Power. This HVK control logic vulnerability was introduced in error by a system modification in 1987. A compensatory measure was put in place to restore operability of the system until a modification can be installed to permanently remove the design vulnerability. Operators are prepared to take action in the event of a loss of Control Building Ventilation to restore the safety function in accordance with existing procedures. Therefore this condition was of minimal significance with respect to the health and safety of the public.
4582018002 | River Bend | 04/26/2018 | 06/19/2018 | ML18170A34 | <strong>Inadvertent High Pressure Core Spray Initiation and Loss of Safety Function due to Inadequate Work Instruction Mitigation Actions</strong><br /><i>Abstract:&nbsp;</i>At 15.31 CST on April 26, 2018, l&C technicians were restoring Reactor Vessel Water Level Transmitter B21-LTN081C to service with the Reactor operating in Mode 1 at 100% power. During this transmitter restoration, the station experienced an invalid initiation of High Pressure Core Spray (HPCS) with injection into tho reactor vessel. Tho HPCS Diesel Generator also started per design, but did not connect to the switchgear because there was no bus under voltage. Operations terminated the injection after approximately 40 seconds in accordance with Alarm Response Procedures. The Feedwater Level Control System responded per design, and maintained nominal Reactor water levels. The cause of this event was inadequate work instruction. This event was of minimal significance to the health and safely of the public.
4582018003 | River Bend | 04/30/2018 | 06/19/2018 | ML18170A34 | <strong>Condition Prohibited by Technical Specifications due to Untimely Recognition of Failed Laboratory Analysis of Ventilation Charcoal Sample</strong><br /><i>Abstract:&nbsp;</i>On April 30, 2018 with the Reactor operating in Mode 1 at 100% power, the results of a periodic surveillance test on Division II Control Room Fresh Air charcoal filter were received. The sample results indicated that the activated charcoal methyl iodide penetration test was above the allowable level. The test failure was determined to be due to the age of the charcoal. The condition was not immediately recognized because the sample results were received from the vendor thirteen days after the sample was obtained. This condition existed for a time longer than permitted by Technical Specifications. The activated charcoal was replaced and the filter has since been declared Operable. This event was of minimal significance to the health and safety of the public because the redundant Division I filter was Operable and available for use for the duration of the event.
4582018004 | River Bend | 05/04/2018 | 07/03/2018 | ML18184A43 | <strong>Unanalyzed Condition due to Inadequate Protection from Tornado Generated Missiles</strong><br /><i>Abstract:&nbsp;</i>On May 4, 2018 with the reactor operating in Mode 1 at 100% power, several licensing basis non-compliances associated with tornado-generated missile protection were identified in the Diesel Generator Building. Structures, Systems, or Components (SSC) affected by the non-compliances were declared inoperable. NRC Enforcement Guidance Memorandum (EGM) 5-002, Enforcement Discretion for Tornado-Generated Missile Protection Noncompliance, was utilized to change the classification of the affected SSCs from Inoperable to Operable but Nonconforming. Several days later, additional non-conformances were identified in the Control Building and Standby Cooling Tower. EGM 15-002 was utilized once again to change the classification of the affected SSCs. The identified non-compliances were introduced during original plant construction. Initial and long-term compensatory actions were put in place to meet the enforcement discretion requirements of EGM 15-002. Plans are underway to resolve the non-compliances.
4582018005 | River Bend | 06/26/2018 | 08/27/2018 | ML18239A38 | <strong>Loss of Reactor Protection System Scram Function During Main Steam Isolation Valve Channel Functional Tests due to Use of a Test Fixture</strong><br /><i>Abstract:&nbsp;</i>On June 26, 2018 during a review of industry operating experience, it was determined that use of the Reactor Protection System (RPS) test fixture described in station procedures would potentially result in the loss of one RPS reactor scram safety function. Technical Specification (TS) 3.3.1.1 requires that RPS instrumentation for Table 3.3.1.1-1 Function 6 for Main Steam Isolation Valve-Closure (MSIV) remain OPERABLE. It was concluded that the required number of Main Steam Line inputs for each RPS trip system was not maintained during the use of the RPS test fixture. Surveillance procedures were revised to incorporate the use of the test box in November 2014. Between November 2014 and May 2018, the MSIV Closure procedure was performed 15 times using the test fixture. While it did not meet the TS bases, RPS remained functional at all times. The failure to recognize the impact of the modification and procedure revisions is considered a human performance error by engineering personnel.
4582018006 | River Bend | 07/06/2018 | 09/04/2018 | ML18247A46 | <strong>Potential Loss of Safety Function and Condition Prohibited by Technical Specifications due to Emergency Diesel Generator Lube Oil Chiller Leak Caused by Design Deficiency</strong><br /><i>Abstract:&nbsp;</i>On 7/4/18 River Bend Station declared the Division II Emergency Diesel Generator (EDG) operable after completing a planned maintenance outage. On 7/4/18 immediately following the outage, the Division I EDG was declared inoperable for planned testing for approximately 4 hours. On 7/5/18 operators noted a rise in the Division II EDG lube oil filter differential pressure. A grab sample was obtained that indicated the presence of water in the lube system which led operators to declare the Division II EDG inoperable. An engineering evaluation later determined that this condition started when the Division II EDG was restored to normal operating temperature following the maintenance outage. It was then recognized that the Division I and the Division II EDG were declared inoperable simultaneously and the Technical Specification required action completion times for one inoperable EDG were not met prior to discovery of the water intrusion. The cause of the water intrusion was determined to be a design deficiency in the EDG lube oil cooler which led to a leak in the floating tubesheet seals. The leak was repaired and the Division II EDG was returned to an operable status. Design changes have been developed to correct the design deficiency and are scheduled to be in place by the end of 2019. This event had minimal significance to the health and safety of the public.
4582018007 | River Bend | 02/01/2018 | 10/31/2018 | ML18304A43 | <strong>Manual Reactor Scram due to Reactor Recirculation Pump Trip Caused by Transformer Failure</strong><br /><i>Abstract:&nbsp;</i>On February 01, 2018 River Bend Station was performing a plant startup. At approximately 27% power, an attempt was made to shift Reactor Recirculation Pump 'B' from slow to fast speed. A failure in the pump motor transformer caused the pump to trip during the upshift, requiring entry into AOP-0024, Thermal Hydraulic Stability Controls and GOP-0004, Single Loop Operation. Both procedures require monitoring core flow using the Validated Core Flow Emergency Response and Information System computer data point (WTX). When operators observed the data point they noted that it was "Suspect" and magenta in color, persuading the control room team to question the validity of WTX. The control room team engaged Nuclear IT to help resolve the anomaly. The control room team attempted to use several alternate indications of core flow, but ultimately was unable to reconcile the anomaly with the quality and color of WTX. Although the reactor was in compliance with Technical Specifications, the decision was made to conservatively shutdown the reactor. Nuclear IT contacted the operating crew several minutes after the shutdown to inform them that the data provided by WTX was indeed valid. AOP-0024 and GOP-0004 were revised, the color of "Suspect" data points was changed, and an extent of condition review was performed to determine if other transformers with the same vulnerability exist.
4582018008 | River Bend | 09/25/2018 | 11/20/2018 | ML18324A74 | <strong>Potential Loss of Safety Function and Unanalyzed Condition due to Legacy Design Deficiency in Control Building HVAC.</strong><br /><i>Abstract:&nbsp;</i>On September 25, 2018, with the plant operating at 90 percent power, a design vulnerability in the Control Building Ventilation (HVK) system control logic was identified during an extent of condition review of a previously reported condition. The review identified a vulnerability in the HVK Chiller start logic. The design vulnerability had been in place since original plant construction and could cause a loss of all Control Building Cooling for up to 20 minutes following a Loss of Offsite Power. Compensatory measures were put in place to restore operability of the system until a temporary modification could be installed to remove the design vulnerability. This condition was of minimal significance with respect to the health and safety of the public.
4582018009 | River Bend | 11/02/2018 | 12/31/2018 | ML19003A14 | <strong>Inadvertent Initiation of Reactor Core Isolation Cooling due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On November 2, 2018 at 03:53 technicians were performing a Surveillance Test Procedure on the Reactor Core Isolation Cooling (RCIC) system with the reactor operating at 94% power. Improper completion of a procedure step caused an inadvertent initiation of the RCIC system. The initiation was recognized as inadvertent and was secured. The RCIC system was restored to a normal standby lineup. RCIC injected into the Reactor Pressure Vessel (RPV) for approximately 30 seconds. A two inch RPV level increase was observed. No change in feedwater temperature or reactor power was noted. The cause of the initiation was attributed to human error. This event was of minimal significance to the health and safety of the public.
4582018010 | River Bend | 11/10/2018 | 01/09/2019 | ML19009A41 | <strong>Reactor Scram due to Turbine Control Valve Failure</strong><br /><i>Abstract:&nbsp;</i>On November 10, 2018 at 00:46, with the reactor operating at 100% power, Turbine Control Valve number 3 (CV3) unexpectedly closed. Turbine Control Valve number 4 (CV4) did not respond as designed and the reactor automatically scrammed on a reactor vessel high pressure signal. Following the scram, all major systems responded as designed. The CV3 closure was due to failure of the valve's push rod spring housing coupling bolts. The CV4 failure to correctly respond to the CV3 closure transient was due to incorrect operating procedure guidance. This event was of minimal significance to the health and safety of the public.
4582018011 | River Bend | 11/29/2018 | 01/23/2019 | ML19023A54 | <strong>Condition Prohibited by Technical Specifications due to Inadequate Design Change of Under Voltage Relay Trip Set Point Range</strong><br /><i>Abstract:&nbsp;</i>On October 24, 2018, three under voltage relay as found trip set points were found outside of the Technical Specification (TS) allowed range. The condition was discovered during the performance of a planned Surveillance Requirement test. The relays were replaced or calibrated to within the TS allowed range and returned to service. On November 29, 2018, a past operability report was completed on the condition. The report concluded that there was no reasonable assurance that the under voltage relay trip values would remain within the TS allowed range for the entirety of the 2 year calibration Preventive Maintenance (PM) interval. The calibration PM interval was changed from 2 years to 60 days. The cause of the out-of-tolerance relay trip values was an inadequate design change. This event was of minimal significance to the health and safety of the public.
4612018001 | Clinton 1 | 03/30/2018 | 05/29/2018 | ML18151A47 | <strong>Degraded Personnel Airlock Interlock Results in Loss of Primary Containment</strong><br /><i>Abstract:&nbsp;</i>On March 30, 2018, at 1305 CDT, with the reactor at 98 percent thermal power a contractor identified that both doors of the Primary Containment personnel airlock at 828 ft elevation were open simultaneously. This individual was closing the interior door when he noticed that the exterior door was off its seat and started to open. The interior airlock door was shut immediately and the Main Control Room was contacted. Operations entered Technical Specification (TS) Limiting Condition for Operation (LCO) 3.6.1.1, "Primary Containment," Required Action A.1 at 1305 CDT. The LCO was exited approximately one minute later. Primary Containment was inoperable during the time both airlock doors were open but restored with the closing of the interior airlock door. Maintenance personnel performed equipment troubleshooting and subsequently repaired the interlock. The cause of the event is due to component wear over time of the exterior airlock door interlock parts that resulted in the containment airlock interlock not functioning properly. Corrective action include creation of a preventative maintenance task to perform an in-depth inspection of the Primary Containment interlocks. This event is reportable under 10 CFR 50.73(a)(2)(ii)(A) as the condition of the nuclear power plant including its principal safety barriers, being seriously degraded, and 10 CFR 50.73(a)(2)(v)(C) as any event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to control the release of radioactive material. This has been evaluated to not constitute a safety system functional failure.
4612018002 | Clinton 1 | 05/17/2018 | 07/16/2018 | ML18199A10 | <strong>Division 2 Diesel Generator Inoperability due to Air Receiver Remaining Isolated Following Clearance Removal Resulting in Unplanned Shutdown Risk Change</strong><br /><i>Abstract:&nbsp;</i>On May 17, 2018, at 1503 CDT, with the plant in Mode 4 during refueling outage C1R18, a plant equipment operator discovered that the Division (Div) 2 Emergency Diesel Generator (DG) air start receiver isolation valves 1DG160 and 1DG161 were shut. At the time of discovery, the Div. 1 DG was inoperable for a 4160V 1A1 partial bus outage. With the Div. 2 air start receiver valves shut, the Div. 2 DG was declared inoperable. Operations entered Technical Specification (TS) Limiting Condition for Operation (LCO) Required Actions for TS 3.8.2, "AC Sources-Shutdown," and TS 3.5.2, "Reactor Pressure Vessel (RPV) Water Inventory Control" as a result of the inoperability of the onsite AC power sources to isolation valves being credited to limit RPV drain time. The Div. 2 DG air receivers were realigned at 1545 CDT and the auto start function was restored. At 2104 CDT, the Div. 2 DG was declared operable following completion of the return to service checklist procedure. The cause of the event is that Operations relied solely on log entries to track component configuration, contrary to Exelon governance. Corrective measures include eliminating procedures that allowed tracking equipment configuration with log entries and reinforcing approved tracking methods with Operators. This event is reportable under the provisions of 10 CFR 50.73(a)(2)(v)(D), as "any event or condition that at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident" and 10 CFR 50.73(a)(2)(i)(B) as "any operation or condition prohibited by Technical Specifications."
4612018003 | Clinton 1 | 06/20/2018 | 02/05/2019 | ML19042A07 | <strong>Load Driver Card Failure Resulting in High Pressure Core Spray Inoperability</strong><br /><i>Abstract:&nbsp;</i>On June 20, 2018, at 1145 CDT, during panel walkdown, a reactor operator identified that High Pressure Core Spray (HPCS) injection valve 1E22-F004 was in the open position. Valve 1E22-F004 is normally closed and receives an open signal upon HPCS initiation. Operations personnel verified that the valve was open locally and that the plant computer indicated the valve was in the 'not closed' position. No alarms or status lamps indicated why the valve would be open and there was no valid demand signal. Reactor power, pressure, level, and feedwater parameters remained steady and unchanged, with no indication of HPCS injection having occurred or required. With valve 1E22-F004 in the open position without a demand signal, closure on a high reactor water level condition was not assured. HPCS was, therefore, declared inoperable. Technical Specifications (TS) 3.5.1, "Emergency Core Cooling Systems (ECCS)-Operating," and 3.6.1.3, "Primary Containment Isolation Valves (PCIVs)," were entered. The HPCS injection valve 1E22-F004 was subsequently observed cycling without operator action. To assure the containment isolation function and closure on a high reactor water level condition, 1E22-F004 was deactivated in the closed position. The apparent cause of the event was the load driver transient voltage suppressors failing causing the open and close circuits to be energized. As a corrective measure, the original load driver circuit cards were replaced. This event was reported as an 8-hour non-emergency notification per 10 CFR 50.73(a)(2)(v)(D) as any event or condition that at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident.
4612018004 | Clinton 1 | 09/26/2018 | 11/21/2018 | ML18331A16 | <strong>Undervoltage Condition Caused by an Offsite Ameren Transformer Bushing Failure Initiates an Automatic Start of an Emergency Diesel Generator</strong><br /><i>Abstract:&nbsp;</i>On September 26, 2018, at 0946 CDT, the Clinton Power Station (CPS) experienced a trip of the Emergency Reserve Auxiliary Transformer (ERAT) Static VAR Compensator (SVC). A fault on the 138 kV feed to the station created a voltage transient which the ERAT SVC could not compensate for causing it to trip. Approximately 15 seconds following the trip of the ERAT SVC, the Division (DIV) 1 Safety Related 4160 kV Bus 1A1 locked out the Reserve Auxiliary Transformer (RAT) feed breaker and the ERAT feed breaker causing the DIV 1 Diesel Generator to start and load to the 1A1 bus due to a sustained degraded (second level) undervoltage condition as designed. Operations entered Technical Specification (TS) Limiting Condition for Operation (LCO) 3.8.1, "AC Sources-Operating" Required Actions A.1 and A.2 as a result of the voltage transient. The cause of the event was a failure of the high side bushing on offsite Clinton Route 54 to Substation Transformer No. 2 which caused the south feed to the Tabor Substation to cycle. Cycling of the south feed of the Tabor Substation caused the transient on the station 138 kV feed, which resulted in the subsequent station equipment responses. Ameren bypassed the affected transformer and restored the station 138 kV feed. The ERAT was restored to normal configuration on September 26, 2018, at 1354 CDT. Operations subsequently exited TS LCO 3.8.1, Actions A.1 and A.2. Ameren has completed installation of a 138 kV ring bus to improve the reliability of the 138 kV feed to CPS and is in the process of upgrading the feeds to the new substation. This event is reportable in accordance with 10 CFR 50.73(a)(2)(iv)(A) as any event or condition that resulted in manual or automatic actuation of emergency electrical power systems.
4612018005 | Clinton 1 | 10/28/2018 | 04/24/2019 | ML19119A07 | <strong>Unplanned Reactor Scram During Maintenance Outage due to High Intermediate Range Monitor Flux</strong><br /><i>Abstract:&nbsp;</i>On October 28, 2018, at 0445 CDT at approximately 0.5% power while performing a soft shutdown in support of a planned maintenance outage (C1M23), the plant experienced an unplanned Reactor Protection System (RPS) actuation due to Intermediate Range Monitors (IRMs) High Flux. At the time of the event Main Steam Line (MSL) drains were being closed to control the reactor cooldown rate. When MSL drain isolation valve 1B21-F016 was full closed, pressure reduction (cooldown) stopped resulting in a small reactor water level change and the Feedwater system responded by injecting a small amount of cold water. This combination of conditions resulted in a positive reactivity change which resulted in the reactor scram. A review of the Feedwater system response determined that the system responded as designed and no equipment failure initiated the conditions leading to the scram. The cause of the event was pressure control guidance was not adequate to address the cooldown rate conditions during a soft shutdown. Corrective actions include implementing best practices for pressure control strategies, abort criteria based on reactor pressure, actions to minimize time in the region of vulnerability, and associated operator training. This event is reportable under the provisions of 10 CFR 50.73(a)(2)(iv)(A) as an "event or condition that resulted in the manual or automatic actuation of the Reactor Protection System."
4822018001 | Wolf Creek | 05/15/2018 | 10/04/2018 | ML18284A32 | <strong>Inappropriate Use of Blind Flange for Containment Isolation Valve Results in Condition Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>During Mode 5 of Refueling Outage 22 in May 2018, containment shutdown purge isolation valve GTHZ0006 was found to have leakage higher than allowed by Technical Specifications (TS). TS LCO 3.6.3 Condition D was entered at 0255 Central Daylight Time (CDT) on May 15, 2018. Blind flanges had been installed for individual valve testing. With the blind flange installed on GTHZ0006, WCGS considered TS LCO 3.6.3 Required Action D.1 met. Wolf Creek Generating Station subsequently entered Mode 4 at 0510 CDT on the same day. <br /><br /> On August 8, 2018, it was discovered that the use of the blind flange on GTHZ0006 would not meet Required Action D.1 of TS LCO 3.6.3. This is due to its being non-safety related and non-seismically qualified. At 1545 CDT on August 8, 2018, TS LCO 3.6.3 Condition D was re-entered to complete Required Action D.1. At 1611 CDT on August 8, 2018, Required Action D.1 was completed when both containment shutdown purge and minipurge inside containment isolation valves were verified as closed and de-energized. <br /><br /> The allowed completion time of LCO 3.6.3 Required Action D.1 to isolate the flow path is 24 hours. Since this action was not completed for approximately 85 days, this represents a condition prohibited by TS.
4822018002 | Wolf Creek | 02/19/2018 | 02/27/2019 | ML19065A04 | <strong>Modification Activities Affected Control Room Envelope Boundary Causing a Condition Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On March 5, 2018, one train of the Control Room Emergency Ventilation System failed the surveillance test which requires a certain level of positive pressure in the control room above that of the outside air. As part of troubleshooting, several potential vulnerabilities were identified that may have contributed to the inability of the system to maintain the expected level of positive pressure. One of these potential vulnerabilities was two new penetrations in a floor separating areas of the Control Building as part of an ongoing plant modification. This vulnerability existed since February 19, 2018. Guidance provided regarding barriers in the Control Building did not identify the floor as a Control Room Envelope or Control Building Envelope boundary. As these penetrations were located outside of the Control Room Envelope boundary and inside the Control Building Envelope boundary, there was no indication that the interim configuration of the modification would affect the ability to maintain the Control Room Envelope pressure. Upon discovery of the failure of the pressure test, mitigating actions were put into place in accordance with Technical Specification requirements. The modification was completed which removed the vulnerability. Further troubleshooting included adjustments to door seals and to the consistency of test conditions. The test was completed satisfactorily on March 15, 2018, and the affected train of the Control Room Emergency Ventilation System was declared operable on March 16, 2018.
4832018001 | Callaway | 01/11/2018 | 03/12/2018 | ML18071A20 | <strong>Violation of Technical Specification 3.6.3, "Containment Isolation Manual Valve Found in Open Position"</strong><br /><i>Abstract:&nbsp;</i>Between 11/25/2017 and 01/11/2018, containment isolation valve KA V0118 was inoperable due to being open. This normally closed manual valve serves as the outside containment isolation valve for a service air line that passes into containment through penetration P-63. The containment isolation/integrity function for P-63 was maintained by KAV0039, the inner containment isolation valve, during the time KAV0118 was inoperable.<br /><br /> An Operations Technician found the valve in the fully open position on 01/11/2018. The valve had been left in the open position after the penetration had been used to provide service air in containment during Refuel 22. Technical Specification (TS) 3.6.3 requires each containment isolation valve to be OPERABLE in Modes 1 through 4. In this case, it was not recognized that the valve was in full open position when the plant entered Mode 4 on 11/25/2017. Therefore, a condition prohibited by TS 3.6.3 occurred due to failure to comply with the Required Actions specified in the TS. The TS 3.6.3 Actions were exited at 0959 on 1 /11/2018 after valve KAV0118 was closed and locked in the closed position.<br /><br /> The root cause of the valve inoperability was inadequate procedural control to ensure KAV0118 was locked closed prior to entering Mode 4. For corrective action, procedures will be revised to ensure that the valve is closed prior to Mode 4.
4832018002 | Callaway | 05/07/2018 | 07/03/2018 | ML18184A38 | <strong>Inadequate EOP Guidance for Asymmetric Natural Circulation Cooldown</strong><br /><i>Abstract:&nbsp;</i>On May 7, 2018, during an engineering review of mission time requirements for Technical Specification related equipment, a deficiency was discovered regarding the Emergency Operating Procedure (EOP) guidance for natural circulation cooldown with a stagnant loop. This condition could be the result of a postulated Main Steam Line Break with a loss of offsite power. <br /><br /> During a natural circulation cooldown with a faulted steam generator, flow in the stagnant reactor coolant system (RCS) loop associated with the isolated faulted steam generator (SG ) could stagnate and result in elevated temperatures in that loop. This could become an issue when RCS depressurization to residual heat removal system (RHR) entry conditions is attempted. The liquid in the stagnant loop would flash to steam and prevent RCS depressurization. In this condition, the time required to complete the cooldown would be sufficiently long such that the nitrogen accumulators associated with Callaway's atmospheric steam dumps and turbine driven auxiliary feedwater pump flow control valves would be exhausted. As a result, the atmospheric steam dumps and turbine driven auxiliary feedwater pump would not be capable of performing their specified safety functions of cooling the plant to entry conditions for RHR operation. <br /><br /> EOPs have been revised and the EOP change process will be revised to address this issue.
4832018003 | Callaway | 05/19/2018 | 07/17/2018 | ML18201A57 | <strong>Violation of Technical Specification 3.7.10, "Control Room Emergency Ventilation System (CREVS)"</strong><br /><i>Abstract:&nbsp;</i>Between 11/01/2012 and 05/21/2018, control room filtration system filter adsorber unit FGK01A was inoperable due to damage on filter media trays. Under accident conditions, this component is designed to filter radioactivity from air that is supplied to the control room by train A of the control room emergency ventilation system (CREVS).<br /><br /> Evidence of the degraded condition was discovered during operator rounds on 05/19/2018, and the degraded condition was subsequently determined to have existed since the filter media trays were last replaced on 11/01/2012. Technical Specification (TS) 3.7.10 requires two trains of CREVS to be Operable during Modes 1, 2, 3, and 4 and during movement of irradiated fuel assemblies. In this case, the inoperability of FGK01A and its associated train A of CREVS was not recognized prior to discovery of the damaged trays. Therefore, a condition prohibited by TS 3.7.10 occurred due to failure to comply with the Required Actions specified in the TS. The TS 3.7.10 Actions were exited at 1128 on 05/22/2018 after he damaged filter media trays were replaced. <br /><br /> The degraded condition likely occurred during transportation and handling of the trays. Corrective Actions for this event will include improving material <br /> handling by transporting trays in a protected manner to prevent damage.
4832018004 | Callaway | 08/24/2018 | 10/22/2018 | ML18295A41 | <strong>Violation of TS 3.8.1 "AC Sources - Operating"</strong><br /><i>Abstract:&nbsp;</i>On 08/24/2018, during a scheduled periodic maintenance activity to filter stored diesel fuel oil for the train B emergency diesel generator, the Operability of the affected diesel generator was questioned. Subsequent evaluation concluded that due to (1) use of a non seismically-qualified filtration flowpath, and (2) exposure of diesel fuel oil transfer system components to postulated tornado missiles during the maintenance activity, the activity rendered the affected diesel generator inoperable. Two instances were identified within the previous 3 years where the maintenance activity had caused unrecognized past inoperability of the train B standby diesel generator for a duration that exceeded the 72-hour restoration Completion Time specified per Technical Specification (TS) 3.8.1 Required Action B.4. These instances are being reported as violations of TS 3.8.1 in accordance with 10 CFR 50.73(a)(2)(i)(B). <br /><br /> Corrective actions are being taken to establish appropriate administrative controls for removal of affected missile barriers, and to assure that the TS implications of temporary system modifications (such as stored fuel oil filtration) are properly evaluated. Until permanent corrective actions are implemented, remedial actions have been taken to prohibit filtration of stored fuel oil for an Operable DG.
4832018006 | Callaway | 11/28/2018 | 01/28/2019 | ML19028A29 | <strong>Inoperability of SSCs due to Improper Environmental Qualification Classification</strong><br /><i>Abstract:&nbsp;</i>On November 28, 2018, during an engineering review of design documentation related to the Environmental Qualification (EQ) classification of SSCs located in the Callaway main steam tunnel (MST), it was determined that the EQ requirements imposed on subcomponents related to the atmospheric steam dumps (ASDs) had been improperly downgraded based on an evaluation that was performed in 1986. Upon discovery of this condition, a conclusion was reached that the ASDs would be incapable of performing their specified safety functions to mitigate a main steam line break outside containment (MSLBOC). <br /><br /> Per the plant's safety analysis, the MSLBOC sequence would result in elevated temperatures in the MST. The ASD subcomponents are not qualified for the calculated post-accident conditions. Engineering past operability evaluations identified that ASD subcomponent failure modes exist that could potentially result in the loss of the common safety-grade accumulator nitrogen inventory that supports the ASD and TDAFP flow control valve operators, thus rendering the ASDs and the TDAFP flow control valves inoperable dating back to initial plant startup. Operability was restored by a temporary plant modification installed to insulate affected components. A permanent plant modification is being developed to restore full qualification.
4982018001 | South Texas 1 | 10/02/2018 | 12/04/2018 | ML18338A55 | <strong>Unit 1 Main Steam Safety Valve As Left Settings Outside of Required Range Contrary to Technical Specifications due to Inadequate Procedure.</strong><br /><i>Abstract:&nbsp;</i>On October 2, 2018, Unit 1 was in Mode 1 in coast down operations at approximately 92% power prior to shut down for a refueling outage when Main Steam Safety Valves (MSSVs) surveillance testing and calibrations for the Loop B steam generator were completed. <br /><br /> Subsequent review of the surveillance test results for the MSSVs on October 8, 2018, identified an error in the as left setting calculation resulting in the discovery that the as left set pressure of two of the MSSVs on steam generator B were outside Technical Specification post test requirements of +/- 1 %. This resulted in the failure to meet Technical Specification requirements for the MSSVs with Unit 1 in Modes 1, 2 and 3 from October 2, 2018, until October 6, 2018. There were no pressure events to challenge the steam generator B MSSVs during that time.<br /><br /> The cause of the condition was determined to be the lack of procedure guidance due to an elevation correction equation having previously been inadvertently deleted. The test procedure was revised to account for the elevation correction adjustment. Previous test results were verified to include the required elevation correction.
4992018001 | South Texas 2 | 03/25/2018 | 06/22/2018 | ML18176A37 | <strong>Condition Prohibited by Technical Specifications That Could Have Prevented the Fulfillment of a Safety Function due to Two Inoperable Extended Range Monitors</strong><br /><i>Abstract:&nbsp;</i>On March 25, 2018, South Texas Unit 2 was in Mode 3 shutting down for a refueling outage when the extended range excore neutron flux monitors, NI-0045 and NI-0046, failed to meet required channel check criteria. NI-0045 was declared inoperable, the applicable Technical Specification Action statements were entered, and a work package was generated for repair and calibration of NI-0045. <br /><br /> Subsequent reviews concluded that NI-0046 was actually the inoperable monitor. Therefore for six hours and eleven minutes, while NI-0045 had been rendered inoperable during maintenance and testing activities, both extended range monitors were inoperable. Technical Specification requirements had not been met for having two inoperable extended range monitors. Additionally, with both extended range monitors inoperable in Modes 3, 4, and 5, the Operators would not have been able to use these monitors to detect a potential unmonitored return to criticality due to an inadvertent Reactor Coolant System dilution event.<br /><br /> Both extended range monitors were returned to operable status and corrective actions involving training are planned.<br /><br /> Further evaluation confirmed this event resulted in a condition that could have prevented the fulfilment of a safety function. This supplement includes additional details to better describe potential safety consequences and actual plant conditions at the time of the event.
5282018001 | Palo Verde 1 | 02/15/2018 | 04/13/2018 | ML18109A04 | <strong>Automatic Actuation of the Reactor Protection System Resulting from a Loss of Reactor Coolant Pumps</strong><br /><i>Abstract:&nbsp;</i>At approximately 2153 Mountain Standard Time on February 15, 2018, an automatic reactor trip of PVNGS Unit 1 occurred when two of four Reactor Coolant Pumps (RCPs) lost power and the Reactor Protection System (RPS) generated trips on all four channels for low departure from nucleate boiling ratio and high local power density following a main turbine generator trip. The two RCPs lost power due to the fast bus transfer feature being blocked in support of planned maintenance activities on Start-up Transformer (SUT) AENANX02. This prevented the RCPs from receiving power from the SUT after receipt of a trip signal from the main turbine generator. <br /><br /> The preliminary root cause of the Unit 1 main turbine generator and reactor trip has been attributed to the susceptibility of the Unit 1 excitation and voltage regulation system (EX2100e) Exciter Auxiliary I/O Interface Board (EAUX) to electrical noise which led to an excitation trip of the Unit 1 main turbine generator. This condition was corrected on February 17, 12018, by replacing the Unit 1 EX2100e EAUX with an updated version that is less susceptible to electrical noise and thereby reduces the possibility of a spurious main turbine generator trip. The root cause is still considered preliminary as the event investigation is still in progress. Any significant changes identified will be reported in a supplement to this Licensee Event Report upon completion of the investigation.<br /><br /> No other RPS actuation signals or actuations of plant engineered safety features systems occurred and all control element assemblies fully inserted into the reactor core. PVNGS Unit 2 and Unit 3 were operating at 100 percent power at the time of the event and were not impacted by the Unit 1 reactor trip. <br /><br /> No previous similar events have been reported by PVNGS in the last 3 years.
5282018002 | Palo Verde 1 | 04/20/2016 | 05/09/2018 | ML18130A98 | <strong>Condition Prohibited by Technical Specification for Inoperable Excore Instrument Channel</strong><br /><i>Abstract:&nbsp;</i>On April 20, 2016, with Unit 1 Defueled, the channel C excore instrument preamplifier connection inside containment was discovered to be missing two o-rings required for the instrument to be environmentally qualified. The instrument had been in this condition since previous maintenance activities in May 2007. New o-rings were installed. The excore instrument channel was successfully tested on May 9, 2016, and Unit 1 was restarted on May 15, 2016. The cause of the event was attributed to an apparent human performance error during maintenance activities in 2007.<br /><br /> No previous similar events have been reported by PVNGS in the last 3 years.
5282018003 | Palo Verde 1 | 03/15/2018 | 05/09/2018 | ML18129A42 | <strong>Condition Prohibited by Technical Specification 3.7.4 due to Inoperable Atmospheric Dump Valve</strong><br /><i>Abstract:&nbsp;</i>On January 5, 2018, an atmospheric dump valve (ADV) failed to open when an open signal was initiated from the Control Room during testing. Troubleshooting determined that the ADV's current to pressure (I/P) converter was not supplying the correct output signal to the valve positioner. <br /><br /> On March 15, 2018, causal analysis concluded that a defective basic component (I/P converter) had been installed in the ADV control loop on April 17, 2016. This defective component rendered the ADV inoperable from installation until the component was replaced and successful post-maintenance testing was completed on the ADV on January 7, 2018. <br /><br /> The cause of the ADV failing to open was a manufacturing defect; the I/P converter nozzle roll pin was not fully inserted into the regulating nozzle. <br /><br /> The condition was corrected when the defective I/P converter was replaced. Four I/P converters of this type are currently installed in ADVs at PVNGS and are scheduled to be examined and replaced if found defective. One spare Model 8005N I/P converter has undergone radiographic examination. This I/P converter has been found defective and has been quarantined. The vendor has been notified of this 10 CFR 21 reportable defect. <br /><br /> No previous similar events have been reported by PVNGS in the last three years.
5282018004 | Palo Verde 1 | 05/17/2018 | 08/22/2018 | ML18234A53 | <strong>Engineered Safety Feature Pump Room Exhaust Air Cleanup System Failure Resulting in a Condition Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On May 17, 2018, PVNGS Unit 1 received "A" train (1A) Engineered Safety Feature (ESF) Pump Room Exhaust Air Cleanup System (PREACS) Air Filtration Unit (AFU) carbon sample test results that exceeded the acceptance criteria of the Technical Specification (TS) Ventilation Filter Testing Program. The Unit 1 Control Room (CR) staff declared the AFU inoperable and entered TS Limiting Condition for Operation (LCO) 3.7.13, ESF PREACS. The carbon filter replacement and testing was completed on May 18, 2018, and the Unit 1 CR staff declared the 1A ESF PREACS AFU operable. <br /><br /> The 1A ESF PREACS AFU was inoperable since the date the initial carbon sample was drawn on May 10, 2018. The duration exceeded the Required Action Completion Time for Conditions A and B of LCO 3.7.13 that expired on May 17, 2018. The cause of the event was accelerated degradation of the carbon filter after the filter efficiency decreased below 99 percent. <br /><br /> Corrective actions include revision of the current filter testing procedure to ensure safety related carbon filters are proactively replaced or tested more frequently when filter efficiency decreases below 99 percent. <br /><br /> PVNGS reported a similar event on September 19, 2016, due to a Unit 3 Control Room Essential Filtration System (CREFS) AFU carbon sample test result exceeding acceptance criteria resulting in a condition prohibited by TS LCO 3.7.11, CREFS (LER 2016-001-00). The cause of this event was exposure to a high amount of volatile organic compounds from a CR renovation project.
5292018001 | Palo Verde 2 | 05/23/2018 | 07/20/2018 | ML18205A81 | <strong>Unit 2 Reactor Trip due to Dropped Control Element Assembly</strong><br /><i>Abstract:&nbsp;</i>On May 23, 2018, at approximately 1128 Mountain Standard Time, the PVNGS Unit 2 control room received a reactor protection system alarm for low departure from nucleate boiling ratio and an automatic reactor trip occurred as a result of a dropped control element assembly (CEA). The trip occurred coincident with maintenance on control element drive mechanism control system (CEDMCS) fuses and fuse caps. <br /><br /> The cause of the dropped CEA and resulting Unit 2 trip was a CEDMCS lower logic assembly misalignment that caused difficulty seating circuit cards. Maintenance activities adversely affected card edge connections of the circuit card that led to a dropped control element assembly. Corrective actions restored the subgroups 15 and 16 circuit cards to a fully seated position. <br /><br /> No major equipment was inoperable prior to the event that contributed to the event or complicated operator response. Units 1 and 3 were not impacted. <br /><br /> No similar conditions have been reported by PVNGS in the past three years.
5302018001 | Palo Verde 3 | 06/27/2018 | 12/20/2018 | ML18355A80 | <strong>Unit 3 Reactor Trip on Low Steam Generator Level</strong><br /><i>Abstract:&nbsp;</i>On June 27, 2018, at approximately 2257 Mountain Standard Time, the PVNGS Unit 3 Control Room received a feedwater control system trouble alarm due to a steam generator feedwater economizer valve position/demand deviation. Interaction with the malfunctioning economizer valve resulted in an unplanned movement of the economizer valve in the closed direction. This caused the main feedwater pump (MFWP) discharge pressure to increase tripping one of two operating MFWPs. This resulted in a rapid decrease in Steam Generator (SG) level that actuated a reactor protection system trip on low SG water level. Water level then rapidly rose to the SG high level trip set point because the malfunctioning economizer valve did not close. At that point an automatic main steam isolation signal occurred, requiring manual actuation of the auxiliary feedwater and essential spray pond (ultimate heat sink) systems. <br /><br /> The cause of the event was attributed to an auxiliary operator taking an action contrary to station requirements to block air venting from an economizer trip valve causing the valve to move in the closed direction.<br /><br /> Corrective actions include enhanced operations training on responding to economizer valve failures, specifically, and prescripted events placing operators in a perceived sense of urgency. Additional guidance and operating experience will be incorporated into the alarm response procedure for the feedwater control system.<br /><br /> No similar conditions have been reported by PVNGS in the past three years.