## Sheet1
LER Number | Plant Name | Event Date | Report Date | Accession # | Title
2202019001 | Nine Mile Point 1 | 04/14/2019 | 07/26/2019 | ML19211B16 | <strong>Automatic Reactor Scram due to High Reactor Pressure</strong><br /><i>Abstract:&nbsp;</i>On April 14, 2019 at 00:03, Nine Mile Point Unit 1 received an automatic scram of the reactor due to high reactor pressure. Due to the Turbine trip, the High Pressure Coolant Injection (HPCI) System automatically initiated, as designed. This event is reportable under 10 CFR 50.72(b)(2)(iv)(B) and 10 CFR 50.72(b)(3)(iv)(A) as any event or condition that resulted in a manual or automatic actuation of any of the systems listed in 10 CFR 50.72(b)(3)(iv)(B). <br /><br /> The cause of the scram is that station personnel did not identify that the Restoring Arm Breakdown was incorrectly installed and therefore non-functional. This resulted in ineffective knowledge-based troubleshooting to correct a condition as opposed to corrections with controlled technical guidance and the right expertise. <br /><br /> The event described in this LER is documented in the plant's corrective action program.
2202019002 | Nine Mile Point 1 | 04/25/2019 | 06/24/2019 | ML19203A12 | <strong>Condition Prohibited by Technical Specifications due to Vacuum Breaker Not Locked Closed</strong><br /><i>Abstract:&nbsp;</i>On April 25, 2019, Nine Mile Point Unit 1 discovered that one vacuum breaker was not kicked closed, as required by Technical Specification 3.3.6.f.(2). The mode of applicability was entered three times on previous startups. This event is reportable under 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by Technical Specifications.<br /><br /> The cause of the event Operations personnel have not consistently implemented the Degraded Equipment Log (DEL)/Equipment Status Log (ESL) to track operability concerns of systems and components. Action to prevent recurrence is reinforce implementation of the process to institutionalize use of the DEL/ESL into day to day operations.<br /><br /> The event described in this LER is documented in the plant's corrective action program.
2202019003 | Nine Mile Point 1 | 04/29/2019 | 08/02/2019 | ML19218A10 | <strong>Manual Reactor Scram due to Pressure and Power Oscillations</strong><br /><i>Abstract:&nbsp;</i>On April 29, 2019 at 16:33, Nine Mile Point Unit 1 inserted a manual reactor scram due to pressure and power oscillations. The High Pressure Coolant Injection (HPCI) System automatically initiated, on low reactor vessel water level, as designed. This event is reportable under 10 CFR 50.73(a)(2)(iv)(A) as any event or condition that resulted in a manual or automatic actuation of any of the systems listed in 10 CFR 50.73(a)(2)(iv)(B).<br /><br /> The cause of the event is the organization did not effectively incorporate appropriate !earnings from previous NMP events and operating history that would have provided adequate flexibility in the operating strategy to mitigate the risks of increased oscillations. The scope of the corrective actions is to incorporate operational history and events into Special Operating Procedures (SOPs).<br /><br /> The event described in this LER is documented in the plant's corrective action program.
2202019004 | Nine Mile Point 1 | 08/04/2019 | 10/03/2019 | ML19281A86 | <strong>Average Power Range Monitors Declared Inoperable</strong><br /><i>Abstract:&nbsp;</i>On August 4, 2019 at 1745, Reactor Recirculation Pump #11 (RRP 11) tripped. Following the RRP trip, the Average Power Range Monitors (APRMs) flow bias trips were inoperable due to reverse flow through the RRP. The APRMs were restored to operable on August 4, 2019 at 1807 when the RRP 11 discharge blocking valve was manually closed by operations, eliminating the reverse flow condition through the pump. This event is reportable under 10 CFR 50.72(b)(3)(v)(A) and 10 CFR 50.73(a)(2)(v)(A) as any event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to: (A) Shut down the reactor and maintain it in a safe shutdown condition. <br /><br /> The cause of the RRP 11 trip is a degraded tachometer generator on the associated motor generator set. Corrective actions to prevent recurrence are to revise the preventative maintenance strategy to replace the tachometer generator every two years. The event described in this LER is documented in the plant's corrective action program.
2372019001 | Dresden 2, Dresden 3 | 01/30/2019 | 03/29/2019 | ML19091A04 | <strong>Secondary Containment Differential Pressure Exceeded Technical Specification due to Excess Ventilation Supply Flow</strong><br /><i>Abstract:&nbsp;</i>On January 30, 2019, the operating heating boiler tripped during a period of extremely cold external air temperatures. To address the potential of freezing the heating steam coils and filters, procedures provided direction to open the ventilation inlet plenum doors. At 0910, the Reactor Building differential pressure degraded and was determined to be below 0.25 inches water column vacuum. Technical Specification (TS) 3.6.4.1, "Secondary Containment," was not met and Condition A, Secondary Containment inoperable, was required since differential pressure degraded below the 0.25 inches water column vacuum by local average gauge readings. Standby Gas Treatment was started to assist in differential pressure control. At 0928, differential pressure improved and was maintaining above 0.25 inches water column vacuum. TS 3.6.4.1 Condition A was exited. This event is reportable under 10 CFR 50.73(a)(2)(v)(C), "Any event or condition that could have prevented the fulfillment of the safety function of ... systems that are needed control the release of radioactive material." The cause of the event was determined to be inadequate procedural guidance for responding to loss of heating boilers during extreme cold external air conditions. Corrective actions include revising station procedure to prioritize actions to mitigate ventilation transients during a loss of heater boilers.
2372019002 | Dresden 2 | 05/09/2019 | 07/02/2019 | ML19189A08 | <strong>Unit 2 Scram due to Main Turbine Low Oil Pressure Trip</strong><br /><i>Abstract:&nbsp;</i>On May 9, 2019, at 0348 CDT, Unit 2 received an automatic reactor scram as the result of the main turbine tripping due to low oil pressure from the main shaft oil pump. Following the scram, all systems operated as expected, decay heat was being removed using the steam bypass valves to the condenser, and the safety relief valves did not lift. Inspection of the main turbine front standard and main oil pump revealed damage to the spline interface between the main gear quill shaft and the high-pressure control rotor. This damage led to a loss of power transfer between the main turbine and the main oil pump which supplies bearing header pressure. This event is reportable under 10 CFR 50.73(a)(2)(iv)(A), "Any event or condition that resulted in manual or automatic actuation of any of the systems listed in paragraph (a)(2)(iv)(B) of this section." The automatic actuation of the reactor protection system is listed in 10 CFR 50.73(a)(2)(iv)(B). The cause of the event was determined to be work order instructions contained an unrecognized critical activity that lacked the detail needed to prevent human error during installation of quill shaft oil gasket. Corrective actions include updating the model work orders for turbine front standard maintenance to include the proper level of detail and establishing new post-maintenance testing practices.
2442019001 | Ginna | 03/07/2019 | 05/02/2019 | ML19127A14 | <strong>Air Leakage from Turbine Driven Auxiliary Feed Pump Lube Oil Accumulator Results in Unexpected Pump Inoperability</strong><br /><i>Abstract:&nbsp;</i>On 3/7/2019, during the performance of quarterly surveillance testing, the Turbine Driven Auxiliary Feedwater (TDAFW) pump was unexpectedly found to be inoperable due to low lube oil (LO) accumulator air precharge pressure. After securing the AC LO pump to test the automatic start of the DC LO pump, the trip throttle valve unexpectedly tripped closed due to low lube oil pressure. The LO accumulator functions to maintain adequate LO pressure during LO pump perturbations. The TDAFW Pump was not in operation when the trip throttle valve unlatched and closed, therefore there was no impact on plant operation. <br /><br /> The most probable cause is that the TDAFW Pump LO accumulator air precharge pressure was lower than expected due to leakage from the air charging valve. Additionally, an acceptance criteria for LO accumulator air precharge pressure leakage, to ensure the accumulator function was maintained, had not been established. The Accumulator was precharged to the required pressure and a successful re-test was performed. Corrective actions are planned to establish LO accumulator air precharge pressure leakage acceptance criteria and a system modification to install an air charging valve manual isolation valve.<br /><br /> Technical Specification (TS) Limiting Condition for Operation 3.7.5.C requires the TDAFW pump to be operable. Due to inability to determine exact time of inoperability, it was conservatively assumed to be inoperable for greater than the TS allowed time of 72 hours, which requires a report to the NRC in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by TS.
2472019001 | Indian Point 2 | 03/15/2019 | 05/14/2019 | ML19143A09 | <strong>Loss of Excitation Main Generator Trip</strong><br /><i>Abstract:&nbsp;</i>On March 15, 2019 at approximately 1300 hours Eastern Standard Time, Indian Point Unit 2 experienced an automatic reactor trip on a turbine trip, which was in response to a main generator trip. The main generator trip was initiated by actuation of the generator Protection System due to a main generator loss of excitation. <br /><br /> All control rods fully inserted and all required safety systems functioned properly. The plant was stabilized in hot standby with decay heat being removed by the main condenser. The Auxiliary Feedwater System automatically started as expected on steam generator low level to provide feedwater flow to the steam generators. The plant was stabilized in hot standby with decay heat being removed by the main condenser. The direct cause of this event was a failure of both diodes in the C-phase middle diode stack of the 24 Rectifier. The root cause of this event was the fact that the power diode test method was unable to detect component degradation. <br /><br /> This event had no effect on the public health and safety. This event was reported to the Nuclear Regulatory Commission on March 15, 2019 under 10 CFR 50.72(b)(3)(iv)(A) and 10 CFR 50.72(b)(2)(iv)(B) as an event that resulted in the automatic actuation of the Reactor Protection System when the reactor is critical and a valid actuation of the Auxiliary Feedwater System.
2472019002 | Indian Point 2 | 03/24/2019 | 05/23/2019 | ML19150A11 | <strong>Automatic Reactor Shutdown due to Turbine Trip Caused by Generator Trip</strong><br /><i>Abstract:&nbsp;</i>On March 24, 2019 at approximately 1445 during a power ascension from a previous trip with indicated reactor power at approximately 96%, the reactor automatically tripped on a turbine trip due to a direct trip from the Main Generator regulator cubicle. All control rods fully inserted and plant equipment responded normally to the unit trip. This reactor protection system (RPS) actuation was reported under 10 CFR 50.72(b)(2)(iv)(B). <br /><br /> The auxiliary feedwater system actuated following the automatic trip as expected. This specified system actuation was reported under 10 CFR 50.72(b)(3)(iv)(A). During the event offsite power remained available and stable. No primary or secondary reliefs lifted, and all required safety systems functioned properly. The plant was stabilized in hot standby (Mode 3) with decay heat being removed via the steam generators to the atmospheric steam dumps.<br /><br /> This event had no effect on the public health and safety.
2492019001 | Dresden 3 | 09/20/2019 | 11/19/2019 | ML19325C09 | <strong>Degraded Differential Pressure Indicating Switch in the LPCI Loop Select Logic Caused by Water Damage Results in a Condition Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On September 20, 2019, one of four channels for the 3A reactor recirculation pump high differential pressure function failed the channel functional test. Technical Specification 3.3.5.1, "EGGS Instrumentation," requires all four channels to be operable. Technical Specification 3.3.5.1, Condition C identifies a Completion Time of 24 hours to restore the failed channel to operable status. The degraded differential pressure switch was replaced. The channel was restored to operable within the 24 hour time limit.<br /><br /> On June 20, 2019, the Unit 3 East Low Pressure Coolant Injection Room cooler was found leaking water onto the panel where recirculation pump differential pressure switches are installed. On July 30, 2019, a surveillance documented that all four channels were functional. The failed channel was determined to be inoperable between July 30 and September 20, 2019, which is longer than the 24 hours allowed by Technical Specification. This event is being reported pursuant to 10 CFR 50.73(a)(2)(i)(B), a condition which was prohibited by the plant's Technical Specifications. The cause of the degraded differential pressure switch was due to water dripping from the Low Pressure Coolant Injection room cooler onto the instrumentation rack. Service Water is isolated to the Unit 3 East Low Pressure Coolant Injection Room cooler until the room cooler is repaired.
2502019001 | Turkey Point 3 | 05/18/2019 | 06/27/2019 | ML19179A29 | <strong>Unit 3 Manual Reactor Trip Following Grid Disturbance</strong><br /><i>Abstract:&nbsp;</i>On 5/18/19 at 11:08am, the Turkey Point Unit 3 reactor was manually tripped from 100% power due to lowering levels in all three Steam Generators. Auxiliary Feedwater automatically actuated and was subsequently secured at 11:53am during plant post-trip restoration. The cause of the event was a grid disturbance that resulted in the Turbine Control Valve (TCV) position deviation faults. All four of the TCVs drifted closed in response to the faults by design. As a result, levels in all three Steam Generators steadily decreased, prompting the Unit 3 Reactor Operator to initiate a manual trip of the Unit 3 reactor. All systems responded as designed during the transient.
2542019001 | Quad Cities 1 | 02/05/2019 | 04/05/2019 | ML19095A38 | <strong>HPCI System Inoperable due to Blown Fuse in the Motor Speed Changer Circuit</strong><br /><i>Abstract:&nbsp;</i>On February 5, 2019, at 1804 hours, a Motor Speed Changer (MSC) logic fuse blew during performance of Quad Cities Nuclear Power Station (QCNPS) Unit 1 High Pressure Coolant Injection (HPCI) operability surveillance following planned maintenance activities. Had HPCI been demanded while the fuse was blown the HPCI turbine would have been unable to reach its required speed. <br /><br /> During investigation of the blown fuse, the MSC motor and the MSC gearbox were discovered to be mechanically bound. Intermittent failure of the Low Speed Stop (LSS) Limit Switch (LS) due to age related degradation of internal electrical contacts allowed the MSC motor to remain energized when it should have been deenergized, leading to degradation. The limit switch contacts were found with high resistance attributed to observed deposits and pitting. None of these components were part of the work scope of this HPCI maintenance window. <br /><br /> The immediate corrective action was replacement of the fuse, the LSS LS, the MSC motor and select MSC gearbox components. The safety impact was minimal based on the availability of other high pressure and low pressure Emergency Core Cooling Systems. <br /><br /> This is being reported in accordance with 10 CFR 50.73(a)(2)(v)(D) for an Event or Condition that Could Have Prevented Fulfillment of a Safety Function to Mitigate the Consequences of an Accident.
2542019002 | Quad Cities 1 | 08/25/2019 | 10/23/2019 | ML19296B20 | <strong>Phase to Ground Fault in Isolated Phase Bus Duct Led to Generator Trip and an Automatic SCRAM</strong><br /><i>Abstract:&nbsp;</i>On August 25, 2019, at 1102 hours CDT, Quad Cities Nuclear Power Station (QCNPS) Unit 1 experienced an automatic reactor SCRAM from 100 percent power. The SCRAM was the result of a generator trip that occurred when leakage current measured by the Generator Stator Ground Detection Relay exceeded its threshold and actuated the Generator Primary Lock Out Relay (86 Device). Following the Reactor SCRAM, water was found in the "A" Isolated Phase Bus Duct (IPBD) between the Unit Aux Transformer (UAT) and the wall of the Turbine Building. It was determined that water entered through a degraded access cover gasket located on the IPBD and the resulting condensation within the duct caused current leakage through one or more of the insulators that support the bus. The corrective actions include replacement of the insulators that were impacted by the water, replacing the degraded gaskets and implementing additional preventative maintenance activities on the IPBD system.<br /><br /> This is being reported in accordance with 10 CFR 50.73(a)(2)(iv)(A) for an event or condition that resulted in automatic actuation of the reactor protection system (RPS) and containment isolation signals for Groups 2 and 3 affecting containment isolation valves in more than one system.
2542019003 | Quad Cities 1, Quad Cities 2 | 10/27/2019 | 12/20/2019 | ML19354A10 | <strong>Water Found in Control Room Emergency Ventilation Air Filtration Unit</strong><br /><i>Abstract:&nbsp;</i>On October 27, 2019, at 1605 hours CDT, the Quad Cities Nuclear Power Station (QCNPS) Unit 1 and Unit 2 Control Room Emergency Ventilation (CREV) system was declared inoperable due to finding water in the Air Filtration Unit (AFU) filter housing. Water leaked into the B CREV AFU through an air operated fire suppression system isolation valve and sprinkler heads internal to the AFU resulting in partial submersion of the AFU filters. Maintenance on the isolation valve actuator on October 10, 2019, did not include post-maintenance testing, which resulted in inadvertently leaving the valve in a condition that provided a path for leakage into the AFU. <br /><br /> The cause of the event was an absence of adequate work instructions for the performance of effective post-maintenance testing. Immediate Corrective actions completed include replacement of the AFU filters. Followup Corrective actions include a repair of the valve, and improvements to the model work order.<br /><br /> This is being reported in accordance with 10 CFR 50.73(a)(2)(i)(B), any operation or condition which was prohibited by the plant's Technical Specifications, for the CREV system being inoperable longer than the seven (7) days allowed by Technical Specification 3.7.4, "Control Room Emergency Ventilation (CREV) System." It is also being reported under 10 CFR 50.73(a)(2)(v)(D), any event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident.
2552019001 | Palisades | 01/03/2019 | 02/28/2019 | ML19059A08 | <strong>Reactor Protection System and Auxiliary Feedwater System Actuation due to Turbine Governor Valve Failure</strong><br /><i>Abstract:&nbsp;</i>On January 3, 2019, while the reactor was in mode 1 at 85% power, the linear variable differential transformer (LVDT) core on CV- 0576, "High Pressure Turbine #4 Governor Valve," broke, causing uncontrolled cycling of the valve and an excursion in generator output. Upon control room notification of the uncontrolled movement of CV-0576, the operators placed the turbine controls in manual operation. However, CV-0576 proceeded to open and close independently of valve controls. Due to the inability to maintain positive control of CV-0576 manually, the operators manually tripped the reactor in accordance with site procedures. The required safety systems and shutdown equipment performed as expected, resulting in an uncomplicated trip. The condition was reported on January 3, 2019 (Event Number 53813) in accordance with 10 CFR 50.72(b)(2)(iv)(B) and 10 CFR 50.72(b)(3)(iv)(A) for a valid reactor protection system (RPS) actuation and an auxiliary feedwater (AFW) actuation. <br /><br /> This condition is reportable in accordance with 10 CFR 50.73(a)(2)(iv)(A) as a condition that resulted in the actuation of both the RPS and the AFW. <br /><br /> The condition was attributed to a high-cycle fatigue failure of the LVDT core, which led to the uncontrolled movement of CV-0576. Corrective actions were taken to replace the LVDT cores on all four governor valves before returning to power operations.<br /><br /> The investigation led to a corrective action to create preventative maintenance tasks to replace the governor valve LVDTs during normally scheduled actuator inspection and refurbishment.
2552019002 | Palisades | 01/09/2019 | 02/28/2019 | ML19059A13 | <strong>Automatic Reactor Trip and AFW System Actuation due to the Loss of Power to the RPS BD matrix</strong><br /><i>Abstract:&nbsp;</i>On January 9, 2019, maintenance personnel were performing a calibration of NI-6, "Power Range Safety Channel." The plant was in mode 1 at 100% power. At approximately 10:28 EST, maintenance personnel removed the panel on EC-06, "Reactor Protection System (RPS) cabinet," and observed an arc in the vicinity of incoming AC power. It was immediately observed that the entire RPS B channel had lost power. Approximately six minutes after the loss of power to RPS B channel, the reactor tripped. Following the reactor trip, it was identified that the RPS D channel matrix BD power supply was not lit, indicating no output. <br /><br /> The required safety systems and shutdown equipment performed as expected, resulting in an uncomplicated trip. The condition was reported on January 9, 2019 (Event Number 53819) in accordance with 10 CFR 50.72(b)(2)(iv)(B) and 10 CFR 50.72(b)(3)(iv)(A) for both a valid reactor protection system (RPS) actuation and an auxiliary feedwater actuation (AFW).<br /><br /> This event is reportable in accordance with 10 CFR 50.73(a)(2)(iv)(A) as a condition that resulted in a valid actuation of both the RPS and the AFW.<br /><br /> The cause was attributed to shorted capacitors in the B RPS cabinet and a blown input fuse to the RPS D channel BD matrix power supply. Corrective actions were taken to replace the capacitors with insulated capacitors, and to replace the RPS D channel BD matrix power supply and fuse.
2592019001 | Browns Ferry 1 | 07/12/2019 | 11/07/2019 | ML19311C47 | <strong>High Pressure Coolant Injection System Declared Inoperable due to Steam Supply Isolation</strong><br /><i>Abstract:&nbsp;</i>On July 12, 2019, at approximately 1640 Central Daylight Time (CDT), the Unit 1 High Pressure Coolant Injection (HPCI) system unexpectedly received a Group 4 Primary Containment Isolation System (PCIS) signal which closed the HPCI inboard and outboard steam supply valves. Operations personnel declared HPCI inoperable and entered Technical Specification (TS) 3.5.1, "Emergency Core Cooling System (ECCS) - Operating," Condition C. <br /><br /> The causes of this event were that Electrical Maintenance personnel failed to follow EPI-0-075-RLY001, "Functional Test of Pressure Suppression Chamber Head Tank Pump Suction Valve Interlock Relays," as written by not verifying panel number or wire number and by failing to use a peer check as required; and that the workers failed to apply maintenance fundamentals and technical skills with appropriate rigor when using test equipment. <br /><br /> Corrective actions include implementing accountability actions for the individuals involved in this event in accordance with TVA's processes, briefing personnel in Electrical Maintenance on the causes and lessons learned from this event, and performing a dynamic learning activity with electricians involved to cover volt-ohm meter usage.
2592019002 | Browns Ferry 1, Browns Ferry 2, Browns Ferry 3 | 09/10/2019 | 11/12/2019 | ML19316B89 | <strong>Unanalyzed Condition due to Inoperable Security Doors Following a Lightning Strike</strong><br /><i>Abstract:&nbsp;</i>On September 10, 2019, at approximately 1502 Central Daylight Time (CDT) a lightning strike caused a power surge which disabled signal repeaters between the Local Intelligence Units (LIUs) of some security doors and the monitoring stations at Browns Ferry Nuclear Plant (BFN). At 1830 CDT, it was discovered that some of the oncoming night shift personnel could not access particular areas which required keycard access. An extent of condition check conducted at 1934 CDT determined that access to the 1A and 3A Electric Board Rooms, which contain remote shutdown panels and Fire Safe Shutdown (FSS) equipment, was prohibited for the night shift personnel. This condition is reportable under Title 10 of the Code of Federal Regulations (10 CFR) 50.73(a)(2)(ii)(B) as an event or condition that resulted in the nuclear power plant being in an unanalyzed condition that significantly degraded plant safety. Specifically, this condition impacted the ability of Operators to perform their required actions in FSS procedures within prescribed time limits if a fire had occurred. <br /><br /> The event was caused by lightning strike, which created a power surge, resulting in a security equipment communications failure. Access was restored to all plant areas at 2106 CDT. The immediate corrective action was to have Security and Operations personnel reset the malfunctioning equipment. This cleared the error and allowed the LIUs of the affected security doors to receive roster updates. As a corrective action to reduce the probability of recurrence, Site Security created a constantly-activated, all-access emergency keycard, as a contingency against future door LIU communication failures. SSI-16.1, "Compensatory Measures," is being revised to proceduralize the emergency keycard's use.
2602019001 | Browns Ferry 2 | 03/23/2019 | 12/19/2019 | ML19353B48 | <strong>Traversing In-core Probe Purge Header Check Valve Leak Rate in Excess of Technical Specifications Limits</strong><br /><i>Abstract:&nbsp;</i>On March 23, 2019, at approximately 1600 Central Daylight Time (CDT), while performing surveillance testing required prior to initial startup from the Unit 2 Refueling Outage, Local Leak Rate Testing (LLRT) identified the failure of a Primary Containment penetration for the Traversing ln-core Probe (TIP) system. Further troubleshooting determined that the TIP Purge Header check valve was leaking by, rendering the test volume unable to be pressurized. The gross leakage Leak Rate value exceeded the Technical Specification allowable value for Type C valves of less than 60 percent of the allowable limit. On March 26, 2019, at approximately 1030 CDT, Engineering evaluation determined that the TIP System leakage test results related to LLRT of the TIP Purge Header Check Valve resulted in a reportable condition. At 1508 CDT, Event Notification 53959 was made to the NRC for a serious degradation of the reactor’s principle safety barriers. <br /><br /> The apparent cause of this event was foreign material in the body of the TIP Purge Header check valve which prevented the valve from seating. The immediate corrective action for this condition was to replace the failed valve. An additional corrective action will be implemented to add another check valve in series for penetrations affected by this condition to allow dual barrier containment isolation for Units 1, 2, and 3.
2602019002 | Browns Ferry 2 | 05/29/2019 | 07/18/2019 | ML19199A33 | <strong>Main Steam Relief Valves Lift Settings Outside of Technical Specifications Required Setpoints</strong><br /><i>Abstract:&nbsp;</i>On May 29, 2019, the Tennessee Valley Authority was notified of as-found testing results that three Main Steam Relief Valves (MSRVs) from Unit 2 were outside the +/- 3 percent setpoint band required for operability. It was determined that these MSRVs failed due to corrosion bonding to the valve seat as a result of its platinum anti-corrosion coating flaking off. Previously, on April 27, 2018, MSRV BFN-2-PCV-001-0041 had been declared inoperable due to excessive leakage. Failure of this MSRV was caused by a delamination of a portion of the platinum anti-corrosion coating which lead to the leak. <br /><br /> More than one MSRV was considered to be inoperable during the entire operating cycle and longer than permitted by Technical Specifications. The affected valves remained capable of maintaining reactor pressure within American Society of Mechanical Engineers code limits. <br /><br /> All thirteen of the MSRV pilot valves have been replaced during the Unit 2 Spring 2019, refueling outage. The previous corrective action from LER 50-259/2018-007-00 to perform nitrogen leak testing prior to platinum coating had not yet been implemented for these valves. This continues to be the corrective action to prevent recurrence. In addition, an improved method of applying the platinum to the pilot discs will now be used which provides a more consistent and forgiving finish on the pilot valve seating surface.
2602019003 | Browns Ferry 2 | 10/01/2019 | 12/02/2019 | ML19336B74 | <strong>Automatic Reactor Scram During Startup due to Intermediate Range Monitor Noise</strong><br /><i>Abstract:&nbsp;</i>On October 1, 2019, at approximately 0307 Central Daylight Time (CDT), Browns Ferry Nuclear Plant (BFN) Unit 2 received a reactor scram signal from less than 1% power that originated from the Neutron Monitoring System. There were no complications associated with this scram. All required safety systems functioned as designed. The initiating condition was discovered to be a scram signal due to electrical noise induced when the pushbutton was depressed for driving Source Range Monitors (SRMs) C and D out concurrently. <br /><br /> On October 1, 2019, at approximately 0605 CDT, Operations personnel completed Event Notification 54302 to the NRC. <br /><br /> The root cause of this event was that BFN engineering and leadership demonstrated weaknesses in risk perception related to the failure to advocate for and implement a permanent solution to the long standing Intermediate Range Monitor (IRM) noise susceptibility issue. Specifically, the IRM system design is not robust enough to mitigate the effects of noise intrusion. Corrective actions which will reduce or mitigate the probability of recurrence are to implement a process to manage the risk of identified equipment vulnerabilities; to implement time constant modifications to BFN Units 1, 2, and 3 which will make the system more robust against noise spiking; and to revise the Bridging and Mitigation Strategy Development procedure to explicitly require review of OE during bridging or mitigation strategy development.
2612019001 | Robinson 2 | 08/11/2019 | 10/09/2019 | ML19282D75 | <strong>Turbine Trip / Reactor Trip due to Main Generator Lockout</strong><br /><i>Abstract:&nbsp;</i>At 0840 hours Eastern Daylight Time (EDT) on 08/11/2019 with the plant in Mode 1 at 100 percent power, H. B. Robinson Steam Electric Plant, Unit No. 2 (HBRSEP2), experienced an electrical fault within the main generator exciter. The exciter field breaker tripped due to a loss of generator field excitation, causing a main generator lockout. As a result, HBRSEP2 experienced an automatic turbine trip and subsequent reactor trip. Plant safety systems operated as designed. Auxiliary Feedwater Pumps started as expected. The plant was stabilized in Mode 3 and subsequently cooled to Mode 4. <br /><br /> The exciter was removed and shipped from HBRSEP2 to a vendor where it was disassembled, tested and inspected. This inspection identified extensive exciter damage. Due to the extensive damage, the precise failure cause is indeterminate. <br /><br /> Actions taken to correct the condition were to reinstall a refurbished exciter. HBRSEP2 returned to power operation on 09/03/2019. There was no impact to the health and safety of the public as a result of this event.
2632019001 | Monticello | 04/13/2019 | 06/13/2019 | ML19164A27 | <strong>RHR Decay Heat Removal Pump Start Permissive Logic Hardening Error</strong><br /><i>Abstract:&nbsp;</i>On April 16, 2019 at approximately 0215 with the plant shutdown in Mode 5 with the cavity flooded and fuel pool gates out, 13 Residual Heat Removal (RHR) Pump failed to start from the control room during performance of the RHR System Cold Shutdown Valve Operability Test. Investigation into the failure to start identified that hardening activities on Division 1 of RHR Shutdown Cooling (SDC) conducted on April 13, 2019 resulted in defeating remote start capability of both 11 and 13 RHR pumps. This condition caused the 11 and 13 RHR pumps to be inoperable between April 13 and April 16. With both pumps inoperable, LCOs 3.4.8, 3.9.7 and 3.9.8 were not met and the Required Action for one or two RHR shutdown cooling subsystems inoperable requiring verification of an alternate method of decay heat removal for each inoperable RHR shutdown cooling system within 1 hour and once per 24 hours thereafter was not performed. This condition was determined to be reportable in accordance with 10 CFR 50.73(a)(2)(i)(B), "Any operation or condition which was prohibited by the plant's Technical Specifications." There were no actual safety consequences from this condition. The 11 RHR pump was operating in SDC mode for the duration of the condition from when hardening was installed until the hardening error was corrected. At no time during this condition was shutdown cooling lost or not in service controlling reactor water temperature. A low pressure ECCS injection/spray subsystem was operable at all times for the duration of the condition.
2632019002 | Monticello | 06/11/2019 | 08/09/2019 | ML19221B73 | <strong>Two Manual Primary Containment Isolation Valves Found Open Resulting in a Condition Prohibited by Technical Specification</strong><br /><i>Abstract:&nbsp;</i>On 6/11/2019 during troubleshooting activities, two in-series manual 1" Primary Containment Isolation Valves (PCIVs), AS-78 and AS-79, were discovered to be open. In Mode 1 the required position of the PCIVs is closed. Investigation determined the valves were left open following a maintenance activity during a recent refueling outage. No formal tracking mechanism had been used for these valves to ensure plant configuration was restored following the maintenance activity as required by procedure. This event is reportable in accordance with 10 CFR 50.73(a)(2)(i)(B) "as a condition was prohibited by the plant's Technical Specifications"; 10 CFR 50.73(a)(2)(v)(C), "event or condition that could have prevented fulfillment of a safety function to control the release of radioactive material"; and 10 CFR 50.73(a)(2)(v)(D), "event or condition that could have prevented fulfillment of a safety function to mitigate the consequences of an accident". There were no actual safety consequences from this condition. The immediate corrective action was to close the valves and independently verify they were locked closed. The applicable procedure will be revised to ensure clarity for when equipment manipulation per Operations Shift Supervisor direction is allowed and what formal tracking methods should be used to ensure equipment is returned to the required position.
2662019001 | Point Beach 1 | 12/05/2018 | 02/03/2019 | ML19035A12 | <strong>Loss of Main Condenser Cooling Results in Manual Reactor Trip</strong><br /><i>Abstract:&nbsp;</i>At 1539 on December 5, 2018, with Unit 1 operating in MODE 1 at full power, Operators removed Unit 1 from service by manually tripping the reactor when operators identified decaying main condenser vacuum conditions. All control rods fully inserted in the core due to the manual trip. The auxiliary feedwater system started as expected when a valid system actuation occurred after the reactor trip. There was no emergency core cooling system actuation and offsite power was maintained throughout the event. <br /><br /> This event is being reported pursuant to 10 CFR 50.73(a)(2)(iv)(A) for both the manual RPS actuation and also for the automatic initiation of Auxiliary Feedwater.
2662019002 | Point Beach 1, Point Beach 2 | 04/09/2019 | 06/08/2019 | ML19161A08 | <strong>Operation Not Maintained Within Pressure and Temperature Limit Report (PTLR) as Required by Technical Specification 3.4.3</strong><br /><i>Abstract:&nbsp;</i>On April 9, 2019, following the Unit 1 Reactor Coolant System (RCS) cooldown for refueling (U1R38), PBNP identified where cold leg temperature was not maintained within the limits specified in the PTLR. An extent of condition review identified time intervals where both units had operated outside of the PTLR temperature limit. During these intervals, the technical specification required action completion times were not satisfied. <br /><br /> Technical Specification 3.4.3, RCS Pressure and Temperature Limits Limiting Condition for Operation (LCO), requires that RCS pressure, temperature, and heat-up and cooldown rates be maintained within the limits specified in the PTLR. The LCO is applicable at all times and requires that if a limit is exceeded, initiate action to restore parameters and determine RCS is acceptable for continued operation prior to entering Mode 4. The RCS heat-up and cooldown rates have been maintained within the limits specified in the PTLR. However, the RCS was not maintained greater than the minimum temperature specified in the PTLR and the required action to determine the RCS acceptable for continued operation was not completed prior to entering Mode 4.<br /><br /> This event is being reported pursuant to 10 CFR 50.73(a)(2)(i)(B), Operation or Condition Prohibited by Technical Specifications.
2692019001 | Oconee 1 | 11/09/2016 | 08/13/2019 | ML19225C40 | <strong>Unit 1 Standby Shutdown Facility Reactor Coolant Makeup Pump Oil Suction Tubing Failure</strong><br /><i>Abstract:&nbsp;</i>On November 9, 2016, with Unit 1 shut down for a refueling outage, a pump lubrication Planned Maintenance (PM) activity was performed on the Unit 1 Standby Shutdown Facility (SSF) Reactor Coolant Makeup (RCM) Pump. During performance of the PM it was discovered that the copper tube to the oil strainer had been sheared above the static oil level. A cause evaluation performed in 2016 identified the cause to be repeated impact from the rotating components associated with the pump shaft due to inadequate clearance being maintained when the tubing was installed on November 12, 2014. <br /><br /> Because the cause was determined to be repeated impact from the rotating components of the pump shaft to the pump's oil suction tubing, the tubing failure would occur while the pump was running. The last time the pump ran prior to discovery of the failed tubing was on October 4, 2016. Oconee staff determined the failed oil tubing impacted operability of the RCM Pump from at least October 4, 2016, until the Unit 1 Shutdown date of November 5, 2016, a total of 32 days. This duration exceeds the 7 days allowed by the TS, therefore this event was reportable under 10 CFR 50.73(a)(2)(i)(B) and is now being reported as an operation or condition prohibited by TS.
2692019002 | Oconee 1 | 07/24/2019 | 09/19/2019 | ML19262H51 | <strong>Unit 1 Core Flooding System Loss of Safety Function</strong><br /><i>Abstract:&nbsp;</i>On July 24, 2019 with Unit 1 in Mode 1, Operations was venting the 1A Core Flood Tank (CFT) in accordance with plant procedures to lower the nitrogen pressure. Upon reaching the desired pressure, Operations attempted to stop the venting by closing a remotely-operated isolation valve (1CF-5) in the vent line. This valve failed to fully close which resulted in the 1A CFT pressure continuing to drop below the Technical Specification (TS) required limit of 575 psig. Another manually operated isolation valve was closed and nitrogen was added to the 1A CFT to restore pressure within the TS required range. <br /><br /> While the Core Flood System contains two (2) Core Flood Tanks, both tanks are required to mitigate certain accident scenarios and is considered a single-train system. When the 1A CFT became inoperable as a result of a component failure, it resulted in a loss of safety function and is therefore being reported under 10 CFR 50.73(a)(2)(v)(d).
2772019001 | Peach Bottom 2, Peach Bottom 3 | 02/11/2019 | 04/11/2019 | ML19109A09 | <strong>Emergency Bus Breaker Relay Failure Results in Loss of Safety Function</strong><br /><i>Abstract:&nbsp;</i>On February 11, 2019, at 2232 hours, an off-site power source was lost due to a malfunction of a lightning arrestor located at an off-site substation. As a result, six of the site's eight 4kV emergency buses transferred to their alternate offsite source. During this process, a breaker that supplies power to a 480 volt load center (E434) fed from the E43 emergency 4kV bus failed to automatically re-close due to a failed relay. This resulted in the E4 emergency diesel generator being inoperable and loss of safety function of the 'B' Core Spray loop. The 'A' Core Spray loop was inoperable at the time due to planned maintenance. This resulted in a loss of the Core Spray safety function for approximately 7 hours and 44 minutes. The 'A' Core Spray loop was restored and returned to an operable status at 0616, which restored the Core Spray safety function. <br /><br /> The transfer to the alternate offsite power source also resulted in a Group II and III primary containment isolation, as designed. This is considered an invalid actuation. There were no actual safety consequences as a result of this event.
2782019001 | Peach Bottom 3 | 10/21/2019 | 12/19/2019 | ML19354A92 | <strong>Failure of Reactor Mode Switch Results in Condition Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On 10/21/19, Unit 3 was being shut down for a scheduled refueling outage. When the Reactor Mode Switch was moved to the Shutdown position, a reactor scram did not occur as expected. The operator depressed the nearby manual scram pushbuttons in accordance with plant procedures, which resulted in a successful scram of the reactor. <br /><br /> An Unusual Event was declared as a result of this condition. Local, State and NRC notifications were made (ENS #54340). <br /><br /> Investigation determined an internal connection in the switch had failed. The switch was repaired during the refueling outage. There were no actual safety consequences as a result of this condition.
2802019001 | Surry 1, Surry 2 | 07/21/2019 | 09/19/2019 | ML19273A42 | <strong>Failure to Align Angle Drive to Pump Results in Inoperable Emergency Service Water Pump</strong><br /><i>Abstract:&nbsp;</i>On June 23, 2019, with Units 1 and 2 at 100% power, the packing gland on the 1B Emergency Service Water Pump (ESWP) failed during periodic pump testing and the pump was declared inoperable. The packing gland was repaired and the pump was returned to service on June 24, 2019. During the next scheduled pump test on July 21, 2019, another packing failure occurred. Subsequent investigation revealed that both packing failures were caused by the angle drive to pump shaft not being aligned when the pump was replaced in May 2019. The decision making was not appropriate in that only first line supervisors were consulted before making the decision not to perform the alignment The decision should have been elevated to ensure a broader group of personnel were involved in the decision. <br /><br /> The ESWP 1B to angle drive alignment was performed in accordance with procedures and returned to service. Additionally, corrective actions will include a revision to the maintenance procedure and other changes focusing on improving proficiency and decision making. <br /><br /> This report is submitted pursuant to 10 CFR 50.73(a)(2)(i)(B) due to operations prohibited by Technical Specifications. Based on a risk assessment, the risk impact was determined to be of very low significance.
2802019002 | Surry 1, Surry 2 | 12/11/2019 | 02/04/2020 | ML20054A14 | <strong>Items Non-Conforming to Design for Tornado Missile Protection</strong><br /><i>Abstract:&nbsp;</i>On December 11, 2019, Surry Nuclear Power Plant determined that the certain Unit 1 and 2 Class 1 Structures, Systems, and Components (SSCs) did not conform with the licensing basis for protection against a design basis tornado generated missile.<br /><br /> The affected equipment was declared inoperable and enforcement discretion invoked in accordance with NRC Enforcement Guidance Memorandum (EGM) 15-002, Rev. 1, "Enforcement Discretion for Tornado Missile Protection Noncompliance." Initial compensatory measures were implemented pursuant to the guidance of NRC Interim Staff Guidance DSS-ISG-2016-01, Appendix A, within the time allowed by the applicable Limiting Conditions for Operation and the associated systems were then declared operable, but nonconforming. <br /><br /> Since the condition was part of the original plant design and licensing of the station, there was no specific cause identified.<br /><br /> There were no safety consequences as a result of this event. Actions are underway to address the condition.
2812019001 | Surry 2 | 01/29/2019 | 04/01/2019 | ML19098A16 | <strong>Foreign Material in Breaker Contact Causes Pressurizer Power Operated Relief Valve Block Valve Inoperability</strong><br /><i>Abstract:&nbsp;</i>On December 27, 2018, at 08:28 hours, with Units 1 and 2 at 100% power, the breaker for a Unit 2 Pressurizer Power Operated Relief Valve (PORV) block valve tripped on thermal over-current while performing a periodic test. Troubleshooting commenced, but the condition could not be duplicated, and the block valve (a motor operated valve) (MOV) was tested and successfully cycled several times with no issues. The valve was declared operable and returned to service at 14:18 hours. On January 29, 2019, additional testing and inspection of the block valve Motor Control Center (MCC) breaker was performed, and a nylon brush bristle was found within the contactor, inhibiting one phase of power to the MOV motor. Operability of the valve was required on December 4, 2018, when Unit 2 was in Intermediate Shutdown and heating up for return to power operation. Due to foreign material located in the contactor causing inconsistent operation, the block valve was conservatively determined to be inoperable since maintenance was performed on the MCC breaker during the Unit 2 2018 refueling outage. On January 29, 2019, the bristle was found and removed from the contactor, and the PORV block valve was returned to operable status. <br /><br /> This report is submitted pursuant to 10 CFR 50.73(a)(2)(i)(B) due to operation prohibited by Technical Specifications.
2812019002 | Surry 2 | 11/20/2019 | 01/17/2020 | ML20028D61 | <strong>Auxiliary Feedwater System Loss of Safety Function due to Check Valve Failure to Close</strong><br /><i>Abstract:&nbsp;</i>At 2144 [EST] on 11/20/2019, with Unit 2 at 100 percent power, all three (3) Unit 2 Auxiliary Feedwater (AFW) pumps were declared inoperable due to the Unit 2 Turbine Driven (TD) AFW pump discharge check valve failing to completely close, which caused flow from a running Unit 2 Motor Driven (MD) AFW to partially recirculate back to the Emergency Condensate Storage Tank. At 2203 the two (2) MDAFW pumps were declared operable after the discharge isolation valves for the TDAFW pump were closed. <br /><br /> The Unit 2 TDAFW discharge check valve condition existed from 10/28/19 to 11/20/19 and could have adversely impacted the ability of AFW to function properly. The cause of this event was determined to be excessive wear on the discharge check valve disc assembly parts causing the disc to stick partially open.<br /><br /> The safety consequences associated with this event are bounded by the safety analyses documented in UFSAR Chapter 14. The affected check valve's internal assembly parts were replaced. To prevent recurrence, a corrective action is planned to periodically inspect and/or replace the check valve internals, as needed, on both units. Unit 1 was not impacted by this event since it was in cold shutdown at the time.
2932019001 | Pilgrim | 01/08/2019 | 02/28/2019 | ML19064A59 | <strong>Reactor Core Isolation Cooling System Declared Inoperable During Surveillance Testing</strong><br /><i>Abstract:&nbsp;</i>On January 8, 2019, the Reactor Core Isolation Cooling (RCIC) system was declared inoperable. This action was taken because the RCIC system turbine-pump did not achieve the acceptance criteria of flow rate, discharge pressure, and speed during the performance of a surveillance test. <br /><br /> Due to the unexpected response a Failure Modes Analysis was initiated to determine the cause. No deficient conditions were identified during troubleshooting. However, based on the investigation, the team determined that the direct cause was output signal loss from the RCIC flow controller. A spare calibrated controller was installed, the system was tested, and successfully returned to service. <br /><br /> The High Pressure Coolant Injection system was operable and capable of providing high pressure core cooling similar to the RCIC system. This event had no impact on the health and/or safety of the public. <br /><br /> This report is submitted in accordance with Title 10 Code of Federal Regulations 50.73(a)(2)(v)(D).
2932019002 | Pilgrim | 01/03/2019 | 03/04/2019 | ML19065A05 | <strong>Failure of Main Steam Isolation Valve Limit Switch Results in a Condition Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On January 5, 2019 during the performance of Main Steam Isolation Valve (MSIV) surveillance testing, control room alarm MSIV Not Full Open did not annunciate when MSIV AO-203-1C was fully closed for stroke time testing. The MSIV Not Full Open alarm is expected when any MSIV position RPS limit switch opens. The cause was traced to failure of the MSIV position Reactor Protection System (RPS) limit switch LS6 to properly open and the associated logic system channel was placed in the tripped condition. On February 7, 2019, a detailed review of plant computer and annunciator system alarm data discovered that the MSIV position RPS limit switch LS6 did not open as expected when MSIV AO-203-1C was closed on January 3; 2019 and the associated logic system channel was not placed in a tripped condition within the time constraints specified in Technical Specifications. The allowable action time to trip (de-energize) the RPS channel associated with failed limit switch LS6 on MSIV AO-203-1C was exceeded because operations personnel did not correctly interpret the absence of the MSIV Not Full Open alarm upon closure of the MSIV on January 3, 2019. At the time of the event, the reactor mode selector switch was in the RUN position and the reactor was at 35 percent reactor thermal power. <br /><br /> This event had no impact on the health and/or safety of the public. <br /><br /> This report is submitted in accordance with Title 10 Code of Federal Regulations 50.73(a)(2)(i)(B); Operation or Condition Prohibited by Technical Specifications.
2932019003 | Pilgrim | 04/13/2019 | 06/10/2019 | ML19161A28 | <strong>Condition Prohibited by Technical Specifications Involving the Mechanical Vacuum Pump</strong><br /><i>Abstract:&nbsp;</i>On April 13, 2019, the operating crew placed the key lock switch for Main Steam Process Radiation Monitor (PRM) 1705-2D to the INOP position and restored the Mechanical Vacuum (MV) pump to ready state. Subsequent research into the INOP position for the PRM 1705-2D switch revealed that this action does not introduce a channel trip signal. Not placing the PRM in a trip condition with the MV pump restored to ready state, is a violation of Technical Specification Action Statement 3.8.2.A.2 to place the channel or associated trip system in trip within 24 hours. <br /><br /> There were no actual consequences to safety of the general public, nuclear safety, industrial safety, or radiological safety for this event. <br /><br /> This report is submitted in accordance with Title 10 Code of Federal Regulations 50.73(a)(2)(i)(B).
2932019004 | Pilgrim | 05/17/2019 | 06/11/2019 | ML19162A03 | <strong>Manual Reactor Scram due to Degrading Condenser Vacuum</strong><br /><i>Abstract:&nbsp;</i>On Friday, May 17, 2019 at 2303 [EDT], with the reactor at approximately 70% core thermal power, Pilgrim Nuclear Power Station initiated a manual reactor scram due to degrading condenser vacuum as a result of the trip of Seawater Pump B. Investigation into the cause identified the Seawater Pump B breaker ground sensing relay in the tripped state. <br /><br /> Following the Seawater Pump B trip and reactor scram, Main Condenser parameters responded as expected to a loss of seawater pump transient, no anomalies were noted. There were no radiological releases due to this event. All control rods inserted fully. All other plant systems responded as designed. <br /><br /> This event had no impact on the health and/or safety of the public. <br /><br /> This report is submitted in accordance with 10 CFR 50.73(a)(2)(iv)(A).
2962019001 | Browns Ferry 3 | 03/09/2019 | 07/08/2019 | ML19189A12 | <strong>Automatic Reactor Scram due to a Turbine Load Reject</strong><br /><i>Abstract:&nbsp;</i>On March 9, 2019, at approximately 2259 Central Standard Time (CST), Browns Ferry Unit 3 received an automatic Reactor SCRAM from 100 percent power as a result of a Turbine Load Reject. Browns Ferry Unit 3 declared a Notification of Unusual Event due to loss of the 500kV offsite source. The automatic SCRAM occurred as a Licensed Reactor Operator (LRO) made adjustments to lower incoming reactive power on Unit 3 at the request of the Balancing Authority. The LRO incorrectly operated a hand switch and changed the automatic voltage regulator (AVR) from auto to manual. In this mode of operation, the dynamic limiter is removed, which allows Operations personnel to adjust Mega Volt Amps Reactive (MVAR) beyond the Under Excitation Limiter (UEL) protection setting. As a result, the generator circuit breaker tripped causing a Turbine Load reject and an automatic SCRAM. All safety systems actuated as designed. <br /><br /> The root cause for this event was determined to be that Operations department leaders have allowed continued negative human performance (HU) behaviors by inconsistently providing coaching or reinforcing the use of appropriate HU barriers. The corrective action to prevent recurrence is to revise the Operations Excellence Program, BFN-ODM-4.28, to require use of a dynamic learning environment to develop Operations Department Leaders' skills in coaching and reinforcing the use of appropriate HU barriers. Training will be required prior to assuming shift following initial qualification as Nuclear Unit Senior Operators (NUSO) and Shift Managers (SM). The currently qualified NUSOs and SMs have received training. <br /><br /> A plastic cover was placed over the manual/auto select voltage regulator hand switch on all three Units to mitigate unintentional operation of the AVR from automatic to manual control. The Operating Instruction procedure for the Turbine Generator System was revised to prompt Operations personnel to validate the initial status of the AVR prior to adjusting MVAR.
2982019001 | Cooper Station | 03/06/2019 | 08/09/2019 | ML19241A24 | <strong>Valve Test Failures Result in a Condition Prohibited by Technical Specifications and a Loss of Safety Function</strong><br /><i>Abstract:&nbsp;</i>On March 4, March 5, and March 6, 2019, three of eight Target Rock safety relief valve (SRV) pilot assemblies, removed during Refueling Outage 30, failed to lift within Technical Specifications (TS) lift setpoint requirements The pressure setpoint of the first failed pilot assembly was 1090 psig, the SRV pilot assembly lifted at 1256.2 psig. The pressure setpoint of the second failed pilot assembly was 1080, the SRV pilot assembly lifted at 1208.5 psig. The pressure setpoint of the third failed pilot assembly was 1090, the SRV pilot assembly lifted at 1124.2 psig. Three subsequent lifts were performed for all failed SRV pilot assemblies and the results were within the TS pressure setpoint tolerances.<br /><br /> The cause of the failures was determined to be corrosion bonding.<br /><br /> Although the setpoint lift pressures of the SRV pilot valve assemblies exceeded TS requirements, an analysis of this event concluded the thermal limits and American Society of Mechanical Engineers overpressure transients did not exceed allowable limits. Public safety was not at risk. Safety to plant personnel and plant equipment was not at risk. <br /><br /> A TS Amendment to TS 3.4.3 will be submitted that will address the failure to meet the TS criteria for the Target Rock two-stage SRVs. Following submittal, a tracking mechanism will be established for TS change approval.
2982019002 | Cooper Station | 08/08/2019 | 10/07/2019 | ML19295F42 | <strong>Secondary Containment Rise in Differential Pressure Results in Loss of Safety Function</strong><br /><i>Abstract:&nbsp;</i>On August 8, 2019, a spike in Secondary Containment occurred with differential pressure (DP) exceeding the Technical Specification limit of 0.25 inch of vacuum water gauge (wg) causing Secondary Containment to be inoperable for 7 minutes. The spike was due to Reactor Building heating, ventilation, and air conditioning (HVAC) supply filter media being advanced excessively causing DP to rise to 0.19 vacuum wg. The DP was not immediately identified by Control Room personnel due to Secondary Containment DP not reaching the high pressure alarm setpoint and they were unaware of the filters being advanced. <br /><br /> Causal factors were that the condition of the supply filters was not properly prioritized and risk associated with the supply filter activities was not recognized and controlled properly due to it being classified as a skill of the craft activity. <br /><br /> The operations department skill of the craft list was revised to delete activities such as advancing the supply filters that have plant operational risk. More formal controls are being implemented for operation and maintenance of the reactor building HVAC supply filters. Operations department wide communications are planned to discuss the event, causal factors, and corrective actions. There was no impact on nuclear safety, plant reliability, radiological safety, or industrial safety.
2982019003 | Cooper Station | 12/06/2019 | 02/04/2020 | ML20043D73 | <strong>Division 2 Service Water Discharge Blockage Resulting in Unplanned Service Water Inoperability</strong><br /><i>Abstract:&nbsp;</i>On December 5, 2019, while attempting to place Reactor Equipment Cooling Heat Exchanger B in service, Service Water flow to the heat exchanger was unable to be established. Reactor Equipment Cooling Subsystem B was declared Inoperable at 02:15 on December 6, 2019 following validation of the condition. On December 8, 2019, troubleshooting determined the flow blockage was on the common buried Division 2 Service Water piping downstream of Diesel Generator 2, Reactor Equipment Cooling Heat Exchanger B, and Residual Heat Removal Heat Exchanger B. Service Water Subsystem B and Diesel Generator 2 were declared Inoperable at 05:00 on December 8, 2019. <br /><br /> Manual sounding of the discharge canal was performed to determine the sediment levels above the Division 2 Service Water pipe outfall. The sounding identified approximately 15 feet of sediment. A Work Order was prepared for removing the sediment by dredging the discharge canal. Dredging commenced on December 12, 2019. Within one hour, Service Water flow was established through the Division 2 outfall. Dredging continued to remove sediment from around the Division 2 outfall, then proceeded to remove sediment from around the Division 1 outfall. A Compensatory Measure was implemented to maintain continuous Service Water flow from the outfalls above 1000 gallons per minute (gpm). Operability was restored at 05:00 on December 13, 2019.
3062019001 | Prairie Island 2 | 08/01/2019 | 09/27/2019 | ML19270D99 | <strong>Reactor Coolant Isolation Valve Leakage Results in Condition Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On August 1, 2019 at 0935, Unit 2 control room received a high rate of change alarm from containment radiation monitors. At the time, station personnel were performing Reactor Coolant System (RCS) sampling. Once the evolution was completed, containment radiation levels decreased to levels observed prior to sampling. Sampling of containment atmosphere found the presence of Argon-41 indicating that the source of the increased radiation levels was from the RCS. A review of system lineup and components found that the most likely source of the increased radiation levels was MV-32410, the reactor coolant loop B hot leg sample inboard isolation valve. Indications are that the seat itself is not leaking but that damage to an internal diaphragm allowed RCS to vent to containment. MV-32410 and MV-32411, reactor coolant loop B hot leg sample outboard isolation valve, are in series primary containment isolation valves for a single penetration. The probable damage to the valve was not identified until August 7, 2019. Per Technical Specification 3.6.3, if a penetration flow path with two primary containment isolation valves is inoperable, isolate the penetration flow path by use of at least one closed and de-activated valve, closed manual valve, blind flange, or check valve within 4 hours. If this condition is not met, Condition F requires the unit to be in Mode 3 within six hours and Mode 5 within 36 hours. As a result, this was a condition prohibited by technical specifications because these conditions were not met.
3112019001 | Salem 2 | 01/31/2019 | 04/01/2019 | ML19091A26 | <strong>Salem Unit 2 Manual Reactor Trip due to Circulating Water Intake Frazil Ice Blockage</strong><br /><i>Abstract:&nbsp;</i>On January 31, 2019 at 0301, Salem Unit 2 Reactor was manually tripped when four of six circulators were manually tripped on high traveling water screen differential pressures (DP) due to the accumulation of Frazil Ice on the traveling water screens. All systems functioned as expected and Unit 2 was stabilized in MODE 3 at normal operating pressure and temperature.<br /><br /> This event was reportable in accordance with 10CFR50.73(a)(2)(iv)(A). Notification of this event was provided via ENS report 53852.
3112019002 | Salem 2 | 08/11/2019 | 10/10/2019 | ML19283A00 | <strong>Salem Unit 2 Manual Reactor Trip and Auxiliary Feed Water System Actuation</strong><br /><i>Abstract:&nbsp;</i>At 0814 on 8/11/19, with Unit 2 at 83 percent power during a planned load reduction, the reactor was manually tripped due to degraded feedwater flow control to the 23 Steam Generator caused by a malfunction of the associated Feedwater Regulating Valve, 2313F19 All systems responded normally post-trip An actuation of the Auxiliary Feedwater system occurred following the manual reactor trip as expected due to low level in the steam generators. The unit was stabilized in Mode 3 <br /><br /> The failed equipment was repaired. <br /><br /> This event is reportable in accordance with 10 CFR 50 73(a)(2)(iv)(A).
3152019001 | Cook 1 | 03/04/2019 | 04/30/2019 | ML19122A17 | <strong>Two Main Steam Safety Valve Setpoints Found Outside Technical Specification Limits</strong><br /><i>Abstract:&nbsp;</i>On March 4, 2019, Donald C. Cook Unit 1 was in Mode 1 and holding at approximately 49% reactor power while performing Technical Specification (TS) surveillance testing on the Main Steam Safety Valves (MSSVs) setpoints, just prior to the Unit 1 Cycle 29 (U1C29) Refueling Outage.<br /><br /> The Unit 1 Steam Generator (SG) #2 MSSVs 1-SV-1B-2 and 1-SV-2A-2 as found setpoints were above the TS allowable setpoint pressure of +/- 3% lift setpoint pressure. <br /><br /> Based on the guidance in NUREG-1022, Revision 3, the Unit 1 SG #2 MSSVs were considered to be inoperable longer than allowed by TS. <br /><br /> The cause of the failure was determined to be setpoint drift. The MSSV setpoints were adjusted and, after adjustment, the MSSVs passed the as left testing criteria of +/- 1% lift setpoint pressure. Since a similar cause was determined for both unsatisfactory as found lift pressures, this condition may have arisen over a period of time, and there is a likelihood that the affected MSSVs may not have been operable during plant operation. <br /><br /> Therefore, this event is reportable as an Operation or Condition Prohibited by TS in accordance with 10 CFR 50.73(a)(2)(i)(B).
3152019002 | Cook 1 | 05/29/2019 | 11/26/2019 | ML19333B81 | <strong>Condition Prohibited by Technical Specification due to an Inoperable Steam Generator Stop Valve Dump Valve</strong><br /><i>Abstract:&nbsp;</i>On May 6, 2019, 1-MRV-222, Steam Generator 2 Stop Valve Train 'B' Dump Valve, was stroke timed in Mode 4, coming out of the U1C29 refueling outage. The valve stroked in approximately 4.4 seconds with an allowable time of 2.0 seconds. A second stroke was performed and the valve appeared to stroke much faster. After the packing was wetted, the valve was then retested and passed with a stroke time of 1.76 seconds.<br /><br /> On May 29, 2019, 1-MRV-222 was stroked for its quarterly test, and again failed with a stroke time of 6.84 seconds.<br /><br /> A Past Operability Determination Evaluation was performed and concluded that 1-MRV-222 was inoperable from May 7, 2019, when Unit 1 entered Mode 3, until it passed its surveillance after being repacked and tested on May 30, 2019. The time period over which 1-MRV-222 was inoperable exceeded the time allowed by Technical Specification (TS) 3.7.2, SGSVs. Unit 1 also entered a Mode of applicability with 1-MRV-222 inoperable, which is prohibited without meeting LCO 3.0.4.<br /><br /> Therefore, this event is reportable as an Operation or Condition Prohibited by TS in accordance with 10 CFR 50.73(a)(2)(i)(B).
3162019001 | Cook 2 | 07/21/2019 | 09/12/2019 | ML19259A02 | <strong>Manual Reactor Trip due to Non-Essential Service Water System Degraded Condition</strong><br /><i>Abstract:&nbsp;</i>On July 19, 2019, Donald C. Cook Nuclear Plant (CNP) Unit 2 started experiencing degraded performance on the Unit 2 Non-Essential Service Water System (NESW), which affected one (1) NESW pump. On July 21, 2019, a second NESW pump on Unit 2 was affected. On July 21, 2019, a rapid downpower over approximately 40 minutes was conducted on Unit 2, and a manual reactor trip was initiated from 17 percent power to allow for investigation and repair of the degraded NESW System, before any thresholds were exceeded. The manual reactor trip was completed at 0826 EDT on July 21, 2019. <br /><br /> The manual Reactor Protection System (RPS) actuation was reported via Event Notification 54176 in accordance with 10 CFR 50.72(b)(2)(iv)(B) and 10 CFR 50.72(b)(3)(iv)(A). This manual RPS actuation is reportable pursuant to 10 CFR 50.73(a)(2)(iv)(A) as, "Any event or condition that resulted in manual or automatic actuation of the RPS." <br /><br /> The direct cause of the degraded NESW system performance was a high differential pressure on both Unit 2 NESW strainers, due to excessive loading of small mussels and plugged backwash lines. Both strainers were cleaned, backwashed lines flushed, and returned to service.
3182019001 | Calvert Cliffs 2 | 02/14/2019 | 06/28/2019 | ML19183A17 | <strong>Misapplication of Technical Specification Following Failed Surveillance Resulted in Operation Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On February 14, 2019 Calvert Cliffs conducted Surveillance Test Procedure (STP) M-471-2, Personnel Access Local Leak Rate Test, on Unit 2 containment personnel air lock (PAL). Calvert Cliffs was performing STP M-471-2 to satisfy Surveillance Requirement 3.6.2.1 to perform air lock leakage rate in accordance with the Containment Leakage Rate Testing Program. During performance of this STP technicians were unable to maintain the required test pressure and heard audible indication of an air leak from Unit 2 containment PAL outer door equalization penetration. <br /><br /> Calvert Cliffs personnel incorrectly evaluated the excessive leakage rendered only the PAL outer door inoperable (Technical Specification (TS) LCO 3.6.2.A) rather than the entire air lock (TS 3.6.2.C). This resulted in not taking the required Actions of TS LCO 3.6.2.C and TS LCO 3.6.2.D. As a result, Calvert Cliffs operated in a condition prohibited by TS when it did not place Unit 2 in MODE 3 and subsequently MODE 5 within the required completion times. Repair activities were completed on the outer door equalization valve, 2HVCPI-1025, and the surveillance was successfully completed. Planned corrective actions include revisions to STP-M- 471-2 and TS Bases to provide clarity to prevent future misapplication of TS.
3232019001 | Diablo Canyon 2 | 11/30/2019 | 01/29/2020 | ML20029E86 | <strong>Containment Spray Inoperable in Mode 4</strong><br /><i>Abstract:&nbsp;</i>On November 30, 2019, at 1100 PST, with Unit 2 in Mode 4, Operations identified that both trains of containment spray had been made inoperable (DC control power removed) earlier in the day, at approximately 0237 hours as part of preparations for a planned Mode 5 entry. <br /><br /> The containment spray pumps are required to be operable (along with the containment fan cooler units (CFCUs)) in Modes 1-4 in accordance with Technical Specification (TS) 3.6.6. With Containment Spray Pumps 2-1 and 2-2 inoperable, TS 3.6.6 Condition F requires immediate entry into TS 3.0.3. Since Unit 2 was in Mode 4, TS 3.0.3 required placing the unit in Mode 5 within 37 hours. At 1125 hours, both trains of containment spray were returned to operable and TS 3.6.6 and TS 3.0.3 were exited. The five CFCUs remained operable at all times throughout the inoperability of the containment spray pumps. <br /><br /> This event was a result of human error. <br /><br /> There was no impact on the health and safety of the public or plant personnel.
3242019001 | Brunswick 2 | 03/05/2019 | 04/30/2019 | ML19120A33 | <strong>Automatic Actuation of the Primary Containment Isolation System</strong><br /><i>Abstract:&nbsp;</i>At 05:35 EST on March 5, 2019, with Unit 2 in Mode 5 at 0% power, an actuation of the Primary Containment Isolation System (PCIS) occurred during hydro-lasing of the reactor water level variable leg instrumentation line nozzle N011B in the reactor cavity. The hydrolasing activity caused low reactor water level to be sensed on the shutdown range level instrumentation. Per design, the low level 1 signal resulted in Group 2 (e.g., floor and equipment drain isolation valves), Group 6 (e.g., monitoring and sampling isolation valves) and Group 8 (e.g., shutdown cooling isolation valves) isolations. This event is being reported in accordance with 10 CFR 50.73(a)(2)(iv)(A) as an event that resulted in a valid actuation of PCIS.<br /><br /> This event resulted from the failure to properly assess risk and put compensatory actions in place when planning the hydro-lasing activity on the N011B nozzle. There was no adverse impact on the health and safety of the public. Although there was a brief interruption of shutdown cooling, the Alternate Decay Heat Removal (ADHR) System was in service and the Reactor Cavity was flooded up. Since decay heat load was within the capacity of the ADHR system, there was no loss of Decay Heat Removal capability. The Group 8 isolation was reset and shutdown cooling was restored within approximately 10 minutes. The safety significance of this event was minimal.
3242019002 | Brunswick 2 | 03/30/2019 | 05/28/2019 | ML19148A59 | <strong>Manual Reactor Protection System Actuation and Specified System Actuation</strong><br /><i>Abstract:&nbsp;</i>At 17:47 Eastern Daylight Time (EDT) on March 30, 2019, with Unit 2 in Mode 1 at approximately 23 percent power and main turbine startup in progress, high temperature was sensed at main turbine bearing 9. A manual main turbine trip and manual actuation of the Reactor Protection System (RPS) were initiated in response to the high bearing temperature. All control rods inserted as expected during the scram. When the scram was inserted, reactor water level dropped below the Low Level 1 (LL1) actuation setpoint. Per design, the LL1 signal resulted in automatic actuation of the Primary Containment Isolation System (PCIS) with closure of Group 2, 6, and 8 isolation valves. Operators manually closed the Main Steam Isolation Valves (MSIVs), in anticipation of low condenser vacuum, prior to the Group 1 PCIS signal being received. All systems responded as designed. This event is being reported in accordance with 10 CFR 50.73(a)(2)(iv)(A) as an event that resulted in valid actuations of RPS and PCIS. <br /><br /> The direct cause of this event was insufficient lubricating oil supply to the main turbine bearing 9 which caused the bearing to overheat; leading to the manual scram. The most probable cause for the insufficient oil flow was design differences which resulted in a misalignment between the lower half bearing flow channel and the oil supply port in the main turbine 9 bearing housing. Corrective actions include a procedure change to ensure that lubricating oil supply oil flow is not restricted as a result of bearing replacement.
3242019003 | Brunswick 2 | 06/12/2019 | 07/31/2019 | ML19213A15 | <strong>High Pressure Coolant Injection (HPCI) Inoperable</strong><br /><i>Abstract:&nbsp;</i>At 21:27 Eastern Daylight Time (EDT) on June 12, 2019, during routine testing on Unit 2, the High Pressure Coolant Injection (HPCI) turbine experienced an overspeed trip. Following the overspeed trip, the turbine coasted down and reset, then restarted and rolled to rated conditions as-designed. As a result, the response time of the system exceeded the 60-second acceptance criteria, thereby rendering the system inoperable. Reactor Core Isolation Cooling (RCIC) System and Automatic Depressurization System (ADS) remained operable during this event. <br /><br /> Failure of Unit 2 HPCI to meet the 60 second response time acceptance criteria was caused by a momentary failure of the Electric Governor – Remote (EG-R) to control HPCI Turbine speed during the initial turbine roll. The EG-R Actuator was replaced and the testing was repeated successfully with the response time acceptance criteria met. Historical data was reviewed on Unit 1 and it was confirmed that this condition was isolated to Unit 2.<br /><br /> The safety significance of this event is minimal. There was no impact on the health and safety of the public or plant personnel. This event is being reported in accordance with 10 CFR 50.73(a)(2)(v)(D).
3252019001 | Brunswick 1, Brunswick 2 | 03/25/2019 | 05/23/2019 | ML19143A37 | <strong>Unplanned Automatic Start of Emergency Diesel Generators</strong><br /><i>Abstract:&nbsp;</i>At 04:02 Eastern Daylight Time (EDT) on March 25, 2019, an actuation of the four Emergency Diesel Generators (EDGs) occurred. Unit 1 was in Mode 1 at approximately 100 percent power and Unit 2 was in Mode 4 at 0 percent power. Unit 2 was in the process of aligning the electrical distribution system to power the emergency buses via the Unit Auxiliary Transformer (UAT) when a main generator differential lockout relay actuated; thereby starting the EDGs. The emergency buses remained energized from offsite power via the Startup Auxiliary Transformer (SAT) and, therefore, the EDGs did not tie to their respective buses. The EDGs responded per design to this event. <br /><br /> The cause of event was a historical design change error. During replacement of the original Main Power Transformers (MPTs), the fact that the new transformers have lower second order harmonic in-rush current was not identified and, as a result, appropriate protective relay settings were not implemented. <br /><br /> Corrective actions include revising operating procedures to preclude EDG automatic starts on Main Generator primary lockout when restoring the UAT backfeed.
3252019002 | Brunswick 1 | 03/28/2019 | 05/23/2019 | ML19143A37 | <strong>Degraded Principal Safety Barrier, Technical Specification Shutdown, and Automatic System Actuation</strong><br /><i>Abstract:&nbsp;</i>At 14:19 Eastern Daylight Time (EDT) on March 28, 2019, with Unit 1 in Mode 1 at approximately 100 percent power, drywell pressure and floor drain leakage began to increase. Operators proceeded with a controlled shutdown per procedures. The reactor was scrammed at 16:03 EDT to complete the shutdown. At 16:54 EDT, following the scram, Primary Containment Isolation System (PCIS) actuation occurred, closing the outboard Main Steam Isolation Valves (MSIVs) due to low condenser vacuum. Subsequently, Reactor Protection System (RPS) actuation occurred due to low reactor water level. The safety function of the MSIVs and RPS had already been completed. There was no impact on the health and safety of the public or plant personnel. <br /><br /> This event was a result of a steam leak in the drywell caused by the failure of a 1-inch cryogenic pipe coupling. The failure was due to hydrogen embrittlement from long-term exposure to high temperature and elevated hydrogen levels. A Unit 1 and Unit 2 extent of condition evaluation was performed; susceptible cryogenic couplings were replaced with welded fittings. <br /><br /> As a result of the Technical Specification-required shutdown, the valid actuations of PCIS and RPS, and the degradation of a principal safety barrier, this event is being reported in accordance with 10 CFR 50.73(a)(2)(i)(A), 10 CFR 50.73(a)(2)(iv)(A), and 10 CFR 50.73(a)(2)(ii)(A) respectively.
3252019003 | Brunswick 1 | 04/21/2019 | 06/19/2019 | ML19170A39 | <strong>False High Reactor Water Level Results in Automatic Specified System Actuations</strong><br /><i>Abstract:&nbsp;</i>At 23:07 Eastern Daylight Time on April 21, 2019, with Unit 1 in Mode 1 at approximately 100 percent power, the Main Turbine and both Reactor Feed Pumps (RFPs) tripped resulting in a reactor scram and reactor water level dropping below Low Level (LL) 1 and 2. The LL1 resulted in Group 2 (i.e., floor and equipment drain isolation valves), Group 6 (i.e., monitoring and sampling isolation valves), and Group 8 (i.e., shutdown cooling isolation valves) isolations. The LL2 resulted in Group 3 (i.e., Reactor Water Cleanup) isolation, a secondary containment isolation signal, and High Pressure Coolant Injection and Reactor Core Isolation Cooling (RCIC) automatically starting and injecting into the vessel. All control rods inserted as expected during the scram and all systems responded as designed. <br /><br /> The Main Turbine and both RFPs tripped due to two out of three level instruments sensing a false high reactor water level. The false signal was a result of hydrogen deflagration in the reactor level condensing chamber due to a flaw in the original design. <br /><br /> There was no impact on the health and safety of the public or plant personnel. This event is being reported in accordance with 10 CFR 50.73(a)(2)(iv)(A) due to actuations of the Reactor Protection System, Primary Containment Isolation System, Emergency Core Cooling System, and RCIC.
3272019001 | Sequoyah 1 | 04/14/2019 | 06/11/2019 | ML19163A04 | <strong>Reactor Trip on Low-Low Steam Generator Level due to the Loss of a Main Feedwater Pump</strong><br /><i>Abstract:&nbsp;</i>On April 14, 2019, at 0320 eastern daylight time (EDT), Sequoyah Nuclear Plant, Unit 1, experienced an automatic reactor trip. The reactor trip was preceded by a turbine runback, because main feedwater pump (MFP) 1A tripped on low lube oil pressure. In response to the 1A MFP trip, the Auxiliary Feedwater (AFW) System actuated, as designed; however, AFW and the remaining main feedwater pump (1B) were not able to provide sufficient feedwater flow to maintain steam generator level. This resulted in an automatic reactor trip due to low-low level in the Loop 3 steam generator (SG). The causes of the reactor trip were previous MFP turbine hydraulic control system modifications coupled with an unvalidated turbine runback setpoint resulting in the inability to supply adequate feedwater flow to the SGs during the loss of a MFP transient. The corrective actions to prevent recurrence are: (1) implement digital feed pump control upgrade via an engineering change package, and (2) implement a revised turbine runback setpoint, as determined, as part of an engineering change package.
3272019002 | Sequoyah 1 | 05/29/2019 | 07/26/2019 | ML19207A06 | <strong>Steam Generator Pressure Transmitter Degraded Sensing Line Causes Condition Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On April 15, 2019, during a post trip review, it was identified that Steam Generator #3 pressure transmitter, 1-PT-1-23, had demonstrated sluggish behavior during the transient. The pressure input is utilized by the Engineered Safety Features Actuation System for several postulated events. Operations declared the instrument inoperable, and entered the appropriate Technical Specifications (TS) Limiting Condition for Operation (LCO) until maintenance activities restored operability. Investigation revealed that the instrument response exceeded the TS channel check acceptance criteria. Historical search and past operability evaluation completed May 29, 2019, determined that previous identification was not effectively resolved, and that there were multiple periods where other transmitters were removed from service at the same time as the affected transmitter. This led to a condition prohibited by TS, and a condition that could have prevented the fulfillment of a safety function. The cause of the component failure was debris found in the pressure transmitter sensing line due to a lack of regularly scheduled preventative maintenance. The corrective action is to ensure preventative maintenance instructions are created to clear sensing lines for Main Steam transmitters.
3272019003 | Sequoyah 1 | 08/27/2019 | 10/23/2019 | ML19297G40 | <strong>Automatic Reactor Trip due to Negative Rate Trip as a Result of a Dropped Control Rod</strong><br /><i>Abstract:&nbsp;</i>On August 27, 2019, at 0109 eastern daylight time, Sequoyah Nuclear Plant, Unit 1, automatically tripped as a result of Control Bank D Control Rod H-8 dropping into the core. All safety related equipment operated as designed, all control rods fully inserted as required, and auxiliary feedwater automatically initiated as expected. Additionally, during a post trip review, it was identified that the Steam Generator #3 pressure transmitter, 1-PT-1-23, demonstrated sluggish behavior. This pressure transmitter had previously been identified as inoperable during a Unit 1 reactor trip occurring April 14, 2019. Maintenance was performed following the April event and the transmitter was declared operable. After further review, it was determined that the transmitter was inoperable since November of 2015. <br /><br /> For Control Rod H-8, troubleshooting was performed and did not identify any immediate concerns with the Control Rod Drive Mechanism (CRDM) System. With no cause identified, a monitoring plan was developed to enable identification of a cause in the event the condition was repeated prior to the Unit 1 refueling outage. For 1-PT-1-23, work orders were completed to backfill and blow out the sensing lines and the transmitter was declared operable on August 28, 2019. The causes of these events are still under investigation. When the final investigations are completed, a supplement to this LER will be provided.
3272019004 | Sequoyah 1, Sequoyah 2 | 12/16/2019 | 02/13/2020 | ML20044D62 | <strong>Automatic Actuation of Emergency Diesel Generators due to Loss of Power to 6.9KV Shutdown Board</strong><br /><i>Abstract:&nbsp;</i>On December 16, 2019, at 03:58 Eastern Standard Time (EST), Sequoyah Nuclear Plant Unit 1 experienced a loss of 1B-B 6.9 kilo-Volt (KV) Shutdown Board offsite power when the normal feeder breaker from the 1C 6.9 KV Unit Board to the 1B-B 6.9 KV Shutdown Board tripped. This resulted in a loss of offsite power to the 1B-B 6.9 KV Shutdown Board, which automatically started all four emergency diesel generators as designed. The 1B-B 6.9 KV Shutdown Board was automatically reenergized from its associated emergency diesel generator, and was subsequently transferred back to an alternate offsite power supply. <br /><br /> The cause of the feeder breaker trip was an overcurrent relay component failure, specifically a metal oxide varistor of the incorrect voltage rating, which actuated the breaker overcurrent protection. The failed relay was replaced with a new relay of the proper voltage rating. An extent of condition will be performed as plant conditions permit to evaluate any other 250 VDC rated applications that may have incorrect voltage components.
3282019001 | Sequoyah 2 | 06/17/2019 | 11/15/2019 | ML19322A62 | <strong>Component Cooling Water System Train A Inoperable Longer Than Allowed by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On June 17, 2019, at 1723 eastern daylight time (EDT), a temporary modification was implemented on the Essential Raw Cooling Water (ERCW) System. The purpose of the modification was to swap the function of two valves in the ERCW System because the function of one valve was determined to be degraded. Ordinarily, one of the valves could be controlled and throttled from the Main Control Room. Various throttling positions are used to allow operational flexibility for ERCW flow rates, while allowing the valve to be quickly placed in throttled positions to satisfy the ERCW flow balance requirements for accident alignments. During the flush of a Component Cooling Water System (CCS) heat exchanger on August 24, 2019, one of the valves was placed in a throttled position determined as part of the temporary modification. Shortly after beginning the flush, CCS alarms were received in the MCR which caused operators to terminate the flush and restore ERCW flows. Section XI test data were evaluated and it was determined that the throttled positions implemented by the modification did not allow the required flow. On August 28, 2019, a flow balance test was conducted and the correct positions were determined. The event rendered Unit 2 A Train of the CCS inoperable for longer than allowed by Technical Specifications.<br /><br /> The cause of this event is the failure to adequately recognize the risk of relying on an indirect method to determine the throttle valve positions. Corrective actions include completing a required reading and lessons learned for the Engineering Department regarding the event and the circumstances associated with the event.
3282019002 | Sequoyah 2 | 12/12/2019 | 02/07/2020 | ML20038A10 | <strong>Loss of Heater Drain Tank Flow Causes Turbine Runback and Manual Reactor Trip</strong><br /><i>Abstract:&nbsp;</i>On December 12, 2019, at 0433 Eastern Standard Time (EST), Sequoyah Nuclear Plant Unit 2 was manually tripped as a result of a secondary system level control valve positioner failure. The failure of the valve led to reduced secondary system Heater Drain Tank flow and a unit down power. During the down power, manual reactor trip criteria was reached. All safety-related equipment operated as designed, all controls rods fully inserted as required, and the Auxiliary Feedwater system automatically initiated as expected. <br /><br /> The failed positioner was replaced with a newer model. Investigation revealed that a fine adjust screw had loosened, preventing the valve positioner from correctly responding to control signals. An extent-of-condition was performed to identify other susceptible components, and actions have been taken to replace a necessary component with a newer model.
3312019001 | Duane Arnold | 04/20/2019 | 06/17/2019 | ML19171A19 | <strong>Manual Reactor Scram due to Lowering Reactor Water Level</strong><br /><i>Abstract:&nbsp;</i>On April 20, 2019, while operating at 100% power, NextEra Energy Duane Arnold (DAEC) experienced a trip of both reactor feed pumps due to a loss of suction pressure. As a result, plant operators inserted a manual scram. All control rods inserted, as required. As a result of the feed pump trips and scram, the High Pressure Coolant Injection (HPCI) and Reactor Core Isolation Cooling (RCIC) automatically injected. In addition, containment isolations occurred, as expected for this event. This resulted in a 4-hour event report to the NRC under 10 CFR 50.72 section 50.72(b)(2)(iv)(A) - ECCS Injection, 50.72(b)(2)(iv)(B) - RPS Actuation - Critical, 50.72(b)(3)(iv)(A) - Valid Specific System Actuation (reference EN#54012). The root cause of this event was brittle fracture of a condensate demineralizer in-line air filter bowl due to heat related age degradation. This event was of very low safety significance and had no impact on public health or safety. There were no systems, structures, or components inoperable at the time of the event and none that contributed to the event. This event is reportable pursuant to 10 CFR 50.73(a)(2)(iv)(A). In addition to the event that occurred on April 20, 2019, this LER is reporting a related event that occurred on April 21, 2019 that resulted in an invalid Primary Containment Isolation System. There were no radiological releases associated with either of these event.
3332019001 | FitzPatrick | 01/16/2019 | 03/15/2019 | ML19074A29 | <strong>Secondary Containment Differential Pressure Exceeded the Technical Specification Surveillance Requirement</strong><br /><i>Abstract:&nbsp;</i>On January 16, 2019, at 0137, with James A. FitzPatrick Nuclear Power Plant at 100% power, Secondary Containment differential pressure exceeded the Technical Specification Surveillance Requirement 3.6.3.1.1 of greater than or equal to 0.25 inches of vacuum water gauge while isolating Reactor Building Ventilation. This condition existed for approximately ten (10) seconds and returned to within limits when the isolation sequence was completed. <br /><br /> The differential pressure did not exceed 0 so there was no unmonitored exfiltration and there were no actual radiological release events. When Secondary Containment did not meet the Technical Specification requirement for differential pressure, Secondary Containment was Inoperable. Therefore, this event is reportable under 10 CFR 50.73(a)(2)(v)(C). <br /><br /> A differential pressure excursion during transition from normal to isolation mode of the Reactor Building Ventilation System is an expected condition, and attributable to the design of the system. The cause of exceeding the differential pressure requirement has been determined not to be associated with a component failure or equipment malfunction. Corrective actions include declaring Secondary Containment Inoperable when manually isolating Reactor Building Ventilation and increase the normal differential pressure in Secondary Containment.
3332019003 | FitzPatrick | 07/29/2019 | 09/20/2019 | ML19263B25 | <strong>Safety Relief Valves Out of Tolerance</strong><br /><i>Abstract:&nbsp;</i>The As-Found test results for the eleven Safety/Relief Valve (S/RV) pilot assemblies removed and replaced during the 2018 Refueling Outage at James A. FitzPatrick Nuclear Power Plant (JAF) identified eight (8) S/RV pilot assemblies that lifted outside of the allowable tolerance required by Technical Specification Surveillance Requirement 3.4.3.1. Eight (8) two-stage S/RV’s were found out of tolerance high. The eight S/RV pilot assemblies are assumed to have been inoperable at some point in the operating cycle that preceded the 2017 Refueling Outage resulting in a condition reportable pursuant to 10 CFR 50.73(a)(2)(i)(B). <br /><br /> The S/RV design features an electric actuation capability that provides a diversified means of opening the S/RV’s despite the out of tolerance condition. However, the electric lift function is considered a backup to the mechanical S/RV’s and is not credited in the accident analysis. Therefore, the TS inoperability of the eight (8) S/RV’s also resulted in a condition reportable pursuant to 10 CFR50.73(a)(2)(v)(D). <br /><br /> The cause of the two-stage failures has been identified as corrosion bonding. The safety consequences associated with this event are considered low due to the electric actuation capability.
3342019001 | Beaver Valley 1 | 11/02/2019 | 12/30/2019 | ML20003D85 | <strong>Low Head Safety Injection Discharge Relief Valve Did Not Reseat During Surveillance Test</strong><br /><i>Abstract:&nbsp;</i>On November 2, 2019, during the Unit 1 twenty-sixth refueling outage (1R26), while performing a surveillance test on the `A' Low Head Safety Injection (LHSI) Pump, the 'A' LHSI discharge relief valve lifted and did not reseat, resulting in approximately 850 gallons of Emergency Core Cooling System water from the Refueling Water Storage Tank (RWST) being discharged to the local area sump. At 1515 hours, the RWST was declared Inoperable due to low level. The 'A' LHSI discharge relief valve was isolated to prevent further leakage, and makeup to the RWST was commenced. At 1602 hours, the RWST was declared Operable. The cause was that personnel did not implement actions intended to ensure that the guide ring settings for spare Crosby relief valves were verified, validated, and corrected, resulting in the valve being installed during 1R26 with its guide ring likely improperly set. <br /><br /> Engineering analysis determined that the postulated design basis Large Break Loss of Coolant Accident would exceed regulatory limits and the projected dose would exceed the Exclusion Area Boundary dose limit, and the General Design Criteria 19 for control room dose limit. The safety significance of the relief valve lifting was very low. This event is reportable per 10 CFR 50.73(a)(2)(ii)(B) and 10 CFR 50.73(a)(2)(v)(B), (C), (D) as reported by Event Notification 54366 on November 2, 2019 at 2303 hours.
3342019002 | Beaver Valley 1 | 11/04/2019 | 12/30/2019 | ML20003D85 | <strong>Manual Reactor Trip at 15% Power due to Lifting of the 1A Main Steam Safety Valve</strong><br /><i>Abstract:&nbsp;</i>On November 4, 2019, at 0535 Eastern Standard Time, the Beaver Valley Power Station Unit 1 reactor was manually tripped at approximately 15% reactor power due to secondary system perturbations that caused the 1A Main Steam Safety Valve (MSSV) to lift. The 1A MSSV opened, instead of the expected opening of the 1A Atmospheric Dump Valve (ADV), as the tolerance range for ADV pressure switch overlapped the tolerance range for 1A MSSV. The 1A MSSV closed just prior to the trip. <br /><br /> The Reactor Trip was without complications. All control rods fully inserted into the core. The plant was stabilized in Mode 3 with normal Main Feedwater System in service. <br /><br /> The reason for the MSSV opening prior to the 1A ADV opening was due to the as-left setpoint of the 1A ADV pressure switch during its calibration in the prior refueling outage. The setpoint drifted high and was found to be above the opening setpoint of the MSSV.<br /><br /> The pressure switch input to the 1A ADV was adjusted to within the tolerance band prior to reactor startup. An Engineering Evaluation established new setpoint and reset values for the three ADVs. <br /><br /> This event was reported per Event Notification 54369 as an actuation of the Reactor Protection System per 10 CFR 50.72(b)(2)(iv)(B). <br /><br /> This event is being reported pursuant to 10 CFR 50.73(a)(2)(iv)(A) as a condition that resulted in the manual actuation of the Reactor Protection System.
3352019001 | St. Lucie 1 | 04/25/2019 | 10/01/2019 | ML19274B73 | <strong>Automatic Reactor Trip Caused by Main Generator Ground Resulting in Generator Lockout/Loss of Load</strong><br /><i>Abstract:&nbsp;</i>On April 25, 2019, St. Lucie was in Mode 1 at 100 percent reactor power. At 0918 hours the reactor tripped due to a generator lockout during reactive power lagging capability testing. The trip was uncomplicated and all safety systems responded as designed. The plant was stabilized in Mode 3 with decay heat removal via the main feedwater system and condenser steam bypass system. <br /><br /> The direct cause of the generator lockout was attributed to a localized breach in the ground wall insulation of stator bar B17. The quarantined equipment was tested at the original equipment manufacturer (OEM) testing facility. The causal analysis could not establish a root cause for the defect. <br /><br /> The generator repairs and post maintenance testing were successfully completed. <br /><br /> Automatic reactor trips are analyzed events in the Updated Final Safety Analysis Report (UFSAR). The trip and post trip actions were uncomplicated. Therefore, this event had no impact on the health and safety of the public.
3352019002 | St. Lucie 1 | 09/07/2019 | 11/05/2019 | ML19309E53 | <strong>Reactor Coolant Pump Motor Ground Results in Reactor Coolant Pump Trip and Subsequent Automatic Reactor Trip</strong><br /><i>Abstract:&nbsp;</i>On September 7, 2019, St. Lucie was in Mode 1 at 100 percent reactor power. At 0824 the Unit 1 Reactor tripped automatically on a low Reactor Coolant System flow actuation of the Reactor Protection System. The trip was uncomplicated and all safety systems responded as designed. The plant was stabilized in Mode 3 with decay heat removal via the main feedwater system and condenser steam bypass system.<br /><br /> The direct cause was an electrical fault in the 1A1 Reactor Coolant Pump (RCP) motor. The electrical fault was initiated after a cooling water pipe for the 1A1 RCP motor's upper bearing failed and the leaking water entered the motor enclosure. The root cause evaluation determined there were inadequate technical controls over the use of generic reuse specifications and engineering quality instructions during a 2010 modification of RCP motor cooling water piping. <br /><br /> The 1A1 RCP motor was replaced, and post maintenance testing was successfully completed. St. Lucie Unit 1 was returned to service on September 21, 2019. <br /><br /> Automatic reactor trips are analyzed events in the Updated Final Safety Analysis Report (UFSAR). The trip and post trip actions were uncomplicated. Therefore, this event had no impact on the health and safety of the public.
3352019003 | St. Lucie 1 | 08/30/2019 | 10/28/2019 | ML19301D25 | <strong>Inoperability of Emergency Diesel Generator due to Cracked Crankshaft</strong><br /><i>Abstract:&nbsp;</i>On July 15, 2019, St. Lucie Unit 1 was in Mode 1 at 100 percent reactor power. At 0839 hours, the 1B Emergency Diesel Generator (EDG) was started for the monthly 1 hour loaded-run surveillance. At 0919 hours, the 1B EDG tripped due to high jacket water temperature. The subsequent investigation revealed that the 1B2 radiator fan on the 1B EDG was not rotating and that the 1B2 EDG crankshaft for the radiator fan was sheared. <br /><br /> Repairs were made, and the 1B EDG was returned to service on July 28, 2019 at 1717 hours. The forensic investigation of the shaft and the root cause report for the failure were finalized on August 30, starting the 60-day reportability clock for this report. These reports provided evidence that the 1B2 EDG was inoperable for a time longer than permitted by the Technical Specifications. <br /><br /> Metallurgy determined that the crankshaft tapered end failure was caused by fatigue. <br /><br /> Based on the diverse methods for supplying electric power at the site, this condition had no major impact on the health and safety of the public.
3362019001 | Millstone 2 | 12/27/2019 | 02/19/2020 | ML20050D67 | <strong>Manual Reactor Trip due to Loss of the 'A' Steam Generator Feed Pump</strong><br /><i>Abstract:&nbsp;</i>On December 27, 2019 at 0704 while operating in MODE 1 at 100 percent power, operators manually tripped the Millstone Power Station Unit 2 (MPS2) reactor due to lowering steam generator levels caused by a loss of flow from the 'A' Steam Generator Feed Pump (SGFP). <br /><br /> The direct cause was the failure of the coupling connecting the MPS2 'A' Steam Generator Feed Pump (M2P1A) to the Steam Generator Feed Pump Turbine (M2H-5A). <br /><br /> The failed 'A' SGFP coupling was replaced and MPS2 was returned to service. <br /><br /> The actuation of Reactor Protection System (RPS) and Auxiliary Feedwater System (AFW) is being reported in accordance with 10 CFR 50.73(a)(2)(iv)(A) as an event that resulted in a manual or automatic actuation of systems listed in 10 CFR 50. 73(a)(2)(iv)(B).
3392019001 | North Anna 2 | 03/02/2019 | 04/26/2019 | ML19123A09 | <strong>Manual Reactor Trip on Degrading Condenser Vacuum due to a Failed Weld</strong><br /><i>Abstract:&nbsp;</i>On March 2, 2019 North Anna Unit 2 Operations personnel were lowering reactor power in preparation for a scheduled refueling outage. Condenser vacuum began to degrade and personnel entered the Abnormal Operating Procedure for Low Condenser Vacuum. The reactor was manually tripped at approximately 12% power. The Operations crew entered the reactor trip procedure and stabilized the Unit in Mode 3 at normal operating pressure and temperature. The manual reactor trip was not complicated and shift personnel responded appropriately. After the trip, decay heat was removed by the Steam Generator Pressure Operated Relief Valves and Unit 2 was cooled down to support a scheduled refueling outage. <br /><br /> The direct cause of the degrading condenser vacuum was a failed socket weld downstream of a High Pressure Turbine Main Steam Supply Header Drain Valve on the condenser (steam) side.<br /><br /> A 4-hour report per 10CFR50.72(b)(2)(iv)(B) at 0013 hours on March 3, 2019 was made for a manual actuation of the reactor protection system. <br /><br /> The reactor trip is reportable per 10CFR50.73(a)(2)(iv)(A) for a manual actuation of the reactor protection system.
3412019001 | Fermi 2 | 01/01/2019 | 03/01/2019 | ML19060A29 | <strong>Unplanned Loss of Safety Function of Gland Seal Exhauster Trip During Planned Maintenance due to Inadequate Procedure</strong><br /><i>Abstract:&nbsp;</i>On 1/1/2019, while performing planned maintenance on the Feedwater Distributed Control System (FW DCS) at 5 percent power, it was discovered that the automatic trip instrumentation of the Gland Seal Exhauster (GSE) was inoperable. The automatic GSE trip function is a documented assumption in the safety analysis for the Control Rod Drop Accident and is required by Technical Specification (TS) 3.3.7.3 when reactor thermal power is less than or equal to 10 percent. The automatic trip function of the GSE was inoperable for 1 minute 19 seconds. <br /><br /> The impact on the GSE trip function during implementation of the site procedures and the applicable work order was inadequately documented prior to starting the planned maintenance on the FW DCS. The unplanned inoperability of the GSE trip function is reportable under 10 CFR 50.73(a)(2)(v)(C) and (D). There was no adverse impact to public health and safety or to plant employees and there were no radiological releases. <br /><br /> The cause of the GSE trip inoperability resulted from inadequate procedural guidance during planned maintenance on the FW DCS. GSE trip operability was restored automatically by FW DCS without any required actions. Site procedures were revised on or before January 11, 2019 to describe the impact of the FW DCS on the GSE trip and reference the applicable TS.
3412019002 | Fermi 2 | 02/19/2019 | 04/22/2019 | ML19112A33 | <strong>Secondary Containment Airlock Doors Opened at the Same Time Resulting in a Condition Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On February 19, 2019, at 1307 EST, with the reactor at 100 percent Core Thermal Power and steady state conditions, plant personnel notified the Main Control Room that both doors in the Secondary Containment Airlock on the Reactor Building Fifth Floor were opened and could not close. The Airlock Doors were opened simultaneously for a period of approximately five minutes (i.e., from 1253 to 1258 EST). A technician had opened both air lock doors simultaneously when he egressed through first door and grabbed the handle of the second airlock door and inadvertently pushed the door open before the opposing door had closed. The interlock device for the doors .had failed. The interlock is designed to prevent both doors from being opened simultaneously. Technical Specification (TS) Surveillance Requirement (SR) 3.6.4.1.3 was not met. The maximum Secondary Containment (SC) pressure observed during that time remained within TS limits. There were no radiological releases associated with this event. Declaring SC inoperable as a result of not meeting TS SR 3.6.4.1.3 is reportable under 10CFR50.72(b)(3)(v)(C) and this written report is required under 10CFR50.73(a)(2)(v)(C) as an event or condition that could have prevented the fulfillment of a safety function needed to control the release of radioactive material. The doors were closed in approximately 5 minutes and SC was restored.
3412019003 | Fermi 2 | 05/29/2019 | 07/26/2019 | ML19210B83 | <strong>Secondary Containment Declared Inoperable due to Opening Both Airlock Doors</strong><br /><i>Abstract:&nbsp;</i>On May 29, 2019 at 2210 hours, during Security Force on Force Practice Drills both doors in the Secondary Containment (SC) air lock on the reactor building first floor were opened simultaneously for a period of approximately two seconds. During the drill exercise, the Controller failed to maintain the access control measures at the outer air lock door which resulted in additional drill personnel accessing through the door. <br /><br /> The condition resulted in Technical Specification (TS) Surveillance Requirement (SR) 3.6.4.1.3 not being met. The doors were secured immediately. SC pressure during that time remained unchanged and within TS limits. There were no radiological releases associated with this event. Declaring Secondary Containment inoperable for not meeting TS SR 3.6.4.1.3 is reportable under 10 CFR 50.72(b)(3)(v)(C). This written report is required under 10 CFR 50.73(a)(2)(v)(C) as an event or condition that could have prevented the fulfillment of a safety function needed to control the release of radioactive material.
3412019004 | Fermi 2 | 07/30/2019 | 09/30/2019 | ML19273A05 | <strong>Division 2 Mechanical Draft Cooling Tower Fan "D" Tripped When Placed in High Speed due to a Blown Fuse</strong><br /><i>Abstract:&nbsp;</i>On July 30, 2019, at 1014 EDT, the Division 2 Mechanical Draft Cooling Tower (MDCT) Fan "D" was declared inoperable due to a trip of the fan while placing it in high speed The MDCT Fans are required to support operability of the Ultimate Heat Sink (UHS). The UHS is required to support operability of the Division 2 Emergency Equipment Cooling Water (EECW) system. The EECW system cools various safety related components, including the High Pressure Coolant Injection (HPCI) system room cooler. An unplanned HPCI inoperability occurred based on a loss of the HPCI Room Cooler. The cause of the event was a blown high speed breaker control power fuse.<br /><br /> The control power fuse was replaced, the MDCT Fan "D" was tested satisfactorily, and HPCI was declared operable on July 30 at 1431 EDT. The blown fuse was quarantined and will be sent for failure analysis. The remaining fuses in the system are being replaced and sent to the vendor for comparison with the blown fuse.
3412019005 | Fermi 2 | 09/29/2019 | 11/22/2019 | ML19329C82 | <strong>Secondary Containment Pressure Exceeded Technical Specification due to Reactor Building HVAC Damper Malfunction</strong><br /><i>Abstract:&nbsp;</i>On September 29, 2019, at 2228 EDT, a planned train swap of the Reactor Building Heating Ventilation and Air Conditioning (RBHVAC) system resulted in the Technical Specification (TS) for secondary containment (SC) pressure boundary not being met for approximately 2 minutes and 15 seconds. The maximum secondary containment pressure recorded during that time was approximately 0.1 inches of water gauge (positive). Secondary containment pressure was restored to within TS limits by restarting the West RBHVAC train. There were no safety consequences or radiological releases associated with this event. The cause of this momentary loss of SC was determined to be the effect of the RBHVAC West exhaust fan discharge damper failing to close due to sticking of a time delay relay. For corrective actions, Fermi 2 will replace the relay and has temporarily modified the RBHVAC swap sequence until the relay has been replaced.
3412019006 | Fermi 2 | 12/18/2019 | 02/14/2020 | ML20045E36 | <strong>Secondary Containment Pressure Exceeded Technical Specification due to Reactor Building HVAC Damper Malfunction</strong><br /><i>Abstract:&nbsp;</i>On December 18, 2019, at 0908 EST, with the East and Center Reactor Building Heating Ventilation and Air Conditioning (RBHVAC) trains in service, secondary containment (SC) pressure degraded to the point where the Technical Specification (TS) for SC pressure was exceeded for approximately 4 minutes. The maximum SC pressure recorded during that time was 0.064 inches of vacuum water gauge. SC pressure was restored to within TS limits by manually starting the Division 1 Standby Gas Treatment System. There were no safety consequences or radiological releases associated with this event. The cause of this momentary loss of SC TS requirements was determined to be a failure in the Center RBHVAC exhaust fan inlet damper positioner. For corrective actions, Fermi 2 has upgraded two of the three RBHVAC exhaust inlet damper positioners and scheduled an upgrade replacement of the third.
3462019001 | Davis-Besse | 06/21/2019 | 10/07/2019 | ML19282A38 | <strong>Emergency Ventilation System Train Inoperable due to Non-specific Test Description of Damper Operation</strong><br /><i>Abstract:&nbsp;</i>On July 19, 2019, with the Davis-Besse Nuclear Power Station operating at approximately 100 percent power, during a scheduled monthly Surveillance Test it was identified Emergency Ventilation System (EVS) Fan 1 failed to produce the desired negative pressure within the Shield Building Negative Pressure area because the recirculation and exhaust dampers were not modulating as required. The degraded differential pressure controller, caused by a premature failure of the controller, was replaced to restore EVS Train 1 Operability A review of the previous month's Surveillance Test performed on June 21, 2019, showed similar results were obtained, but it was not recognized at that time the dampers were not operating properly. It was determined that EVS Train 1 was inoperable for a 30-day period, which resulted in the plant operating in a condition prohibited by the Technical Specifications. The cause of the degraded controller not being' identified during the previous month's test was a lack of specific description of damper operation in the monthly Surveillance Test, and the tests for both EVS Trains have been revised to specify the expected/ required damper positions and to clarify the test acceptance criteria. <br /><br /> This issue is being reported in accordance with 10 CFR 50.73(a)(2)(i)(B).
3462019002 | Davis-Besse | 08/19/2019 | 10/18/2019 | ML19295F43 | <strong>Auxiliary Feedwater Trains Inoperable due to Loss of Train Separation from Door Being Left Open</strong><br /><i>Abstract:&nbsp;</i>On August 19, 2019, with the Davis-Besse Nuclear Power Station operating in Mode 1 at approximately 100 percent power, the door separating the two Auxiliary Feedwater (AFW) Pump Rooms was left open for approximately 75 minutes during scheduled work on AFW Train 1 piping. The watertight door, which serves as a Fire, Flood, Tornado, Security, and High Energy Line Break barrier, was closed upon discovery by a plant operator performing rounds. With the door open and unattended, both AFW trains were inoperable due to the loss of train separation.<br /><br /> The cause of the door being left open and unattended was worker inattention to door signage, resulting in nonadherence to door usage requirements. Contributing to the event was less than adequate monitoring of the door by Site Protection in accordance with procedures. Corrective actions included coaching of the workers on the importance of maintaining vital area doors, communication on door design, functions and usage with site employees, discussion on lessons learned from the event, and incorporation of additional guidance in Site Protection procedures. <br /><br /> This event is being reported pursuant with 10 CFR 50.73(a)(2)(v)(B) and 10 CFR 50.73(a)(2)(vii)(B).
3462019003 | Davis-Besse | 09/07/2019 | 11/06/2019 | ML19312A07 | <strong>Anticipatory Reactor Trip System Actuated During Turbine Stop Valve Testing due to the Closure of a Main Turbine Stop Valve</strong><br /><i>Abstract:&nbsp;</i>On September 7, 2019, with the Davis-Besse Nuclear Power Station operating at approximately 95 percent power, during scheduled Main Turbine Stop Valve 2 (MSV) testing, Main Turbine Stop Valve 4 unexpectedly stroked closed and Anticipatory Reactor Trip System (ARTS) actuated, tripping the reactor. <br /><br /> The most likely cause of the MSV 4 closure was mechanical binding / sticking or foreign material in the internals of the valve operating system (fast acting solenoid valve) causing its inadvertent actuation. <br /><br /> Actions taken include replacing and testing the MSV 4 fast acting solenoid valve and testing ARTS. Scheduled actions include replacing similar components on the other MSVs, and cleaning the EHC fluid sump, replacing the EHC fluid and particulate strainers. <br /><br /> This issue is being reported in accordance with 10 CFR 50.73(a)(2)(iv)(A).
3482019001 | Farley 1 | 10/11/2019 | 12/09/2019 | ML19343B09 | <strong>Pressurizer Safety Valve Lift Pressure Outside of Technical Specifications Limits due to Setpoint Drift</strong><br /><i>Abstract:&nbsp;</i>On October 11, 2019, while at 0% power level and defueled, it was discovered that a Unit 1 pressurizer safety valve (PSV), which had been removed during the October 2019 refueling outage (1R29) and shipped off-site for testing, failed its as-found lift pressure test. The PSV lifted below the Technical Specification (TS) 3.4.10 allowable lift setting value. Setpoint drift is the cause of the PSV failure.<br /><br /> It is likely that the PSV was outside of the TS limits longer than the allowable completion times for the associated Required Action Statements during the previous operating cycle in all applicable modes of operation. Therefore, this condition is being reported in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by TS. <br /><br /> The PSV was replaced during the October 2019 refueling outage.
3522019001 | Limerick 1 | 08/27/2019 | 10/24/2019 | ML19297D39 | <strong>Multiple Trains of RHRSW Inoperable for Greater than Time Allowed by Technical Specifications due to Pipe Corrosion</strong><br /><i>Abstract:&nbsp;</i>On 7/11/19 a pin hole leak was identified on the 18-inch distribution piping of the C Spray Network while the spray network was in operation for Spray Pond cooling. Subsequent NDE inspections identified wall thinning over a large arc of the piping's circumference; approximately 34 feet of piping required replacement. On 08/25/19, the extent of condition inspection of the A Spray Network identified similar corrosion damage. The condition was determined to be reportable for a condition prohibited by Technical Specifications and a common cause inoperability of independent trains. All four Spray Networks were inspected, and corrosion damage was identified on all four of the Spray Networks' 18-inch distribution piping.<br /><br /> Although the 18-inch spray network distribution piping was degraded, the spray networks and the ultimate heat sink were determined to be functional. The cause of the pipe corrosion damage observed on the 18-inch distribution piping of each spray pond spray network was flow-induced film removal accompanied by high humidity electrochemical atmospheric corrosion. This condition was not identified prior to the piping becoming inoperable because there was a lack of understanding of this potential failure mechanism. The affected piping was replaced and an NDE inspection and proactive pipe replacement strategy will be established to ensure long term reliability of the above ground spray pond spray network piping.
3532019001 | Limerick 2 | 06/04/2019 | 08/05/2019 | ML19217A28 | <strong>Valid Actuation of the Reactor Protection System due to a Trip of D214-24 Load Center</strong><br /><i>Abstract:&nbsp;</i>On June 3, 2019, with Limerick Unit 2 at approximately 100% power, the D214-24 Load Center tripped due to an invalid undervoltage signal; resulting in de-energization of a 480 VAC Divisional Motor Control Center (MCC) D214-G-D. The power failure impacted several components in the Offgas System resulting in water building up in the system and causing stalling of the Steam Jet Air Ejectors and a resultant degradation of Main Condenser vacuum. At 01:45 June 4, Operators inserted a manual SCRAM due to Main Condenser vacuum approaching the Main Turbine trip setpoint. The cause of the event is the procedure used to stabilize the plant did not fully address the loss of power to the Offgas System. The corrective action is to revise the procedures used to stabilize the plant to address the loss of power to the Offgas System.
3532019002 | Limerick 2 | 07/22/2019 | 09/20/2019 | ML19263A64 | <strong>Emergency Diesel Generator Lube Oil Pressure Sensing Line Leak Resulting in a Condition Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On 7/22/19, the instrumentation line threaded pipe connection for a pressure indicator, was found sheared during Emergency Diesel Generator (EDG) D24 slow start monthly run. The one-quarter inch instrumentation line threaded connection tees off the four-inch main lube oil piping near the discharge of the engine driven lube oil pump. Prior to the run there was no indication of a leak at this connection. This threaded pipe was pro-actively replaced on 5/23/18, and on 1/21/19 the threaded pipe connection failed due to high-cyclic fatigue. The corrective actions to address the failure on 1/21/19 were to install a support on the threaded connection and repair a broken U-bolt. These actions did not resolve the underlying condition. The cause of the failure on 7/22/19 was high-cyclic fatigue experienced at the threaded pipe connection. The corrective action is to redesign the connection to reduce the stress on the threaded pipe connection. In the interim, the instrument line was removed from service.
3542019001 | Hope Creek | 08/03/2019 | 10/02/2019 | ML19274D12 | <strong>Manual Scram and Manual Actuation of Reactor Core Isolation Cooling</strong><br /><i>Abstract:&nbsp;</i>At 1906 EDT on August 3 2019, while in OPCON 1 at 93.8 percent power, operators identified degrading main condenser vacuum and commenced reducing power. Degrading vacuum was due to the circulating water cooling tower bypass valve failing open At 1947, the reactor was manually scrammed from 37 percent due to loss of condenser vacuum. Reactor feedwater pumps (RFP) tripped when reactor pressure vessel (RPV) water level rose to level 8 (+54 inches) because the reactor feedwater startup level control valve (SULCV) failed open Operators initiated the reactor core isolation cooling (RCIC) system, recovered a RFP and secured RCIC after establishing control of RPV water level The failed equipment was replaced. <br /><br /> This event is reportable per 10 CFR 50 73(a)(2)(iv)(A).
3542019002 | Hope Creek | 11/07/2019 | 01/06/2020 | ML20006E54 | <strong>Safety Relief Valve (SRV) As-found Set-point Failures</strong><br /><i>Abstract:&nbsp;</i>On November 08, 2019, Hope Creek Generating Station (HCGS) received results that the second 'as-found' set-point test for safety relief valve (SRV) pilot stage assemblies had exceeded the lift setting tolerance prescribed in Technical Specification (TS) 3.4.2.1. The TS requires the SRV lift settings to be within +/-3% of the nominal set-point value. <br /><br /> During the twenty-second refueling outage (H1R22), all fourteen SRV pilot stage assemblies were tested at an offsite facility. Between October 22 and November 25, 2019, HCGS received the test results for all fourteen of the SRV pilot valve assemblies. A total of six of the fourteen SRV pilot stage assemblies were outside of the TS 3.4.2.1 specified values. All of the valves failing to meet the limits were Target Rock Model 7567F two-stage SRVs. <br /><br /> Exceeding the set points for five of the six SRV pilot stage assemblies is attributed to corrosion bonding between the pilot discs and seating surfaces, which is consistent with industry experience. The cause of exceeding the sixth SRV set-point was pilot failure or spindle/disc contact wear.
3642019001 | Farley 2 | 04/12/2019 | 06/10/2019 | ML19161A20 | <strong>Inoperable Containment Isolation Valve due to Design Control Error</strong><br /><i>Abstract:&nbsp;</i>On April 12, 2019, with Farley Nuclear Plant (FNP) Unit 2 in Mode 6 (refueling) it was determined through surveillance testing that Containment Isolation Valve (CIV) Q2P16MOV3131 (MOV-3131), Service Water (SW) From Reactor Coolant Pump (RCP) Air Cooler would not close on a simulated Safety Injection (SI) Signal. Following troubleshooting it was identified on April 24, 2019 (Mode 6) that MOV-3131 was incorrectly wired. An omission error completed in a previous design change (October 2017) created a wiring discrepancy that prevented MOV-3131 from closing on an SI signal. This condition is being reported pursuant to the requirements of 10 CFR50.73(a)(2)(i)(B) as an operation prohibited by the Technical Specifications for the inoperable containment isolation valve.<br /><br /> The wiring discrepancy was caused by an engineering human performance error during issuance of a design change. The circuit wiring was corrected, post-maintenance testing was completed satisfactorily, and the valve was returned to service.
3642019002 | Farley 2 | 05/01/2019 | 06/27/2019 | ML19178A23 | <strong>Manual Reactor Trip due to Misaligned Rod during Low Power Physics Testing</strong><br /><i>Abstract:&nbsp;</i>At 16:43 CDT on May 1, 2019. with Farley Nuclear Plant (FNP) Unit 2 in Mode 2 with power in the Intermediate Range the reactor was manually tripped. Operators manually tripped the reactor during Low Power Physics Testing due to a misaligned rod. The trip was not complex with all systems responding normally. Operations stabilized the plant in Mode 3. Decay heat was removed by the Steam Generator Atmospheric Relief Valves due to Main Steam Isolation Valves being closed during Low Power Physics Testing. <br /><br /> This event is reportable under 10CFR50.73(a)(2)(iv)(A) due to manual actuation of systems listed in 10CFR50.73(a)(2)(iv)(B). FNP Unit 1 was not affected during this event. <br /><br /> Corrective Actions included resistance readings in the power cabinet and inspecting local connectors on the reactor head. Additionally, multiple control rod bank withdrawals and insertions were performed while collecting system operating data. No abnormal conditions were identified, and crud is the suspected reason for the misalignment.
3642019003 | Farley 2 | 09/21/2019 | 11/12/2019 | ML19316C57 | <strong>Manual Reactor Trip due to 2C Reactor Coolant Pump High Vibration Indication</strong><br /><i>Abstract:&nbsp;</i>On September 21, 2019, at 0744 CDT, while operating at 100% power, Farley Nuclear Plant (FNP) Unit 2 received a vibration alarm on the 2C Reactor Coolant Pump (RCP). Operators entered the applicable Annunciator Response Procedure (ARP). At 0800 CDT, the Control Room Operators manually tripped Unit 2 due to indicated vibrations on the 2C RCP exceeding procedural limits. The post-trip response was normal. All trains of Auxiliary Feed Water pumps actuated normally due to low Steam Generator (SG) levels post trip. Operators took appropriate action to stabilize the unit in Mode 3.<br /><br /> The investigation determined the most likely cause for the RCP vibration indication was the temporary in-phasing of the various contributing frequencies. The ARP contained insufficient information to allow the Control Room Operators to determine if the indications represented an actual vibration condition that threatened RCP operation. The Control Room Operators tripped the reactor based on available indications per the guidance of the ARP. Corrective Actions included revising the ARP to enhance the guidance for vibration conditions that require action to protect the RCP.<br /><br /> This event is reportable under 10CFR50.73(a)(2)(iv)(A) due to manual actuation of systems listed in 10CFR50.73(a)(2)(iv)(B). FNP Unit 1 was not affected during this event.
3662019001 | Hatch 2, Hatch 1 | 02/23/2019 | 04/23/2019 | ML19113A26 | <strong>Emergency Diesel Generator Valid Actuation Signal due to Inadvertent Electrical Bus De-Energization</strong><br /><i>Abstract:&nbsp;</i>At 0212 EST on February 23, 2019, with Unit 2 in MODE 5, an actuation signal for the 2C Emergency Diesel Generator (EDG) was received during the Loss of Coolant Accident / Loss of Offsite Power logic system functional test. The 2C EDG was running and tied onto the 2G 4160 Volt emergency bus when the alternate supply breaker was closed as required per the test procedure. Immediately upon closing the alternate supply breaker, both the alternate supply breaker and 2C EDG output breaker tripped open. Additionally, the power circuit breakers supplying power to the 10 Station Auxiliary Transformer (SAT) and 2C SAT also tripped open. This placed Unit 1, which was in MODE 1, into Required Action Statement 3.8.1.A for one required offsite circuit inoperable. The 2C EDG output breaker reclosed once the 2G 4160 Volt bus undervoltage relays sensed a deenergized bus. An 8-hour notification was made on February 23, 2019 (Event Notification No 53893) per 10 CFR 50 72(b)(3)(iv)(A) due to the valid actuation of an emergency AC electrical power system that was not part of a pre-planned sequence. <br /><br /> Subsequent investigation and analysis determined that the Potential Transformers and Current Transformers for 2C SAT had been wired incorrectly, which allowed the 2C EDG and 2C SAT to be paralleled out of phase. Corrective actions were taken to correct the wiring. Independent and concurrent verifications were immediately put in place for ongoing degraded grid electrical work.
3662019002 | Hatch 2 | 03/19/2019 | 05/16/2019 | ML19136A38 | <strong>High Pressure Coolant Injection System Inoperable Due to a Lack of Hydraulic Oil Pressure by the Auxiliary Oil Pump</strong><br /><i>Abstract:&nbsp;</i>At 0140 EST on March 19, 2019, while Unit 2 was at approximately 1 percent power in Mode 2, Operations declared the High Pressure Coolant Injection (HPCI) inoperable following a failed Operability test. During the test, the HPCI auxiliary oil pump failed to start when the control switch was taken to start. Due to the lack of hydraulic oil pressure provided by the auxiliary oil pump, the HPCI main stop valve did not open followed by the illumination of the HPCI turbine trip annunciator, thus preventing HPCI from starting and making it inoperable. An investigation was performed and found the secondary connection stabs on the Motor Control Center Pan Assembly feeding the auxiliary oil pump were not making adequate contact. The stab tension was adjusted and the oil pump was started followed by successful completion of the HPCI pump operability test. Because HPCI does not have a redundant system, the pump failure to start on demand represents a safety system functional failure as defined in NEI 99-02 and is reportable per 50 72(b)(3)(v)(D).
3662019003 | Hatch 2 | 03/24/2019 | 05/22/2019 | ML19142A35 | <strong>Manual Reactor Scram from 25 Percent Power Due to Loss of Condenser Vacuum</strong><br /><i>Abstract:&nbsp;</i>On March 24, 2019 at 0026, with Unit 2 in Mode 1 and ascending in power, Control Room Operators noticed the Main Condenser was losing vacuum and initiated a power reduction. Due to vacuum continuing to degrade, Operators lowered reactor power down to 25 percent and initiated a manual reactor SCRAM at 0159. Following the trip of the Main Turbine, the non-safety Station Service 4160V buses failed to fast bus transfer from normal to the alternate power supply resulting in the loss of all non-safety loads. Operators entered an abnormal operating procedure for the Loss of 4160V buses to manually re-energize the Station Service buses. The de-energized Station Service buses resulted in a loss of the Condensate Feedwater system. Reactor water level was then maintained by the Reactor Core Isolation Cooling system while pressure was controlled by High Pressure Coolant Injection. A primary containment isolation signal was received on low reactor water level. The event is reportable pursuant to 10 CFR50.73(a)(2)(iv)(A) for a manual reactor SCRAM and general containment isolation signal.<br /><br /> Corrective actions were taken to properly align the Steam Jet Air Ejector system, which was the cause of the loss of condenser vacuum, and to replace the failed relay, which caused the failure of the Station Service buses to transfer.
3662019004 | Hatch 2 | 08/22/2019 | 10/16/2019 | ML19289E22 | <strong>High Pressure Coolant Injection System Declared Inoperable due to Brief Loss of Power to HPCI Pump Flow Controller</strong><br /><i>Abstract:&nbsp;</i>On August 22, 2019 at 2234 EST with Unit 2 operating at 100% rated thermal power, the "High Pressure Coolant Injection (HPCI) system inverter circuit failure" alarm was received on a Main Control Room panel. This alarm indicates a loss of AC power from the HPCI inverter, and is caused by either a loss of DC power to, or a failure of, the inverter. Operating personnel immediately noticed the loss of indication on several digital recorders and on the HPCI flow controller. At 2235 EST, the "HPCI system inverter circuit failure" alarm cleared, and all referenced digital indications returned to normal. <br /><br /> Subsequent investigation into the HPCI inverter circuit failure revealed a failed ceramic capacitor in the HPCI turbine speed control power supply. The failed capacitor caused a short-circuit condition that momentarily drew power down on the HPCI inverter. This caused a momentary loss of indication to the referenced digital recorders and a momentary loss of power to the HPCI flow controller. In the event of a valid HPCI initiation signal, the momentary loss of power to the HPCI flow controller would have resulted in a loss of HPCI function. Operations personnel therefore declared HPCI inoperable at 2234 EST. <br /><br /> The cause of the capacitor failure was not determined. Ceramic capacitors of this type are not known to fail at a specified frequency and are not recommended for replacement on a periodic basis. The HPCI turbine speed control power supply was subsequently removed from service, replaced, and the new power supply tested satisfactorily.
3682019001 | Arkansas 2 | 05/26/2019 | 07/23/2019 | ML19204A31 | <strong>Reactor Trip due to a Reactor Coolant Pump Motor Failure</strong><br /><i>Abstract:&nbsp;</i>On May 26, 2019, the Arkansas Nuclear One, Unit 2 (ANO-2), reactor automatically tripped due to a fault and subsequent trip of Reactor Coolant Pump (RCP) 2P-32B. <br /><br /> The direct cause of the event was determined to be the loss of stator core compression coupled with broken compression finger welds allowing a finger to migrate into contact with the RCP rotor. The broken finger plate section damaged the stator insulation resulting in a short to ground. <br /><br /> The plant transient led to an automatic reactor trip due to a Plant Protection System actuation. After the reactor trip, the unit was stabilized in Mode 3 with Emergency Feedwater (EFW) initially being used to maintain plant temperature under automatic control.
3692019001 | McGuire 1 | 05/03/2019 | 07/01/2019 | ML19183A17 | <strong>Valid Actuation of the Unit 1 Reactor Protection System and Auxiliary Feedwater System</strong><br /><i>Abstract:&nbsp;</i>At 1554 [EST] hours on May 3, 2019, with Unit 1 in Mode 1 at approximately 100 percent power, the reactor automatically tripped on Over Temperature Delta Teniperature following a pressure transient in the Reactor Coolant System. The trip was uncomplicated with all systems responding normally post-trip. Operations manually started the motor driven auxiliary feedwater pumps.<br /><br /> The cause was determined to be: The Control Room Supervisor and Reactor Operators involved failed to adhere to established administrative standards. <br /><br /> The Control Room Supervisor and Reactor Operators involved failed to perform the correct level of pre-job brief in accordance with administrative standards. Adherence to the administrative standards would have ensured proper consideration of human factors and contingency actions prior to performing manual manipulations of the pressurizer pressure master controller. The licensed operators involved were removed from duty and are being remediated.<br /><br /> Planned Action: Complete remediation of the licensed operators.
3732019001 | LaSalle 1 | 11/16/2018 | 01/15/2019 | ML19015A10 | <strong>Turbine Stop Valve Limit Switch Failure due to Lubricant Degradation</strong><br /><i>Abstract:&nbsp;</i>During quarterly surveillances of turbine stop valve (TSV) limit switch number 3 (1C71-N006C), the component exhibited degraded performance on May 20, 2018 and a failure on September 9, 2018. The component was replaced and sent offsite for component testing and failure analysis. The component failure analysis completed on November 16, 2018 determined the cause was attributed to degradation of the switch lubricant due to exposure from a high temperature environment, which established firm evidence that the sluggish performance exhibited in May 2018 was related to the failure in September 2018 and that a past inoperability condition existed.<br /><br /> The component 1C71-N006C is the TSV-3 Closure RPS channel A2 scram limit switch. This device is required by technical specifications to support LCO 3.3.1.1 function 8 (RPS) and LCO 3.3.4.1 (EOC-RPT). Each TSV position is monitored by two limit switches (for TSV-3, A2 and B1 channels). This condition results in the TSV-3 input to RPS A2 as well as one channel of the EOC-RPT trip being INOPERABLE. The appropriate LCO Conditions and Required Actions were entered and tracked. The RPS and EOC-RPT functions were maintained due to the redundant channels remaining OPERABLE. There were no reportability thresholds applicable to this issue at the time of the event, and there was no loss of safety function. The condition is reportable in accordance with 10 CFR 50.73(a)(2)(i)(B) for operation or condition prohibited by Technical Specifications.<br /><br /> Immediate corrective actions were taken to replace the component and restore the associated channel to OPERABLE. Additional actions included performance of a causal investigation, identification of a new limit switch model that has greater heat tolerance, with a component replacement schedule starting in 2019.
3732019002 | LaSalle 1 | 05/03/2019 | 06/27/2019 | ML19178A20 | <strong>Turbine Stop Valve Limit Switch Failure due to Insufficient Lubrication</strong><br /><i>Abstract:&nbsp;</i>On March 23, 2019, during quarterly scram functional surveillances of turbine stop valves (TSV), the limit switch associated with TSV number 3 failed to return to shelf state when the lever arm was released. The failed component was replaced and sent offsite for component testing and failure analysis. The component failure analysis completed on May 3, 2019 determined the cause was attributed to insufficient lubrication in the shaft to bushing section of the limit switch. This established firm evidence that the failure mechanism and past inoperability condition may have existed since its last successful surveillance on December 15, 2018.<br /><br /> The affected component 1C71-N006C is the TSV-3 Closure RPS channel A2 scram limit switch. This device is required by Technical Specifications to support LCO 3.3.1.1 function 8 (RPS) and LCO 3.3.4.1 (EOC-RPT). Each TSV position is monitored by two limit switches (for TSV-3, A2 and B1 channels). This condition resulted in the TSV-3 input to RPS A2 as well as one channel of the EOC-RPT trip being INOPERABLE. The appropriate LCO Conditions and Required Actions were entered and tracked. The RPS and EOC-RPT functions were maintained due to the redundant channels remaining OPERABLE. There were no reportability thresholds applicable to this issue at the time of the event, and there was no loss of safety function. The condition is reportable in accordance with 10 CFR 50.73(a)(2)(i)(B) for operation or condition prohibited by Technical Specifications.<br /><br /> Immediate corrective actions were taken to replace the component and restore the associated channel to OPERABLE. Additional actions included performance of a component failure analysis and to complete scheduled limit switch replacements of the current model with a new limit switch model that has greater heat tolerance.
3742019001 | LaSalle 2, LaSalle 1 | 02/28/2019 | 04/29/2019 | ML19119A23 | <strong>Safety Related Electrical Bus Undervoltage Results in Valid Actuation of the Common Emergency Diesel Generator</strong><br /><i>Abstract:&nbsp;</i>On February 28, 2019, while shut down for a scheduled refueling outage in Mode 5, Unit 2 Division 1 safety-related electrical bus (241Y) tripped during surveillance testing. The purpose of the surveillance testing was to demonstrate the operability of the air circuit breakers (ACBs) necessary to provide the second off site source to Unit 2. The trip of the electrical bus resulted in a valid undervoltage actuation signal to the common emergency diesel generator ('0' EDG), causing it to start and load to Bus 241Y. Resulting from the 241Y bus trip and '0' EDG actuation signal, plant responses occurred as designed. Affected systems were restored, with no adverse impacts to either unit. Unit 1 remained stable during this event. <br /><br /> This condition was previously reported on March 1, 2019 (ENS 53903) in accordance with 10 CFR 50.72(b)(3)(iv)(A) for a valid specified system actuation. This event is reportable in accordance with 10 CFR 50.73(a)(2)(iv)(A), as an event that results in a valid actuation of the emergency AC electrical power system.<br /><br /> Troubleshooting and causal investigation determined the cause was attributed to ACB 2414 having a degraded lug on the terminal between the Unit 2 ACB 2414 A-phase current transformer and the Unit 1 ACB 1414 differential current relay. Corrective actions were taken to replace a degraded lug on the terminal that feeds the relay from the Unit 2 Bus 241Y A-phase current transformer.
3822019001 | Waterford 3 | 12/13/2018 | 02/11/2019 | ML19042A78 | <strong>Past Inoperability of Effluent Accident Monitor Exceeds Allowed Outage Time Resulting in Condition Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On December 13, 2018, a past operability evaluation determined that the Fuel Handling Building (FHB) Wide Range Gas Monitor (WRGM) had been inoperable from January 16, 2017 to November 30, 2018. The FHB WRGM had been inoperable due to a calibration error that was identified during the most recent surveillance calibration. Operability was restored after the calibration error was corrected on November 30, 2018. The FHB WRGM is credited as the FHB exhaust effluent monitor in Technical Specification (TS) 3.3.3.1. The TS allowed outage time is 72 hours before an alternative method of monitoring is required and 7 days before a special report to the Commission is required to be submitted.<br /><br /> This condition resulted from an error in the model work order for performing the FHB WRGM surveillance that uses an air flow calculation to calibrate the FHB WRGM air flow meter. The air flow calculation contained an incorrect value for orifice area due to a design change that re-sized orifice plates in the FHB Ventilation system. The calibration error resulted in the FHB WRGM measuring lower than actual effluent air flow through the FHB ventilation system. The orifice area value was corrected during performance of the last surveillance calibration. Long term corrective actions are to move these steps into a mechanical maintenance procedure and add a note to verify orifice areas in the field. There are no actual consequences as a result of this condition prohibited by Technical Specifications.
3822019002 | Waterford 3 | 12/19/2018 | 02/18/2019 | ML19049A02 | <strong>Control Room Envelope Declared Inoperable due to Outside Air Intake Isolation Valve Exceeding Closed Stroke Time During Inservice Testing Resulting in Event or Condition That Could Have Prevented Fulfillment of a Safety Function</strong><br /><i>Abstract:&nbsp;</i>On December 19, 2018, at 2322 Central Standard Time (CST), the shift operating crew declared the Control Room Envelope inoperable in accordance with Technical Specification (TS) 3.7.6.1 due to valve HVC-102 exceeding its maximum allowed closed stroke time of 2.0 seconds during performance of inservice testing. The actual closed stroke time was 2.1 seconds. Valve HVC-102 is part of the Control Room Envelope. The inoperability of the Control Room Envelope resulted in an event or condition that could have prevented fulfillment of a safety function. The TS required action to implement mitigating actions was completed on December 19, 2018 at 2355 CST by placing the control room ventilation system in isolate mode. <br /><br /> An equipment failure evaluation determined that the cause of this event was that there was lack of lubrication in the HVC-102 valve actuator. Actions were taken to rebuild and properly lubricate the valve actuator. Following a successful inservice test of HVC-102, the Control Room Envelope was declared operable on December 27, 2018. Additional corrective action includes reviewing the maintenance procedure and vendor manual to determine if a change in the preventive maintenance task is warranted.
3822019003 | Waterford 3 | 01/17/2019 | 03/15/2019 | ML19078A17 | <strong>Relevant Indications Identified in Reactor Coolant Pump 1A and 2A Suction Drain Nozzle Dissimilar Metal Welds Resulting in the Condition of the Nuclear Power Plant, Including its Principal Safety Barriers, Being Seriously Degraded</strong><br /><i>Abstract:&nbsp;</i>On January 17 and 18, 2019, relevant indications were detected on the Reactor Coolant System (RCS) Loop Reactor Coolant Pump (RCP) suction drain nozzle to safe-end butt welds 07-009 (RCP 1A) and 11-007 (RCP 2A) during the performance of Phased Array Ultrasonic Examination of Alloy 600 dissimilar metal piping welds during planned inspections which were being conducted during Refueling Outage 22. This resulted in an event or condition that resulted in the condition of the nuclear power plant, including its principal safety barriers, being seriously degraded because they did not meet acceptance criteria referenced in American Society of Mechanical Engineers Section XI, IWB-3514-2 and Code Case N-770-2. The RCS was declared inoperable per Technical Requirements Manual (TRM) requirement 3.4.9, "Structural Integrity." <br /><br /> The cause of this event was Primary Water Stress Corrosion Cracking. Action was taken to restore full component integrity and assure structural integrity of the affected welds by applying dissimilar metal weld full structural weld overlays over the affected components. The RCS was subsequently declared operable on February 18, 2019 and TRM 3.4.9 was exited.
3822019004 | Waterford 3 | 03/10/2019 | 05/09/2019 | ML19129A43 | <strong>Boron Dilution Alarm (Startup Channel High Neutron Flux) Inoperable Resulting in Operation or Condition Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On March 10, 2019, at 2310 Central Daylight Time (CDT), Startup Channel 1 was declared inoperable due to discovery that it was de-energized. Technical Specification (TS) 3.1.2.9, "Boron Dilution," was entered. It was determined that this condition originated during the previous shift, when the Plant Protection System (PPS) Channel 'C' Functional Test was performed. Per the test, Startup Channel 1 was selected to 'Alternate,' resulting in it being automatically de-energized based on the indicated value of Log Power Channel 'D', which had been previously declared inoperable due to erratic behavior. The condition went undetected until discovery, resulting in an event or condition prohibited by Technical Specifications. Operability was restored to Startup Channel 1 and TS 3.1.2.9 was exited at on March 10, 2019 at 2318 CDT. <br /><br /> The cause of this event was there was no guidance in the surveillance procedure to verify the operability of the associated Log Power Channel prior to performing the test. Action to revise the procedure to require verification of operability has been completed.
3822019005 | Waterford 3 | 05/16/2019 | 07/15/2019 | ML19196A34 | <strong>Automatic Reactor Scram due to Steam Generator #1 High Level Resulting from a Main Turbine Trip and Subsequent Reactor Power Cutback due to Failed Diode Modules within the Main Exciter</strong><br /><i>Abstract:&nbsp;</i>On May 16, 2019, at 1348, Waterford 3 experienced an automatic reactor trip due to Steam Generator 1 high level, which occurred following a main turbine trip and reactor power cutback. The automatic reactor trip due to Steam Generator 1 high level was caused by feedwater control shifting to manual during reactor power cutback due to a deviation between Steam Generator level channels. Because feedwater control was in manual, the system could not lower feed water flow in response to rising Steam Generator level. Main Feedwater Isolation Valves #1 and #2 closed on high Steam Generator levels. Emergency Feedwater automatically actuated as expected for Steam Generator #1 and #2. Main Feedwater was restored to both Steam Generators by 1629. The cause of the Steam Generator level deviation is still under investigation.<br /><br /> The main turbine trip was caused by a loss of excitation within the main generator field. The cause of the loss of excitation was determined to be a short between 2 diode modules within the rotating rectifier circuit of the Main Exciter. The Main Exciter was mechanically disassembled and the failed fuses and diode modules in the rotating rectifier wheel were replaced. The entire rotating rectifier assembly was refurbished and/or repaired as appropriate. The exciter control system was fully calibrated prior to startup. <br /><br /> All required safety-related equipment responded as expected during this event.
3822019006 | Waterford 3 | 06/25/2019 | 08/23/2019 | ML19235A26 | <strong>Unplanned Loss of Both Trains of Broad Range Gas Monitors Results in a Condition that Could Have Prevented Fulfillment of a Safety Function</strong><br /><i>Abstract:&nbsp;</i>On June 25, 2019, at 0428, Waterford 3 declared both Broad Range Gas Monitor (BRGM) channels inoperable and the control room emergency air filtration system was manually placed in isolate mode at 0441 to comply with the 1-hr action requirement of Technical Specification (TS) 3.3.3.7.3, "Broad Range Gas Detection." With both BRGM channels declared inoperable, TS 3.7.6.1, "Control Room Emergency Air Filtration," was not met. For the 13 minutes prior to the control room being manually isolated, the Control Room Envelope Boundary was inoperable, resulting in an event or condition that could have prevented fulfillment of a safety function.<br /><br /> The root cause of the event was that the Broad Range Gas Monitoring System is not designed to automatically isolate the Control Room Envelope for conditions resulting in a Toxic Gas Monitor Trouble Alarm. Actions were completed to restore both trains of BRGMs to operable status and issue a Standing Instruction to preventively isolate Control Room ventilation during BRGM or Chlorine Monitor outages. Planned actions are to complete a design modification that would isolate the control room emergency filtration system upon the receipt of a toxic gas monitoring trouble alarm.
3822019007 | Waterford 3 | 07/31/2019 | 09/26/2019 | ML19269D86 | <strong>Plant Shutdown Required by Technical Specifications due to Charging Pump Suction Line Flaw</strong><br /><i>Abstract:&nbsp;</i>On June 30, 2019, at 2112 Central Daylight Time, Reactor Coolant System (RCS) unidentified leakage experienced a step increase from 0.02 gpm to 0.24 gpm. During the subsequent leak investigation, leakage was identified in a Chemical and Volume Control (CVC) system drain line upstream of valve CVC-186. CVC-186 provides a drain path from the Volume Control Tank and Charging Pump suction header to the Equipment Drain Tank. This line is on the suction path to all three charging pumps and is part of the boration flow path to the Charging Pumps. <br /><br /> Radiography was performed and determined that the line had a 1.162-inch-long circumferential flaw. The flaw was located on the approximate 1/8-inch exposed portion of the line between weld toes. Analysis was performed and determined that the maximum allowable flaw size for the piping configuration was 1.7 inches. Daily monitoring of the piping flaw was established. On 7/31/2019, the flaw size was measured to be 1.75 inches. The flaw growth resulted in all three Charging Pumps and the associated boration flow path being inoperable. Operations entered Technical Specification 3.0.3 and commenced a plant shutdown. Repairs were attempted in Mode 3 but were unsuccessful. The plant entered Mode 5 and replaced the damaged section of pipe. After the repairs were completed the system was successfully returned to service.
3872019001 | Susquehanna 1, Susquehanna 2 | 05/22/2019 | 12/11/2019 | ML19345F67 | <strong>Loss of Both Control Structure Chillers due to Misaligned Breaker Stab</strong><br /><i>Abstract:&nbsp;</i>On May 22, 2019, at 0240, the A Control Structure (CS) Chiller tripped due to a loss of power to Motor Control Center (MCC) 0B136. At the time of the trip, the B CS Chiller was out of service for planned maintenance on the Emergency Service Water (ESW) System. The CS Chillers are required to be operable by Technical Specifications (TS) Limiting Conditions for Operation (LCOs) 3.7.3, “Control Room Emergency Outside Air Supply (CREOAS) System” and 3.7.4, “Control Room Floor Cooling System.” The CREOAS and Control Room Floor Cooling systems provide cooling and ventilation to various safety-related loads including the control room, computer room, relay rooms, and emergency switchgear rooms. The loss of both chillers required entry in LCOs 3.7.3, 3.7.4, and 3.0.3, thereby requiring the commencement of a dual unit shutdown. As a result, this event was reported in accordance with 10 CFR 50.72(b)(3)(v) as a condition which could have prevented the fulfillment of a safety function and 10 CFR 50.72(b)(2)(i) for the initiation of a plant shutdown required by TS. The power reduction was halted upon restoration of the A CS Chiller. The condition was also determined to be reportable in accordance with 10 CFR 50.73(a)(2)(v) as a condition that could have prevented the fulfillment of a safety function. <br /><br /> The direct cause was determined to be inadequate engagement of cubicle stabs. The root cause was determined to be vendor design differences in cubicle stab assemblies introduced during replacement of original plant equipment. Corrective actions include removing the misaligned breaker stab from service and de-energizing, cleaning, and inspecting MCC 0B136.<br /><br /> There were no actual safety consequences associated with the condition.
3872019002 | Susquehanna 1, Susquehanna 2 | 08/28/2019 | 12/18/2019 | ML19352E17 | <strong>Inoperability of "C" Emergency Service Water Pump</strong><br /><i>Abstract:&nbsp;</i>On August 28, 2019 at approximately 17:40, during lnservice Testing (IST) of the "A" loop of Emergency Service Water (ESW), the differential pressure for the "C" ESW pump (0P504C) was found to be 88.875 psid, which was below the established IST acceptance criteria. Based on the test results, the "C" ESW pump was in the IST Required Action Range, which requires the pump to be declared inoperable. At the time of discovery of this condition, Susquehanna was already in Technical Specification (TS) 3.7.2 Condition C for "A" loop maintenance. On August 29, 2019, the pump lift setting was adjusted and the "C" ESW pump was retested. The retest resulted in an acceptable differential pressure of 91.9 psid, which was in the Alert Range and no longer in the Required Action Range. TS 3.7.2 Condition C was exited on August 29, 2019 at approximately 15:45. On October 04, 2019, Susquehanna completed replacement of the "C" ESW pump. <br /><br /> The direct cause was determined to be separation of the lower pump casing flange (bottom column to top case) resulting in a loss of differential pressure. The apparent cause was determined to be corrosion of the carbon steel bolting in raw water. This was accelerated by galvanic interactions with silt, Copper never-seize, and alloy steel. Completed corrective actions include replacement of the "C" ESW pump. Planned corrective actions include a review of the appropriate preventive maintenance (PM) frequency for pump replacement. <br /><br /> Based on available information, the condition is considered to have existed for longer than allowed by TS 3.7.2. The condition is being reported in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by Technical Specifications and 10 CFR 50.73(a)(2)(v) as an event or condition that could have prevented fulfillment of a safety function. <br /><br /> There were no actual safety consequences associated with the condition.
3872019003 | Susquehanna 1, Susquehanna 2 | 10/13/2019 | 12/11/2019 | ML19345F62 | <strong>D Diesel Generator Inoperable due to Inadequate Post-Maintenance Test</strong><br /><i>Abstract:&nbsp;</i>On October 13, 2019, at 10:08, during performance of surveillance testing, the D Diesel Generator (DG) failed to reach the required frequency within the time specified by the acceptance criteria. Operators declared Surveillance Requirement 3.8.1.7 failed and entered Technical Specification (TS) Limiting Condition for Operation (LCO) 3.8.1, Condition B, on both Susquehanna Steam Electric Station units for the inoperable D DG. The other three DGs (A, B, and C) were verified to be OPERABLE before operators commenced a subsequent test of the D DG at 12:12, during which the D DG met all required acceptance criteria. The D DG was declared OPERABLE at 17:56 and LCO 3.8.1, Condition B, was exited for both units.<br /><br /> The failure to reach the required frequency within the acceptance criteria was the result of inadequate oil pressure in the D DG mechanical governor internals which was caused by an inadequate Post Maintenance Test (PMT). The condition of the inoperable D DG was determined to have existed since September 17, 2019, and the event was determined to be reportable in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by TS. Due to a concurrent inoperability of the C DG, the event was also determined to be reportable in accordance with 10 CFR 50.73(a)(2)(v) as an event or condition which could have prevented the fulfillment of a safety function. Corrective actions include procedure updates to ensure adequate PMTs are performed in the future. <br /><br /> There were no actual safety consequences associated with this event.
3882019001 | Susquehanna 2 | 03/28/2019 | 07/10/2019 | ML19192A01 | <strong>Main Steam Isolation Valve Leakage</strong><br /><i>Abstract:&nbsp;</i>During the Susquehanna Unit 2 refueling outage, Local Leak Rate Testing (LLRT) conducted on March 27, 2019 determined combined as-found leakage through the inboard Main Steam Isolation Valve (MSIV) (HV241F022D) and the outboard MSIV (HV241F028D) in the "D" Main Steam Line was 55,425 standard cubic centimeters per minute (sccm). Subsequent testing, on March 28, 2019 at approximately 20:30, measured the leakage through HV241F028D as 47,791 sccm, which exceeded the Technical Specification (TS) Surveillance Requirement (SR) 3.6.1.3.12 limit of 100 standard cubic feet per hour (scfh) (47,194 sccm) for individual valve leakage. <br /><br /> Based on cause and history, the condition likely existed during the last operating cycle for longer than allowed by TS 3.6.1.3. The condition is being reported in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by Technical Specifications. <br /><br /> The direct cause of the LLRT failure was valve seating surface wear/degradation over the 34 years in service. Repairs made to the valve resulted in an acceptable as-left LLRT. <br /><br /> There were no actual safety consequences associated with the condition.
3882019002 | Susquehanna 2 | 06/27/2019 | 08/22/2019 | ML19234A25 | <strong>Valid Actuation of the Primary Containment Isolation System due to a Trip of Reactor Protection System Bus 2B</strong><br /><i>Abstract:&nbsp;</i>On June 27, 2019, at 0937 a half scram signal was received on Unit 2, Division 2 of the Reactor Protection System (RPS). The half scram signal resulted in a trip of the 2B RPS instrument bus, a trip of the 2A Residual Heat Removal Service Water (RHRSW) Pump, a loss of the 2A and 2B Containment Radiation Monitors (CRMs), and Primary Containment Isolation System (PCIS) actuations. The loss of both CRMs resulted in entering Condition B of Technical Specifications (TS) Limiting Condition for Operation (LCO) 3.4.6, “RCS Leakage Detection Instrumentation.” The PCIS actuation resulted in isolation of containment isolation valves in multiple systems and was determined to be reportable in accordance with 10 CFR 50.72(b)(3)(iv)(A) for the valid isolation signal. The 2B RPS instrument bus was transferred to its alternate power supply and the 2A and 2B CRMs were restored. The 2B RPS instrument bus was realigned to its normal source on July 2, 2019. The condition was also determined to be reportable in accordance with 10 CFR 50.73(a)(2)(iv)(A) for the valid PCIS signal. <br /><br /> The event was determined to be caused by an age-related failure of a control relay on the normal power supply to the 2B RPS instrument bus. Corrective actions included replacing the failed relay. <br /><br /> There were no actual safety consequences associated with the condition.
3902019001 | Watts Bar 1, Watts Bar 2 | 04/23/2019 | 05/20/2019 | ML19140A09 | <strong>Control Room Emergency Ventilation System Inoperable due to Main Control Room Door Being Left Open</strong><br /><i>Abstract:&nbsp;</i>At 0232 Eastern Daylight Time (EDT) on April 23, 2019, a Main Control Room (MCR) alarm was received for low control room positive pressure. At 0233 EDT, a Control Room Envelope (CRE) door was found ajar and immediately closed. Technical Specification Limiting Condition for Operation (LCO) 3.7.10, Control Room Emergency Ventilation System (CREVS), was declared not met for both trains and Condition B entered. At 0233 EDT on April 23, 2019, the alarm cleared, CREVS was declared operable and LCO 3.7.10, Condition B was exited. <br /><br /> This event was caused by a human performance error when an individual traversing the control building complex failed to confirm the MCR envelope boundary door was properly latched. The open control room door was identified and promptly closed. The individual involved was coached on the requirement to challenge the door when traversing the control building complex. Work orders to install engineering features on MCR doors to ensure they are closed after opening were completed after this event occurred.<br /><br /> This condition is being reported as an event or condition that could have prevented fulfillment of a safety function needed to mitigate the consequences of an accident in accordance with 10 CFR 50.73(a)(2)(v)(D).
3902019002 | Watts Bar 1, Watts Bar 2 | 06/12/2019 | 08/07/2019 | ML19219A21 | <strong>Loss of Control Room Emergency Air Temperature Control System due to Air Filter Failure</strong><br /><i>Abstract:&nbsp;</i>On June 12, 2019 at 0849 Eastern Daylight Time (EDT) a significant air leak on an inline air filter was identified. At 0908 EDT the leak on the filter was bypassed. This air leak impacted operation of the Control Room Emergency Air Temperature Control System (CREATCS) A Train. Two CREATCS trains are required to be operable in accordance with Technical Specification 3.7.11. At the time of this event, CREATCS B Train was out of service for planned maintenance. <br /><br /> The direct cause of this event is an air filter gasket leak. As corrective action, a different vendor approved gasket has been installed. <br /><br /> This condition is being reported as an event or condition that could have prevented fulfillment of a safety function needed to mitigate the consequences of an accident in accordance with 10 CFR 50.73(a)(2)(v)(D).
3902019003 | Watts Bar 1 | 08/31/2019 | 10/21/2019 | ML19294A01 | <strong>Manual Reactor Trip due to Main Feedwater Regulating Valve Failing Closed</strong><br /><i>Abstract:&nbsp;</i>On August 31, 2019, at 2055 Eastern Daylight Time (EDT), the Watts Bar Nuclear Plant (WBN) Unit 1 reactor was manually tripped due to a loss of Steam Generator (SG) number 2 level control. Concurrent with the reactor trip, the Auxiliary Feedwater system actuated as designed. All Control and Shutdown rods inserted properly. All safety systems responded as designed. <br /><br /> This event was likely caused by diaphragm case bolt relaxation. This relaxation resulted in additional load on the bolt holes of the diaphragm, causing tearing and failure. Corrective actions include replacement of the defective diaphragm and revising the diaphragm case bolt torque requirement in the vendor manual and maintenance procedure. <br /><br /> This condition is being reported as a safety system actuation in accordance with 10 CFR 50.73(a)(2)(iv)(A).
3902019004 | Watts Bar 1, Watts Bar 2 | 11/15/2019 | 01/13/2020 | ML20013D72 | <strong>Control Room Emergency Ventilation System Inoperable due to Main Control Room Door Being Left Open</strong><br /><i>Abstract:&nbsp;</i>On November 15, 2019, on two occasions, a Main Control Room (MCR) alarm was received for low control room positive pressure. At 2234, and again at 2353 Eastern Standard Time (EST), a Control Room Envelope (CRE) door was found ajar and immediately closed. Technical Specification (TS) Limiting Condition for Operation (LCO) 3.7.10, Control Room Emergency Ventilation System (CREVS), was declared not met for both trains and Condition B entered for both instances. At 2236 EST, and at 2355 EST on November 15, 2019, the alarm cleared, CREVS was declared operable and LCO 3.7.10, Condition B was exited.<br /><br /> These events were caused by human performance errors when individuals traversing the control building complex failed to confirm the MCR envelope boundary door was properly latched. The open control room door was identified and promptly closed. Contributing to this event, maintenance had been performed on the door sweep which resulted in the door involved not closing on its own. Immediate corrective actions included posting a door watch, coaching the individuals involved, and correcting the door sweep issue. Actions to prevent recurrence include training on proper door maintenance post maintenance testing and increased observations of plant staff related to door operation. <br /><br /> This condition is being reported as an event or condition that could have prevented fulfillment of a safety function needed to mitigate the consequences of an accident in accordance with 10 CFR 50.73(a)(2)(v)(D).
3912019001 | Watts Bar 2 | 05/22/2019 | 07/18/2019 | ML19199A08 | <strong>Manual Reactor Trip due to Main Feedwater Regulating Valve Failing Closed</strong><br /><i>Abstract:&nbsp;</i>On May 22, 2019, at 0233 Eastern Daylight Time (EDT), Watts Bar Nuclear Plant Unit 2 reactor was manually tripped due to a failure of the Steam Generator (SG) number 2 Main Feedwater Regulating Valve (MFRV) during power ascension following a refueling outage. Concurrent with the reactor trip, the Auxiliary Feedwater system actuated as designed. All Control and Shutdown rods fully inserted. All safety systems responded as designed. <br /><br /> This event was caused by a defective actuator diaphragm that led to premature failure and subsequent loss of control of the SG 2 MFRV. Contributing to this event, personnel missed an opportunity to identify the actuator diaphragm was defective during its replacement. Corrective actions include replacement of the defective diaphragm and revising the procedure for diaphragm inspection and installation. <br /><br /> This condition is being reported as a safety system actuation in accordance with 10 CFR 50.73(a)(2)(iv)(A).
3912019002 | Watts Bar 2 | 06/20/2019 | 08/19/2019 | ML19231A03 | <strong>Breach due to Penetration Boot Seal Separation Results in Shield Building Inoperability</strong><br /><i>Abstract:&nbsp;</i>On June 20, 2019, at 1340 Eastern Daylight Time (EDT), a breach in excess of allowable margin was identified in the Watts Bar Nuclear Plant (WBN) Unit 2 Shield Building annulus. The breach consisted of a penetration boot seal that had pulled away from the shield building wall, creating a gap between the boot seal and the annulus wall. As a result, WBN U2 entered Technical Specification (TS) Limiting Condition for Operation (LCO) 3.6.15, Condition A, for the shield building being inoperable. On June 21, 2019, at 0036, the boot seal was repaired, and WBN U2 exited LCO 3.6.15, Condition A. <br /><br /> There were no human performance errors identified that contributed to this event. Corrective actions included repairing the boot seal, and modifying permanent scaffolding. <br /><br /> This event is being reported to the Nuclear Regulatory Commission (NRC) under 10 CFR 50.73(a)(2)(v)(C) as an event or condition that could have prevented fulfillment of a safety function of structures or systems that are needed to control the release of radioactive material.
3952019001 | Summer 1 | 12/06/2018 | 08/19/2019 | ML19231A34 | <strong>Condition Prohibited by Technical Specification 3.4.6.1</strong><br /><i>Abstract:&nbsp;</i>On September 16, 2017, during the Reactor Building Cooling Unit (RBCU) Functional Test, STP-116.001, RBCU condensate drain flow switch 'A' (IFS01900A) came into alarm, would not clear, and was removed from service. Since one condensate flow switch is required for compliance with Virgil C. Summer Nuclear Station (VCSNS) Technical Specifications (TS) Limiting Condition for Operation (LCO) 3.4.6.1, RBCU condensate flow switch 'B' (IFS01900B) was credited for operability for the remainder of the cycle (CY24). <br /><br /> On October 29, 2018, during the Refuel 24 (RF24) inspection and cleaning of IFS01900B, it was discovered that the switch did not change states and the required alarm failed to initiate when flow was applied to the drain line with demineralized water. Inspection and cleaning identified that debris in the drain sensing line, including algae growth, had constricted flow. A past operability evaluation was performed and determined that the failure mechanism indicated that IFS01900B could not have been relied on as operable during the last cycle. Conservatively, it was determined inoperable for the entirety of the past cycle.<br /><br /> Review of station work orders identified that for short periods of time between September 16, 2017 to October 6, 2018, the TS-required compensatory actions were not met.
3952019002 | Summer 1 | 03/08/2018 | 10/09/2019 | ML19283B20 | <strong>Condition Prohibited by Technical Specification 3.6.4</strong><br /><i>Abstract:&nbsp;</i>On March 8, 2018, Steam Generator (SG) Power Operated Relief Valve (PORV), IPV-2010-MS, failed its operability test. An apparent cause evaluation determined that excessive grease in the valve positioner was blown downstream into the pilot stem, which caused the pilot stem to stick. A past operability evaluation determined that the SG PORV was inoperable between the time period of 1/30/2018 through 03/08/2018 due to the SG PORV's inability to open. This is a violation of Technical Specification 3.6.4, since the past operability exceeded the restoration time described in Technical Specification 3.6.4.
3952019003 | Summer 1 | 11/05/2019 | 01/03/2020 | ML20006D94 | <strong>Completion of a Technical Specification Required Plant Shutdown</strong><br /><i>Abstract:&nbsp;</i>On November 5, 2019, at 1041, while operating in Mode 1 at 100% reactor power, the Virgil C. Summer Nuclear Station entered Technical Specification (TS) Limiting Condition for Operation (LCO) action statement 3.6.2.3.a as a result of having one group of Reactor Building Cooling Units (RBCU) inoperable. TS 3.6.2.3.a requires the inoperable group to be restored to operable status within seven days or be in at least hot standby within the next six hours and in cold shutdown within the following thirty hours. <br /><br /> Due to ongoing efforts to identify an existing Reactor Coolant System (RCS) leak, the station conservatively shutdown to further investigate both the unidentified RCS leakage and the cause of the RBCU trips. The plant entered Mode 3 on November 7, 2019, at 0528, completing the plant shutdown. At the time of shutdown it was not evident that the failure could not be corrected within the LCO allowed outage time. Therefore, a notification was not submitted in accordance with 10 CFR 50.72(b)(2)(i). This Licensee Event Report (LER) is being provided per the requirements of 10 CFR 50.73(a)(2)(i)(A) because the RBCU condition was not restored within the seven day LCO allowed outage time. <br /><br /> A Failure Mode Analysis (FMA) and Root Cause Analysis (RCA) are being performed. A supplemental LER will be submitted to provide the results of these investigations.
3952019004 | Summer 1 | 11/21/2019 | 01/17/2020 | ML20017A19 | <strong>Condition Prohibited by Technical Specification 3.6.1.1</strong><br /><i>Abstract:&nbsp;</i>On November 21, 2019, at approximately 0217 while operating in Mode 1 at 30% reactor power, operators found the nitrogen supply header valves to the steam generators open and unlocked while performing Surveillance Test Procedure (STP) -115.001, "Penetration Isolation Verification". Satisfactory completion of STP-115.001 demonstrates Containment Integrity per Technical Specification (TS) Surveillance Requirement 4.6.1.1.a. The nitrogen supply header valves being open resulted in a condition prohibited by TS 3.6.1.1 since the valves were open longer than allowed by the TS 3.6.1.1.a Limiting Condition for Operation (LCO) action statement.<br /><br /> Immediate actions were taken to restore system alignment at the time of discovery. Since the Steam Generator secondary side was intact there was no direct open flow path from containment during the time the valves were open. <br /><br /> This Licensee Event Report (LER) is being provided per the requirements of 10 CFR 50.73(a)(2)(i)(B) because Containment Integrity was not restored within the one hour LCO allowed outage time.
3972019001 | Columbia | 09/24/2019 | 11/25/2019 | ML19329E56 | <strong>Loss of Diesel Starting Air During Maintenance Leads to Loss of High Pressure Core Spray System</strong><br /><i>Abstract:&nbsp;</i>On September 24, 2019, at 2338 PDT during maintenance to drain an air receiver in the High Pressure Core Spray (HPCS) Diesel Starting Air (DSA) system a pressure control valve (PCV) vented, due to a leaking isolation valve, causing the in-service air receiver pressure to drop below the minimum Technical Specifications value. Operations declared the HPCS Diesel Generator, HPCS Service Water, and the HPCS system inoperable.<br /><br /> The root cause of the event was that the plant procedure was revised in 2009 to open the air start motor cross connect valve to retain all 4 air start motors available for diesel start which is not in accordance with current licensing/design bases. Corrective actions include revision to station procedures and repair of the leaking isolation valve. <br /><br /> This is reportable under 10 CFR 50.73(a)(2)(v)(D) as an event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident. This event was reported under 10 CFR 50.72(b)(3)(v)(D) as Event Notification #54292.
4002019001 | Harris | 04/17/2019 | 09/16/2019 | ML19259A07 | <strong>Turbine Control System Auto-Stop Trip Solenoid Operated Valves Response Times Impacted</strong><br /><i>Abstract:&nbsp;</i>On April 16-17, 2019, the Shearon Harris Nuclear Power Plant, Unit 1, attempted to perform turbine trip testing of each individual solenoid operated valve (SOV) within the Auto-Stop Trip (AST) and Overspeed Protection Control (OPC) Quadvoter Trip Block assemblies. The response received on April 16th for the first AST Quadvoter SOV indicated that the valve was unable to cycle. Troubleshooting efforts were successful in restoring functionality of the valve. The redundant SOV in the A channel tested satisfactorily. On April 17th, testing of the B channel was completed and the first SOV tested failed similarly to the first A channel valve. Troubleshooting efforts were successful in restoring functionality and preemptively applied to the second SOV in the B channel. Based on the test results, it is likely that both channels of the system were non-functional at the same time. With both AST channels rendered non-functional, the system was incapable of depressurizing the AST hydraulic header to trip the main turbine within the time response requirements of Technical Specifications. The root cause of this event is that the vendor design of the Quadvoter utilized spool-type pilot SOVs without adequately addressing inherent design vulnerabilities in a Fyrquel fluid application to ensure consistent, reliable operation of the trip and reset functions. Immediate action was taken to increase the frequency of AST valve testing and to increase the cycling of the solenoid valves for each test. Pilot valve springs were replaced with a stronger spring in all AST valves. Planned corrective actions include a design change to reduce the sensitivity of the pilot SOVs to the determined failure mechanisms and the flushing of AST and OPC Quadvoter Trip Block assemblies.
4002019002 | Harris | 07/14/2019 | 09/16/2019 | ML19259A07 | <strong>'B' Train Chiller for the Essential Services Chilled Water System Tripped on High Compressor Oil Temperature</strong><br /><i>Abstract:&nbsp;</i>On July 14, 2019, the Shearon Harris Nuclear Power Plant, Unit 1, declared the 'B' train of the Essential Services Chilled Water (ESCW) system inoperable after the water chiller (WC-2B) tripped on high compressor oil temperature. The ESCW system was last ran successfully on July 13, 2019, and was restored on July 16, 2019. This time frame exceeded the technical specification (TS) allowed out-of-service time. The 'A' train of the ESCW system was operable during this time period. The event represents a condition prohibited by TS per 10 CFR 50.73(a)(2)(i)(B). <br /><br /> Several factors caused WC-2B to trip on high oil temperature. Fouling of WC-2B raw water condenser, along with a reduction in refrigerant volume, led to reduced heat transfer from refrigerant to service water in the condenser. The result was an overall increase in compressor bearing loading that exacerbated the effects of the oil level, which was low though in-band. Oil and refrigerant were added and a refrigerant leak was addressed, restoring the system to operable. <br /><br /> The condenser was physically cleaned, recovering additional chiller operational margin. Actions are being taken to address service water fouling.
4002019003 | Harris | 10/14/2019 | 12/12/2019 | ML19346D06 | <strong>Both Source Range Nuclear Instruments Inoperable</strong><br /><i>Abstract:&nbsp;</i>On October 14, 2019, while in Mode 5, both Source Range (SR) Nuclear Instruments (NIs) were inoperable simultaneously. NI-32 was inoperable on October 12 for surveillance testing, and was restored by October 15. NI-31 was removed from service to support an emergent maintenance activity on October 14, and was restored the same day. However, NI-31 remained inoperable after restoration due to an invalid indication of a steadily increasing count rate. This issue was not identified until October 15, 2019, when NI-31 failed a channel check. <br /><br /> Work was planned to address NI-31, with NI-32 operable. However, on November 8, 2019, while in Mode 6, NI-32 began exhibiting an invalid count increase. This was identified on November 9, 2019, after a failed channel check, and NI-32 was declared inoperable. NI-31 and NI-32 were inoperable simultaneously until NI-32 was repaired on November 9, 2019. NI-31 was repaired November 15, 2019. The cause of NI-31's degraded performance was borated water intrusion into the detector well from overfilling the lower reactor cavity the previous outage. <br /><br /> The cause of NI-32's degraded performance was a failed potentiometer associated with the power supply. These unrelated issues have both been repaired. The loss of control of the lower cavity water level was addressed by adding additional monitoring capability (camera) to track any slow changes in lower cavity water level.
4102019001 | Nine Mile Point 2 | 11/01/2019 | 12/31/2019 | ML20014D45 | <strong>High Pressure Core Spray Declared Inoperable</strong><br /><i>Abstract:&nbsp;</i>At 03:16 on November 1, 2019, the Nine Mile Point Unit 2 (NMP2) High Pressure Core Spray (HPCS) System was declared inoperable when the Control Room Annunciation for HPCS SYSTEM INOPERABLE and INOP Status Light Indication for TRIP UNITS OUT OF FILE/POWER FAIL was received. The unplanned inoperability of the HPCS System per T.S. 3.5.1 is reportable in accordance with 10 CFR 50.72(b)(3)(v)(D) and 10 CFR 50.73(a)(2)(v)(D). Further investigation determined the 24VDC HPCS Trip Unit Power Supply (E22A-PS1) had failed. The Power Supply was replaced, and HPCS was declared operable on 11/01/19 at 15:55.
4132019001 | Catawba 1 | 03/21/2019 | 05/20/2019 | ML19140A41 | <strong>Condition Prohibited by Technical Specifications - Cooling Water Flow Path to 1A Emergency Diesel Generator Not Properly Aligned</strong><br /><i>Abstract:&nbsp;</i>On March 21, 2019, the 1A Emergency Diesel Generator (EDG) was started for monthly surveillance testing. After three minutes of operation, control room operators identified there was no Nuclear Service Water System (NSWS) flow to the 1A EDG Jacket Water Heat Exchanger. The 1A EDG was subsequently secured.<br /><br /> At the time of the NSWS no flow issue, the NSWS was in the Single Pond Header Discharge Operation alignment. In this alignment, the NSWS was supplying water to the 1A EDG Jacket Water Heat Exchanger from the normal supply valve, but the return path was in an alternate alignment. <br /><br /> 1A EDG was declared inoperable on March 21, 2019, at 1500 following the determination by Operations that the flow path through the B Train Standby Nuclear Service Water Pond (SNSWP) discharge header would not pass flow, which prevented cooling flow to the 1A EDG Jacket Water Heat Exchanger. Subsequent investigation found 1RN-P09 (1A EDG Crossover Valve to B Train Discharge) in the failed closed position due to actuator separation and the valve could not be opened using the gear operator. Valve 1RN-P09 was repaired and returned to service at 0354 on March 22, 2019. <br /><br /> There were no actual safety consequences and no effect on public health and safety as a result of this event.
4132019002 | Catawba 1 | 04/11/2019 | 09/11/2019 | ML19254F55 | <strong>Condition Prohibited by Technical Specifications and Loss of Safety Function due to Auxiliary Feedwater Sump Pump Conditions</strong><br /><i>Abstract:&nbsp;</i>On April 11, 2019, the 1B Motor Driven (MD) Auxiliary Feedwater (AFW) sump pump failed to start in manual and was nonoperational. The pump impeller was found seized. The 1B MDAFW sump pump was repaired and returned to service on May 1, 2019.<br /><br /> A new Auxiliary Building flooding calculation subsequently has shown that, in the event of a feedwater line break in the interior doghouse coincident with a loss of offsite power, the sump pumps for all three trains of the AFW pumps are required to remain functional. Taking into consideration the specified function of the AFW sump pumps, the 1B MDAFW pump should have been declared inoperable for the corresponding times that the sump pump was out of service. Therefore, the 1B MDAFW pump was inoperable for a period longer than the allowed Technical Specification (TS) Limiting Condition for Operation (LCO). <br /><br /> An extent of condition review identified two additional instances between April 11, 2019, and April 18, 2019, where two trains of AFW were inoperable due to the associated non-functional sump pumps and/or MDAFW pump inoperability for a period longer than the allowed TS LCO. Furthermore, the review identified one instance on January 19, 2019, where a test procedure resulted in all associated Unit 1 AFW sump pumps discharge valves being closed which resulted in a condition prohibited by the TS LCO and a loss of safety function. The health and safety of the public were not affected by this event.
4142019003 | Catawba 2 | 07/06/2019 | 09/04/2019 | ML19247D81 | <strong>Component Cooling Water System Alignment Led to Both Trains of Component Cooling Water Inoperable</strong><br /><i>Abstract:&nbsp;</i>On July 5, 2019, the 2A1 component cooling water (KC) pump discharge check valve 2KC-5 failed to close when the 2A1 KC pump was secured. The condition resulted in an unplanned entry into a 72-hour Technical Specification (TS) action statement for one train (2A) of KC inoperable. On July 6, 2019, during the repair of 2KC-5, the isolation boundary was expanded which caused Operations to perform an existing procedure which defeated the interlocks for the Non-Essential Reactor Building Supply and Return Header Valves to close on an engineered safeguards actuation signal. At the time, Operations was unaware that defeating the interlocks would cause a failure to meet a TS surveillance. Once the interlocks were defeated, the 2B KC Train should have also been declared inoperable due to the inability to meet the surveillance requirement. <br /><br /> The cause of this event was determined to be that a calculation and procedure change failed to identify the requirement to meet the TS surveillance. Operators also lacked a questioning attitude with information in the design bases document and approved procedures. Actions will be to correct procedures, implement training, and address the Operator learning. This event was determined to be reportable under 10CFR 50.73 (a)(2)(i)(B) for Condition Prohibited by TS and 10 CFR 50.73 (a)(2)(v) for Event or Condition that Could Have Prevented Fulfillment of a Safety Function.
4142019004 | Catawba 2 | 08/18/2019 | 10/17/2019 | ML19290G72 | <strong>Condition Prohibited by Technical Specification and Loss of Safety Function due to Refueling Water Storage Tank Volume Below the Minimum Requirement</strong><br /><i>Abstract:&nbsp;</i>On August 18, 2019, at 1700 hours, while aligned for purification of the Unit 2 Refueling Water Storage Tank (RWST), Catawba entered an unplanned action statement per Technical Specification (TS) Limiting Condition for Operation (LCO) 3.5.4 "RWST," Condition B. The Unit 2 RWST wide range (WR) level was discovered at a volume below the minimum TS required value when accounting for uncertainty. The Unit 2 RWST was removed from purification and makeup was immediately started. Unit 2 exited TS LCO 3.5.4 Condition B at 1744 on August 18, 2019. <br /><br /> At the time of the event, the Unit 2 RWST level narrow range (NR) channels were unavailable for completion of the TS Surveillance Requirement (SR) due to a previously known issue. Operators at the time failed to recognize that using WR level indication required accounting for additional instrument uncertainty. While actual level in the U2 RWST was later confirmed greater than the amount required for accident mitigation, the surveillance could not be met. <br /><br /> The cause of this event is overconfidence and a lack of validating assumptions regarding equipment deficiencies associated with the event, as well as a formal evaluation process was not used to fully evaluate risk when the NR indications were lost. The health and safety of the public was not affected by this event.
4162019001 | Grand Gulf 1 | 02/23/2019 | 08/22/2019 | ML19234A07 | <strong>Automatic Reactor Shutdown due to Activation of Generator Lockout</strong><br /><i>Abstract:&nbsp;</i>On Saturday, February 23, 2019, Grand Gulf Nuclear Station (GGNS) experienced an unplanned, automatic reactor shutdown without complications. This shutdown was initiated by the Reactor Protection System (RPS), as a result of a main generator lockout when the Generator Protective Relays responded to a negative phase sequence condition. All systems responded as designed. The negative phase sequence protection scheme set-point was changed (reduced from 9 percent to 5 percent) during the 2018 refueling outage, as part of the new main generator protective relay modification. The new set-point was exceeded resulting in the main generator trip. The direct cause of the trip was the negative phase sequence protection scheme 5 percent set-point for the Generator Protective Relays was exceeded. The cause has been determined to be the failure to ensure systematic and rigorous control of the configuration change process. Corrective actions include returning the negative phase sequence relay set-point back to 9 percent and establishing an audible alarm to alert the control room staff of any of the Generator Protective Relays approaching a protective scheme set-point. Planned actions include the development and implementation of improved standards for overseeing and controlling engineering rigor during the design change process. <br /><br /> This report is made pursuant to 10 CFR 50.73(a)(2)(iv)(A) for the actuation of the reactor protection system, as specified by 10 CFR 50.73(a)(2)(iv)(B). <br /><br /> There were no consequences to the general safety of the public, nuclear safety, industrial safety and radiological safety for this event.
4162019002 | Grand Gulf 1 | 05/12/2019 | 07/09/2019 | ML19190A21 | <strong>Manual Reactor Shutdown due to Loss of Service Water</strong><br /><i>Abstract:&nbsp;</i>On May 12, 2019, Grand Gulf Nuclear Station (GGNS) shutdown the reactor by moving the mode switch from RUN to SHUTDOWN due to a partial loss of Plant Service Water (PSW), in accordance with plant procedures. <br /><br /> The partial loss of PSW was caused by a partial loss of power to PSW pumps, and degraded capacity in one PSW well. Loss of power to plant service water pumps was caused by animal intrusion onto electrical service lines. <br /><br /> Drywell temperature briefly exceeded the technical specification limit but did not cause a loss of safety function, and Standby Service Water (SSW) was manually initiated to supply engineered safety function room and control room coolers. <br /><br /> Completed corrective actions include restoration of electrical service, procedure revisions, and training. Planned corrective actions include improved plant and engineering focus on degraded systems, installation of more robust electrical service, and a revised maintenance strategy for plant service water components. <br /><br /> This report is made pursuant to 10 CFR 50.73(a)(2)(iv)(A) for the actuation of the reactor protection system and initiation of SSW per 10 CFR 50.73(a)(2)(iv)(B); and 10 CFR 50.73(a)(2)(v)(D) for the potential loss of safety function. <br /><br /> There were no consequences to the general safety of the public, nuclear safety, industrial safety and radiological safety for this event.
4162019003 | Grand Gulf 1 | 08/05/2019 | 03/04/2020 | ML20064F75 | <strong>Secondary Containment Personnel Door Failure due to Broken Hinges</strong><br /><i>Abstract:&nbsp;</i>On August 5, 2019, at 09:36, the Control Room was notified that a Secondary Containment Door was found with door hinges broken and the door was unable to be closed. <br /><br /> Grand Gulf Nuclear Station performed action A.1 for Technical Specification (TS) LCO 3.6.4.1, Secondary Containment, not met due to the Secondary Containment door being inoperable. The broken hinges were replaced with qualified spares, and TS LCO 3.6.4.1 was met on August 5, 2019 at 13:36. <br /><br /> Based on vendor's engineering analysis, the Direct Cause was Door 1T101A401B hinge pins failed due to brittle fracture, resulting in a loss of the Secondary Containment Safety Function. <br /><br /> The Root Cause for the event is a design deficiency related to the mounting of the door hinges. The planned corrective action is a modification to the door. <br /> This will be done when secondary containment is not required to be operable. <br /><br /> This report is made pursuant to 10 CFR 50.73(a)(2)(v)(C) for an event or condition that at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to control the release of radioactive material. There were no consequences to the general safety of the public, nuclear safety, industrial safety and radiological safety for this event.
4162019004 | Grand Gulf 1 | 08/28/2019 | 10/24/2019 | ML19297H20 | <strong>Loss of High Pressure Core Spray due to Instrument Inverter Failure</strong><br /><i>Abstract:&nbsp;</i>On August 28, 2019, at 13:16, the Grand Gulf Nuclear Station Unit 1, Control Room received High Pressure Core Spray (HPCS) Out-of-Service annunciator, HPCS SYS OOSVC. HPCS was declared INOPERABLE and the following Technical Specification (TS) Action statements were entered: ECCS TS 3.5.1 Action B.1 and Primary Containment Isolation Valves TS 3.6.1.3 Action A.1.<br /><br /> The Direct Cause for the event is that the HPCS system instrument inverter lost inverter output that resulted in the inability to automatically initiate HPCS. Immediate corrective actions were taken to replace the instrument inverter restoring HPCS to an operable condition on August 28, 2019, at 23:15.<br /><br /> This report is made pursuant to 10 CFR 50.73(a)(2)(v)(D) for an event or condition that at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident. <br /><br /> There were no consequences to the general safety of the public, nuclear safety, industrial safety and radiological safety for this event.
4162019005 | Grand Gulf 1 | 09/11/2019 | 11/07/2019 | ML19311C25 | <strong>Primary Containment Personnel Airlock Potential Loss of Safety Function due to Inadequate Door Closure</strong><br /><i>Abstract:&nbsp;</i>On September 11, 2019 at 5:19pm, the Grand Gulf Nuclear Station primary containment was unable to fulfill its safety function because both doors on one airlock were open simultaneously for approximately thirty seconds.<br /><br /> The cause of this event is that the 208 primary containment airlock inner door latch pin position is not included in the electrical interlock or indication circuits. This caused the condition by allowing the outer airlock door open permissive to be met when the inner airlock door was not properly latched in the closed position. The 208-foot elevation airlock doors were immediately closed and verified latched and sealed. Additional corrective actions include revising the system operating procedure and the local operating placard instructions and a modification to ensure the proper closure, latching, and sealing of the 208-elevation airlock door. <br /><br /> This report is made pursuant to 10 CFR 50.73(a)(2)(v)(C) for an event or condition that at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident. <br /><br /> There were no consequences to the general safety of the public, nuclear safety, industrial safety and radiological safety for this event.
4162019006 | Grand Gulf 1 | 09/20/2019 | 11/18/2019 | ML19322C80 | <strong>Failure to Meet Technical Specifications 5.5.7 for Division II Standby Gas Charcoal Filter Media Efficiency</strong><br /><i>Abstract:&nbsp;</i>On September 20, 2019, Division II Standby Gas Treatment System (SBGT) was declared inoperable due to the failure to restore Division II SBGT to OPERABLE within the Limiting Condition for Operation (LCO) 3.6.4.3 seven (7) day action completion time.<br /><br /> Test results from the Division II SBGT charcoal filter did not meet the acceptance criteria in Technical Specification (TS) 5.5.7, Ventilation Filter Testing Program (VFTP). The test results were received on September 20, 2019 at 5:14 pm. The charcoal filter sample was obtained on September 4, 2019 at 2:38 am CDT. The charcoal media was considered deficient starting from the September 4, 2019 date of sample, to the discovery date of September 20, 2019, when the results were received. This deficiency placed the station in a condition that is prohibited by TS 3.6.4.3. Upon receipt of the charcoal filter results on September 20, 2019 the station entered TS 3.6.4.3. On September 22, 2019 at 10:05 pm, the charcoal bank was replaced. All testing and acceptance criteria were met, and TS 3.6.4.3 LCO was met on September 23, at 1:41 am. <br /><br /> The cause of the failure not being detected beforehand was contributed to inadequate monitoring and inadequate identification of adverse trends.<br /><br /> This report is made pursuant to 10 CFR 50.73(a)(2)(i)(B) for any operation or condition which was prohibited by the plant's Technical Specification. <br /><br /> There were no consequences to the general safety of the public, nuclear safety, industrial safety and radiological safety for this event.
4232019001 | Millstone 3 | 12/18/2019 | 02/13/2020 | ML20055D32 | <strong>Plant Shutdown Required by Technical Specifications, Emergency Diesel Generator Exceeded Allowed Outage Time</strong><br /><i>Abstract:&nbsp;</i>On December 17, 2019 at 1936 hours, while operating in Mode 1, at 100% power, Millstone Power Station Unit 3 (MPS3) operators commenced an orderly shutdown of MPS3 when it was determined that the 'A' Emergency Diesel Generator (EDG) maintenance, modifications and testing would not be completed within the allowed outage time by Technical Specification Action Statement (TSAS) 3.8.1.1 action b.5. The TSAS required that the plant be placed in Hot Standby (HSBY) within 6 hours and Cold Shutdown within the following 30 hours. The plant entered Hot Standby on December 18, 2019 at 0117 hours and entered Cold Shutdown on December 18, 2019 at 1948 hours.<br /><br /> During the post maintenance testing activities, the EDG first experienced unexpected EDG load reductions and then turbocharger surging. The load reductions were caused by an intermittent speed signal change (while paralleled to the grid). This was resolved by implementing a design change to utilize a magnetic pick up speed signal. The primary resolution for turbocharger surging was the replacement of the newly installed spread exhaust system with the original exhaust system, which was removed during the plant maintenance activities. Resolving these two unrelated issues required more than the TSAS Allowed Outage Time to correct.<br /><br /> This condition is being reported pursuant to 10 CFR 50.73(a)(2)(i)(A) - The completion of any nuclear plant shutdown required by the plant's technical specifications.
4242019001 | Vogtle 1 | 02/10/2019 | 04/08/2019 | ML19100A44 | <strong>Engineered Safety Feature Chiller Inoperability Causes Operation in a Condition Prohibited by TS</strong><br /><i>Abstract:&nbsp;</i>At approximately 0317 EST on February 7, 2019 while the unit was in Mode 1 and 100 percent power, the Unit 1 A-train Engineered Safety Feature Chiller was stopped after a post maintenance run. When the chiller was restarted on February 12, 2019 at 0026 EST it immediately tripped on high condenser pressure. During post-event analysis, it was determined that the chiller was inoperable immediately after being shut down from the post-maintenance run until it was repaired and declared operable on February 14, 2019 at 0436 EST. This resulted in the chiller being inoperable for approximately 169.3 hours, which is longer than the Technical Specification allowed out of service time of 72 hours. This resulted in the unit operating in a Condition Prohibited by Technical Specifications which is reportable under 10 CFR 50.73(a)(2)(i)(B). This event had no adverse effects on the health and safety of the public and is of very low safety significance
4252019001 | Vogtle 2 | 03/30/2019 | 05/28/2019 | ML19148A46 | <strong>Spurious Closure of Main Steam Isolation Valve results in Manual Reactor Trip</strong><br /><i>Abstract:&nbsp;</i>On March 30, 2019 at 2130, while Unit 2 was in Mode 1 and 30 percent power, exiting a refueling outage, when one of the Main Steam Isolation Valves (MSIV) failed closed unexpectedly. This resulted in an inability to maintain Steam Generator (SG) levels and pressures. The unit was manually tripped. All systems responded as designed. All control rods fully inserted into the core, auxiliary feedwater was started, and decay heat was removed through the main steam lines through the steam dumps and into the condenser. The plant was stabilized in Mode 3. Due to the manual actuation of systems listed in 10 CFR 50.73(a)(2)(iv)(B), specifically the Reactor Protection System and the Auxiliary Feedwater System, this event is reportable under 10 CFR 50.73(a)(2)(iv)(A). Because all systems responded as designed and had no adverse effects on the health and safety of the public, this event is of very low safety significance.
4252019002 | Vogtle 2 | 07/19/2019 | 09/04/2019 | ML19247C28 | <strong>Microswitch Failure Causes Closure of Main Steam Isolation Valve and Subsequent Automatic Reactor Trip</strong><br /><i>Abstract:&nbsp;</i>At 0945 EDT on July 19, 2019, with Unit 2 in Mode 1 and 100 percent power, the reactor automatically tripped due to the Loop 2 'B' Main Steam Isolation Valve failing shut. All systems responded as designed. All control rods fully inserted into the core, auxiliary feedwater started, and decay heat was removed through the main steam lines through the steam dumps and into the condenser. The plant was stabilized in Mode 3. <br /><br /> Due to the automatic actuation of systems listed in 10 CFR 50.73(a)(2)(iv)(B), specifically the Reactor Protection System and the Auxiliary Feedwater System, this event is reportable under 10 CFR 50.73(a)(2)(iv)(A). <br /><br /> Because all systems responded as designed and had no adverse effects on the health and safety of the public, this event is of very low safety significance.
4252019003 | Vogtle 2 | 10/09/2019 | 12/04/2019 | ML19338C61 | <strong>Transformer Deenergization Results in Emergency Diesel Generator and Auxiliary Feedwater Systems Starting</strong><br /><i>Abstract:&nbsp;</i>At 1023 EDT, on October 9, 2019, with Unit 2 in Mode 1 and 100 percent power, an actuation of the Unit 2 A-Train Emergency Diesel Generator (EDG)[EK] and the Unit 2 A-Train Auxiliary Feedwater (AFW)[BA] Systems occurred. The reason for the EDG auto-start was the loss of power to the 4160V 1E electrical bus 2AA02 [EB] due to a fault at an offsite electrical switchyard. The AFW system started as a result of the undervoltage condition on the safety bus. The EDG automatically started and energized the bus as designed. <br /><br /> Due to the automatic actuation of systems listed in 10 CFR 50.73(a)(2)(iv)(B), specifically the Emergency Diesel Generator and the Auxiliary Feedwater Systems, this event is reportable under 10 CFR 50.73(a)(2)(iv)(A). Corrective actions have been taken to ensure that additional controls are in place over this offsite switchyard when the SAT is in operation. <br /><br /> The operating crew responded correctly to the event. The applicable abnormal operating procedures were properly entered, and documentation met expectations.
4402019001 | Perry | 02/25/2019 | 04/24/2019 | ML19114A44 | <strong>Loss of Generator Excitation Causes Turbine Trip and Reactor Protection System Actuation</strong><br /><i>Abstract:&nbsp;</i>On February 25, 2019, at 0024 hours, the Reactor Protection System (RPS) automatically actuated due to turbine stop and control valve closure caused by a turbine trip. The turbine trip was caused by a loss of generator excitation, resulting in the loss of the main generator field. <br /><br /> The cause was determined to be inadequate preventive maintenance (PM) acceptance criteria for generator exciter brush replacement. The criteria for brush inspection and replacement should have added margin to brush lifetime to ensure brushes could not wear to the point where brush spring tension could no longer be properly maintained. Corrective actions included modifying preventive maintenance criteria to add margin to replace brushes earlier in their lifetime, and ensuring all brushes are checked for vibration during the PM.<br /><br /> The plant responded as expected, all control rods inserted and there were no Emergency Core Cooling System (ECCS) actuations. The risk of this event is considered very small in accordance with the Regulatory Guidance. This event is reported in accordance with 10 CFR 50.73(a)(2)(iv)(A) as an event or condition that resulted in an automatic actuation of the RPS.
4402019002 | Perry | 05/24/2019 | 07/18/2019 | ML19199A15 | <strong>Loss of Safety Function due to Low Pressure Core Spray Inoperability</strong><br /><i>Abstract:&nbsp;</i>On May 24, 2019, at 0730 hours, the Low Pressure Core Spray (LPCS) system was declared inoperable due to the inoperability of the Emergency Service Water (ESW) A pump. ESW A pump was declared inoperable based on a loss of continuity through the breaker control power closing fuses. Since LPCS is a supported system and a single train safety system, as specified in site procedures, LPCS inoperability is considered a loss of safety function and is reportable. <br /><br /> The cause for ESW A inoperability is that the Non-Licensed Operators (NLO) did not recognize that the control power fuses (AX) for ESW A pump breaker closing power were not fully seated following installation, after recent breaker racking activities. Corrective actions include changes to Switchgear, and Electrical Operator Safety training lesson plans, and a discussion of the event during NLO continuing training. <br /><br /> The safety significance of this event is considered very small. This event is being reported in accordance with 10 CFR 50.73(a)(2)(v)(D) as an event or condition that could have prevented the fulfillment of a safety function needed to mitigate the consequences of an accident.
4402019003 | Perry | 07/27/2019 | 09/25/2019 | ML19268A53 | <strong>Equipment Fault Causes Turbine Stop Valve Closure and Reactor Protection System Actuation</strong><br /><i>Abstract:&nbsp;</i>On July 27, 2019, at 1929 hours, the Reactor Protection System (RPS) automatically actuated due to a closure of the turbine stop valves. This event was caused by a failed component in the mechanical overspeed trip testing circuit. <br /><br /> The defective component was replaced, restoring the mechanical overspeed testing circuit The apparent cause of the event was determined to be infant mortality of mechanical shutoff valve 1N32F0400, as the valve had been replaced four months earlier during the last refueling outage. <br /><br /> A corrective action will evaluate and apply enhanced procurement for the Electro Hydraulic Control (EHC) Single Point Vulnerability components that are a part of the turbine front standard. <br /><br /> The plant responded as expected and all control rods inserted fully. The safety significance of this event is considered very small in accordance with the Regulatory Guidance. This event is reported in accordance with 10 CFR 50.73(a)(2)(iv)(A) as an event or condition that resulted in an automatic actuation of the RPS and a valid actuation of the Reactor Core Isolation Cooling (RCIC) system.
4402019004 | Perry | 08/06/2019 | 11/06/2019 | ML19310F56 | <strong>Loss of Feedwater Heating Results in Loss of Safety Function</strong><br /><i>Abstract:&nbsp;</i>On August 6, 2019, at 1335 hours, while performing feedwater heater alignments, a partial loss of feedwater heating occurred due to the isolation of the 5A and 6A feedwater heaters, resulting in lowering the temperature of feedwater to the reactor vessel by approximately 38 degrees F. This caused the Turbine First-Stage pressure to be outside of the normal calibration value, thereby changing instrumentation setpoints, and resulting in the INOPERABILITY of Reactor Protection System (RPS) instrumentation functions for Turbine Stop Valve Closure and Turbine Control Valve Fast Closure, End of Cycle Recirculation Pump Trip (EOC-RPT) instrumentation, and Control Rod Block instrumentation. <br /><br /> The Direct Cause is determined to be the continued rise of water level in the heater, after the emergency drain valve reached 100% demand, actuating the high-high isolation level switch. <br /><br /> The apparent cause was determined to be inadequate organizational communication following a change in the feedwater heater level control tuning strategy. A contributing cause was determined to be a lack of written guidance for Instrument and Control (I&C) technicians to perform the feedwater heater mode transfer successfully.<br /><br /> The increase in risk for this event is considered very small in accordance with the Regulatory Guidance. This event is reported in accordance with 10 CFR 50.73(a)(2)(v)(A) and 10 CFR 50.73(a)(2)(v)(D) as an event or condition that could have prevented the fulfillment of a safety function.
4452019001 | Comanche Peak 1, Comanche Peak 2 | 03/13/2019 | 04/25/2019 | ML19127A07 | <strong>LTOP Power Operated Relief Valve (PORV) Setpoint</strong><br /><i>Abstract:&nbsp;</i>On February 2, 2019 at 1500, Westinghouse reported that while reviewing the Low Temperature Overpressure (LTOP) system analysis of record (CN-SCS-04-100, Rev. 3) for areas of margin that could offset the increase in differential pressure required to support the Mechanical Stress Improvement Project (MSIP), errors were discovered. On March 9, 2019 an evaluation was completed that determined the Unit 2 LTOP system had been inoperable in the past for longer than allowed by Technical Specifications. Corrective actions include changing the LTOP PORV lift settings, on both Units 1 and 2 to meet the protection requirements of 10 CFR 50 Appendix G, Fracture Toughness Requirements.<br /><br /> All times listed in this report are Central Standard Time (CST).
4462019001 | Comanche Peak 2 | 03/02/2019 | 04/25/2019 | ML19127A14 | <strong>Manual Reactor Trip due To Feedwater Isolation Valve Closure</strong><br /><i>Abstract:&nbsp;</i>At 0317 on March 2, 2019, Comanche Peak Nuclear Power Plant (CPNPP) Unit 2 was manually tripped due to an unexpected closure of Feedwater Isolation Valve 2-04 and loss of Steam Generator 2-04 level control. All systems functioned as designed and the Unit 2 Auxiliary Feedwater Pumps started as designed due to low level in Steam Generator 2-04. There was no impact on Unit 1. <br /><br /> The cause of this event was the inadvertent actuation of a Feedwater circuit relay which caused Feedwater Isolation Valve 2-04 to close. Corrective actions include a site wide stand down on the event and suspension of activities involving relay checks. All times in this report are approximate and Central Standard Time unless noted otherwise.
4462019002 | Comanche Peak 2 | 05/14/2019 | 07/11/2019 | ML19199A03 | <strong>Automatic Actuation of Auxiliary Feedwater System</strong><br /><i>Abstract:&nbsp;</i>At 2151 on May 14, 2019, Comanche Peak Nuclear Power Plant (CPNPP):experienced a loss of the Stephenville 138 KV transmission line causing the Unit 2, 6900 V Safeguards buses (2EA1 and 2EA2) to transfer to the alternate off site power source and an actuation of Train A and Train B, Unit 2 blackout sequencers and an automatic start of both Unit 2 Motor Driven Auxiliary Feedwater pumps (MDAFWPs) and the Unit 2 Turbine Driven Auxiliary Feedwater pump (TDAFWP). The Emergency. Diesel Generators did not start since they were not required to start due to the successful bus transfer. There was no impact on Unit 1.<br /><br /> The cause of this event was a ground fault upstream of the Stephenville 138 KV transmission line causing undervoltage to CPNPP. Neither the upstream fault nor the Stephenville transmission line undervoltage were due to CPNPP equipment. The Unit 2 MDAFWPs and TDAFWP were stopped and returned to automatic. The off site source was recovered at 0256 on May 15, 2019. All times in this report are approximate and Central Daylight Time unless noted otherwise.
4552019001 | Byron 2 | 04/22/2019 | 06/20/2019 | ML19171A17 | <strong>Manual Actuation of Auxiliary Feedwater due to High Inboard Motor Bearing Temperature on Startup Feedwater Pump</strong><br /><i>Abstract:&nbsp;</i>On April 22, 2019 at 0850 hours, the non-safety related Start Up Feedwater (SUFW) pump [SJ] was started in support of plant heat up per Byron procedure 2BGP 100-1, "Plant Heatup". Engineering was performing monitoring and identified that the inboard motor bearing temperature of the SUFW pump was elevated and continuing to rise. Operations was notified and continued to monitor the bearing temperature in parallel with Engineering monitoring. At 1300 hours, the bearing reached 208 degrees F and the SUFW pump was secured to prevent damage to the motor. During this time, Operations was not able to begin the startup process for the non-safety related Motor Driven Feedwater (MDFW) pump because it was not filled and vented. Therefore, upon securing the SUFW pump, Operations entered Byron procedure 2BOA SEC-1, "Secondary Pump Trip" and performed the appropriate attachment for loss of Feedwater flow in Mode 3. The attachment required Operations to start an Auxiliary Feedwater (AF) [BA] pump. The motor driven AF pump [AFW Train A] was manually started at 1323 hours on April 22, 2019 and supplied water to the Steam Generators as designed. This resulted in ENS 54020 for manual actuation of the AF system. Filling and venting of the MDFW pump were completed and the pump was started at 1626 hours, allowing the motor driven AF pump to be shut down at 1632 hours on April 22, 2019.
4562019001 | Braidwood 1 | 09/23/2019 | 11/20/2019 | ML19324D92 | <strong>Unit Trip on Low Steam Generator Level due to Failure of a Controller on a Feedwater Regulating Valve</strong><br /><i>Abstract:&nbsp;</i>On September 23, 2019 at 1106 hours, Braidwood Unit 1 reactor tripped due to lowering steam generator water levels following closure of the 1B steam generator feed water (FW) regulating valve. <br /><br /> The cause of the event was an unexpected, premature internal failure of the FW regulating valve digital valve controller (DVC). Corrective actions completed included replacement of the failed DVC for the 1B FW regulating valve, as well as the DVCs for the remaining three Unit 1 steam generator FW regulating valves. Planned corrective actions include replacing the DVCs for Unit 2 Unit steam generator FW regulating valves at the next Unit 2 refueling outage. <br /><br /> This event is reportable in accordance with 10 CFR 50.73(a)(2)(iv)(A) for "Any event or condition that resulted in manual or automatic actuation of any of the systems listed in paragraph (a)(2)(iv)(B) of this section, ..." Specifically, for 1) 10 CFR 50.73(a)(2)(iv)(B)(1) for the "Reactor protection system (RPS) including: reactor scram or reactor trip," and 2) 10 CFR 50.73(a)(2)(iv)(B)(6) for the "PWR auxiliary or emergency feedwater system."
4582019001 | River Bend | 04/04/2019 | 06/03/2019 | ML19154A07 | <strong>Initiation of Standby Service Water due to Inadequate Monitoring of System Parameters During Maintenance Activities</strong><br /><i>Abstract:&nbsp;</i>On April 4, 2019, the operating Normal Service Water pumps tripped on low suction pressure, resulting in the initiation of the Standby Service Water System. The low suction pressure condition was caused by inadequate monitoring of system parameters during operation in an off-normal system configuration. After the event, both the Normal and Standby Service Water Systems were returned to their normal configurations. This event did not constitute a loss of Shut Down Cooling. This event was of minimal significance to the health and safety of the public.
4582019002 | River Bend | 04/26/2019 | 08/29/2019 | ML19241A50 | <strong>Reactor Coolant Pressure Boundary Leakage due to Contaminates Deposited on External Pipe Surface After Legacy Adhesive Spill</strong><br /><i>Abstract:&nbsp;</i>Through-wall leakage in the Safety Related Standby Liquid Control (SLC) system piping segment was identified and confirmed by Non-Destructive Evaluation personnel during a system leakage examination. The identified leakage from this section of piping was at a rate of 1 drop every 1 to 2 minutes. The leak was discovered while conducting pressure test activities. At the time of discovery, the station was conducting refueling activities in Mode 5.<br /><br /> The section of piping affected was cut out and replaced in accordance with ASME Section XI IWA-4000. The required elements for examination/material as required in the ASME Code were followed during the replacement of the affected segment of piping. After the required examinations, the pipe was returned to service. The leak was caused by Transgranular Stress Corrosion Cracking due to the presence of aggressive chemical species and crack morphology. A visual external surface inspection was performed which found no evidence of contaminants on any additional SLC system piping.
4582019003 | River Bend | 05/31/2019 | 07/30/2019 | ML19211A85 | <strong>Manual Reactor Scram Initiated in Response to Loss of Feedwater due to Abnormal Plant Configuration</strong><br /><i>Abstract:&nbsp;</i>On May 31, 2019, the Reactor was operating at 32% power with a planned shutdown in progress. The 'A' Low Pressure Feedwater Heater (LPFH) string was isolated due to level control issues in one of the heaters. The process of securing one of the Reactor Feedwater Pumps (FWP) resulted in higher than anticipated flow through the 'B' LPFH string. The high flow condition caused water level to rise in one of the 'B' LPFHs which resulted in automatic isolation and bypass of the LPFHs. The LPFH string isolation restricted supply flow to the operating FWPs resulting in an automatic trip of the pumps and a loss of all feedwater. At 23:45 a manual Reactor Scram was inserted. Reactor Core Isolation Cooling (RCIC) was manually initiated for Reactor water level control. The 'C' FWP was restarted and Reactor water level control was transferred from RCIC to the 'C' FWP. The LPFH system configuration was not changed and approximately 43 minutes after the Scram, the 'C' FWP automatically tripped due to low suction pressure. Reactor water level lowered to level 3 causing a second Reactor Protection System actuation. Operators reestablished flow through the 'B' LPFH string and restarted the 'A' FWP restoring Reactor water level to the normal band. Corrective Actions are planned to revise procedures to accurately reflect the limitations of the configuration which lead to this event.
4582019004 | River Bend | 10/24/2019 | 12/23/2019 | ML19357A22 | <strong>Potential Loss of Safety Function for all ADS (Automatic Depressurization System) Valves</strong><br /><i>Abstract:&nbsp;</i>On 24 October 2019, the Automatic Depressurization System (ADS) air supply header pressure began to lower. This header provides air for the automatic or manual operation of the Safety Relief Valves (SRV's) from the Control Room. A loss of header pressure was caused by leaking Air Operated Valves (AOV's) on the 'B' Train Dryer of ADS which was worked on during a scheduled maintenance window. When a tagout was removed on the 'B' Train ADS AOV's, header pressure began to lower. Attempting to control header pressure, the 'A' Train ADS Safety Vent Valve (SVV) Compressor (SVV-C4A) tripped on a thermal overload. This trip was due to excessive start/stops caused by the air leak on the 'B' Train Dryer ADS AOV's. During this time the 'B' Train compressor, SVV-C48, was still tagged out for maintenance. The tagout for SVV-C48 was then removed and the compressor started, but header pressure continued to lower. Maintenance personnel were dispatched to assist Operations to investigate why header pressure continued to lower. SVV-C4A was reset and started and SVV-C4B secured. ADS header pressure then recovered to its normal operating pressure. <br /><br /> Seven SRV's were declared inoperable due to ADS header pressure lowering below the Technical Specification limit of 131 psig. This required entry into a 12-hour shutdown LCO. Approximately 40 minutes after the LCO was entered, header pressure recovered and the LCO was exited.
4612019001 | Clinton 1 | 05/22/2019 | 11/01/2019 | ML19322A10 | <strong>Main Feed Breaker Failed to Close During Bus Shift</strong><br /><i>Abstract:&nbsp;</i>On May 22, 2019, at 0925 CDT, at approximately 98.4% power while attempting to transfer 4160V bus 1A1 to the Reserve Auxiliary Transformer (RAT) (main) from the Emergency Reserve Auxiliary Transformer (ERAT) (reserve), RAT 4160V bus 1A1 main feed breaker 1AP07EK failed to close and immediately indicated tripped. A walkdown of feed breaker 1AP07EK showed no abnormal indications or relay flags. Feed breaker 1AP07EK was replaced and tested satisfactory. Initial troubleshooting identified that the latch check switch breaker closure permissive was not made up: As this permissive makes up following breaker closure it has been determined that feed breaker 1AP07EK was inoperable since April 17, 2019. The cause of the breaker failure was determined to be establishment of a breaker preventive maintenance strategy which was beyond the capability of the Molykote BR-2 lubricant used in the breaker. Changes to DHP Breaker preventive maintenance frequencies will be implemented to ensure that lubrication periodicities support the effective life of the lubricant. In addition, DHP Breaker maintenance and refurbishment procedures will be revised to incorporate use of Molykote G-4700 grease in place of Molykote BR-2. This event is reportable in accordance with 10 CFR 50.73(a)(2)(i)(B) as, "any operation or condition which was prohibited by the plant's Technical Specifications."
4612019002 | Clinton 1 | 08/03/2019 | 10/01/2019 | ML19277E36 | <strong>Turbine Driven Reactor Feed Pump Hydraulic Control Failure Results in Automatic SCRAM</strong><br /><i>Abstract:&nbsp;</i>On August 3, 2019, at 0226 CDT, while operating at approximately 98% power, the Turbine Driven Reactor Feed Pump (TDRFP) B horizontal hardware connection to the Linear Variable Differential Transformer (LVDT) failed causing loss of feedback to the feedwater control system. Flow from TDRFP B decreased while TDRFP A flow increased and reactor level decreased to the scram setpoint, which caused an automatic Reactor Protection System (RPS) scram. All control rods fully inserted. The reactor water Level 2 setpoint was reached and High Pressure Core Spray (HPCS), Reactor Core Isolation Cooling (RCIC), Division 3 diesel generator, Standby Gas Treatment Systems A and B, and all safety related shutdown service water pumps started as expected. RCIC and HPCS injected as expected. All Level 2 containment isolation valves closed as expected. As a result of automatic isolation of the containment ventilation system, the Primary Containment to Secondary Containment and the Drywell to Primary Containment differential pressure limits were exceeded. The cause of the event was the design of the horizontal connecting hardware to the TDRFP B operating cylinder position LVDT was not adequate to withstand cyclic loading. The failed LVDT was replaced on TDRFP B, along with associated horizontal connecting hardware. A design change will be developed and installed to strengthen the connecting hardware to the TDRFP B operating-cylinder LVDT such that it is adequate to withstand cyclic loading. This event is reportable under 10 CFR 50.73(a)(2)(iv)(A), 10 CFR 50.73(a)(2)(v)(D), 10 CFR 50.73(a)(2)(ii)(B), and 10 CFR 50.73(a)(2)(v)(C).
4612019003 | Clinton 1 | 09/16/2019 | 11/14/2019 | ML19333B81 | <strong>Reactor Water Cleanup System Differential Flow Instrumentation Inoperable</strong><br /><i>Abstract:&nbsp;</i>On 09/16/19, at 0817 CDT, at approximately 0% power during shutdown for refueling outage C1R19, the Division 1 and Division 2 Reactor Water Cleanup (RT) system differential flow instrumentation was declared inoperable due to failing downscale caused by flashing in the sensing lines that occurred during reactor cooldown. The Division 1 and 2 RT differential flow instrumentation were declared inoperable in accordance with Technical Specification (TS) 3.3.6.1. The cause of this event was unit shutdown procedures were not optimized to increase subcooling in the RT system during reactor cooldown. The system alignment was changed in accordance with procedures to increase subcooling and indication was restored by 0852 CDT on 09/16/19. Procedures governing unit shutdown will be revised to increase subcooling in the RT system during reactor cooldown to reduce the likelihood of flashing in the sensing lines. This condition met the reportability requirements of 10 CFR 50.73(a)(2)(v)(D), any event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident.
4612019004 | Clinton 1 | 10/02/2019 | 01/29/2020 | ML20031D05 | <strong>Safety Relief Valve Wiring Issue Results in Condition Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On October 2, 2019, at 0200 CDT, at 0% power with the unit shutdown for refueling outage C1R19, while performing Safety Relief Valve (SRV) testing, SRV 1B21-F041B did not open upon demand using the Division 1 Main Control Room (MCR) switch. Further investigation identified that the Division 1 MCR switch for SRV 1621-F041B opened SRV 1B21- F051B and the Division 1 MCR switch for SRV 1B21-F051B opened SRV 1B21-F041B. Initial investigation determined this condition was a Division 1 SRV wiring issue that occurred during refueling outage C1R17 in May 2017. The causes of this event were determined to be imprecise work instructions combined with performance of multiple actions within a single work step in conjunction with lack of adequate signage on SRVs. The Division 1 SRV 1621-F041B and SRV 1B21-F051B wiring was corrected and a post-maintenance test completed. In addition, work order instructions will be revised to incorporate more robust verification practices and SRV signage will be added during the next refueling outage. This condition rendered the Automatic Depressurization System (ADS) function for SRV 1B21-F041B inoperable since May 2017. As a result, Technical Specifications Limiting Condition for Operation 3.5.1, Emergency Core Cooling System - Operating, Action E (One ADS valve inoperable), which requires an inoperable ADS valve be restored within 14 days, was not met. Therefore, the condition described in this Licensee Event Report is reportable under 10 CFR 50.73(a)(2)(i)(B), any operation or condition which was prohibited by the plant's Technical Specifications.
4822019001 | Wolf Creek | 05/24/2019 | 07/18/2019 | ML19281C06 | <strong>Loss of Startup Transformer Results in Emergency Diesel Generator Actuation</strong><br /><i>Abstract:&nbsp;</i>On May 24, 2019, at 1310 Central Daylight Time (CDT), while operating in Mode 1 at 100% power, a trip of the startup transformer resulted in a loss of offsite power to the safety-related 4.16 kV NB002 bus. This caused the actuation of the "B" Emergency Diesel Generator as well as a valid auxiliary feedwater actuation signal.<br /><br /> The presence of recently deceased birds in the area, along with the pattern of arc strikes, indicated that the probable cause of the startup transformer trip was a fault caused by bird activity in the vicinity of the secondary side bushings. Further inspection revealed that birds had been nesting within the bushing covers previously installed to prevent faults due to rodents. This condition was previously reported on May 24, 2019 (ENS 54087) in accordance with 10 CFR 50.72(b)(3)(Iv)(A) for a valid specified system actuation. <br /><br /> The startup transformer was restored and declared operable on May 27, 2019, at 1258 CDT. There was no impact to the health and safety of the public as a result of this event. All safety-related equipment performed as expected in response to the loss of offsite power to the NB002 bus.
4822019002 | Wolf Creek | 08/19/2019 | 10/14/2019 | ML19295D72 | <strong>Emergency Diesel Generator Inoperable due to Temperature Control Valve Failure</strong><br /><i>Abstract:&nbsp;</i>On August 19, 2019, at 0223 Central Daylight Time (CDT), during performance of its monthly operability run, the 'A' Emergency Diesel Generator (EDG) was declared inoperable due to high intercooler water temperature. Condition B of Technical Specification (TS) Limiting Condition for Operation (LCO) 3.8.1, "AC Sources - Operating" was entered at this time. At the time of the event, the unit was in Mode 1 at 100 percent power.<br /><br /> Investigation revealed that the reason for the high intercooler water temperature was the failure of the thermostatic "power pills" in the intercooler heat exchanger temperature control valve. The failed power pills caused the valve to fail in the bypass position, thereby reducing cooling flow through the intercooler heat exchanger. It was determined that the power pills most likely failed prematurely due to accelerated aging induced by annual shelf life testing. Due to the probable cause of failure, there is firm evidence that the condition existed following the previous successful run of the 'A' EDG on July 15, 2019, which is longer than the 72-hour completion time required by TS LCO 3.8.1. In addition, the 'B' EDG was out of service for maintenance for approximately 2 days during this period, so this was also a condition that could have prevented fulfillment of a safety function.<br /><br /> The failed power pills were replaced and the 'A' EDG was returned to service on August 20, 2019, at 0500 CDT. Condition B of TS LCO 3.8.1 was exited at this time. There was no impact to the health and safety of the public as a result of this event.
4832019001 | Callaway | 04/17/2019 | 11/07/2019 | ML19312B66 | <strong>Unplanned Loss of Switchyard Bus B Results in System Actuation</strong><br /><i>Abstract:&nbsp;</i>On April 17, 2019 at approximately 0137 CDT, a valid actuation of the "A" emergency diesel generator (EDG) at the Callaway plant occurred due to inadvertent tripping of the "B" switchyard bus. The plant was in No Mode (defueled) when the switchyard 345-kV main generator output breaker (MDV53) was closed to backfeed the unit auxiliary transformer. MDV53 immediately reopened due to a ground located on a set of current transformers that set up an unwanted path for current to flow between the protection circuits for switchyard breakers MDV53 and MDV55. De-energization of the "B" switchyard bus resulted in de-energization of two transformers in the switchyard circuit connection to the 4.16-kV NB01 safety bus. The loss of voltage on the NB01 bus triggered the "A" EDG actuation.<br /><br /> The following root causes were identified: <br /> 1. Ineffective management by the Transmission Substations department of a design scope change introduced a design error, i.e., an extraneous jumper that enabled the unwanted current path to the breaker protection circuits. <br /> 2. Engineering supervision assumed the Transmissions Substations design process included an independent review, and thus, an independent review was not requested. <br /> Corrective actions to prevent recurrence include:<br /> 1. Revising the Engineering Design Quality Review Process procedure to require an independent review of Callaway specific schematic and wiring diagrams. <br /> 2. Establishing procedural requirements for reviewing the design review documentation from Transmission Substations. <br /><br /> The automatic actuation of the emergency diesel generator was a valid actuation and is reportable in accordance with 10 CFR 50.73(a)(2)(iv)(A). There was no impact to the health and safety of the public as a result of this event. Systems responded as expected (i.e., per design) in response to de-energization of the "B" switchyard bus.
4832019002 | Callaway | 05/11/2019 | 07/10/2019 | ML19191A23 | <strong>Mode 4 Entry with Inoperable Auxiliary Building Pressure Boundary</strong><br /><i>Abstract:&nbsp;</i>On May 11, 2019, during mode ascension exiting from Refueling Outage 23, Callaway Plant entered Mode 4 from Mode 5 while not in compliance with Technical Specification 3.7.13, "Emergency Exhaust System (EES)." Specifically, a door that is a part of the Auxiliary Building pressure boundary was not closed prior to Mode 4 entry. This mode transition was not in compliance with the requirements of LCO 3.0.4. This event was previously reported as an event or condition that could have prevented fulfillment of a safety function per ENS 54061, but that notification is being retracted.<br /><br /> This event was caused by the failure to initiate equipment out of service tracking when a pressure boundary door was impaired. Callaway administrative procedures for control of hazard barriers will be revised to ensure that mode change restrictions associated with hazard barrier impairment are appropriately tracked.
4832019003 | Callaway | 05/16/2019 | 07/15/2019 | ML19196A09 | <strong>Reactor Trip due to Source Range Hi-Flux</strong><br /><i>Abstract:&nbsp;</i>At 2303 on May 16, 2019, Callaway plant tripped during reactor startup due to a Source Range (SR) Hi-Flux trip signal, which resulted in reactor protection system and auxiliary feedwater system actuations. The control room operators failed to block the SR Hi-Flux trip prior to reaching the setpoint of 10E5 counts per second. All plant systems responded as expected. <br /><br /> Analysis identified the following causes and contributing causes: <br /> 1. The Reactor Operators did not have an appropriate strategy for monitoring SR detector count rate relative to other critical parameters that were being monitored. <br /> 2. The Control Room Supervisor was also fulfilling the role of Reactivity Management Senior Reactor Operator but became distracted from this primary function. The reactor startup procedure required going to several attachments and performing lower priority steps prior to blocking the SR Hi-Flux trip, thus delaying performance of this action. <br /> 3. The reactor startup procedure did not support expeditious action to block the SR Hi-Flux trip. <br /> 4. Operators were not aware of the time constraints when blocking the SR Hi-Flux trip. <br /><br /> Corrective actions include revising the reactor startup procedure to ensure the correct monitoring behaviors and revising the standard to require an additional Senior Reactor Operator who can focus solely on reactivity control.
4832019005 | Callaway | 07/17/2019 | 02/06/2020 | ML20038A18 | <strong>Inoperability of CREVS B Train</strong><br /><i>Abstract:&nbsp;</i>On July 17, 2019, the thermal overload relay for control room filtration fan B tripped when the fan was secured from surveillance testing. This resulted in the B train of the Control Room Emergency Ventilation System (CREVS) being declared inoperable at 2134 CDT, at which time Condition A of TS 3.7.10 was entered. The trip occurred approximately 4 hours and 48 minutes after the fan was started. The CREVS B train was restored to operable status on July 19, 2019 at 1710 CDT after the thermal overload relay was adjusted to prevent inadvertent tripping during normal operation. <br /><br /> A modification to replace the motor control center bucket for control room filtration fan B was installed June 18, 2019. The thermal overload settings and the thermal overload device used in this modification were in accordance with electrical design calculation NG-23 which used design documents specifying a 3.15 brake horsepower (BHP). The calculation, however, was based on design documents specifying a brake horsepower value that had not been updated to reflect the results of testing performed on the fan by its manufacturer prior to installation at the Callaway Plant (i.e., during plant construction). This resulted in the establishment of a thermal overload relay setting too close to actual fan performance. Past operability was evaluated and could not be supported from the time the modification was installed to the time when the control room filtration fan tripped. <br /><br /> This condition is required to be reported pursuant to 10 CFR 50.73(a)(2)(i)(B) as a condition or operation prohibited by the Technical Specifications. <br /><br /> The cause of the event was the fan motor current exceeding the setpoint of the thermal overload relay. Corrective actions include correcting the applicable design documents.
4832019006 | Callaway | 05/10/2019 | 10/22/2019 | ML19295D51 | <strong>Unrecognized Inoperability of Boron Dilution Mitigation System (BDMS) Train 'B'</strong><br /><i>Abstract:&nbsp;</i>On August 23, 2019, it was discovered that Flux Doubling Test Bypass Switch S604 had failed to close when it was placed in its Normal position at 1543 on May 10, 2019. This failure would have prevented train 'B' of the Boron Dilution Mitigation System from performing its required safety function when required to be Operable in accordance with Technical Specification (TS) 3.3.9, "Boron Dilution Mitigation System (BDMS)," for the periods from 1543 on May 10, 2019 to 2259 on May 16, 2019, and from 2301 on May 16, 2019 to 1212 on May 17, 2019. Due to the unrecognized inoperability of BDMS train 'B', the TS 3.3.9 Limiting Condition of Operation (LCO) requiring two trains of BDMS to be Operable was not met during these periods, and the applicable Required Actions were not completed within their specified Completion Times. In addition, Mode changes were performed during these periods of BDMS train 'B' inoperability without satisfying the provisions of TS LCO 3.0.4.a, thereby resulting in a violation of TS LCO 3.0.4. Following discovery of the failure on August 23, 2019, remedial actions were taken to close the affected switch in its Normal position.<br /><br /> Failure of the switch contacts to close on May 10, 2019 has been attributed to either a stack misalignment or mechanical binding. Corrective actions to prevent recurrence include establishing requirements to verify continuity through the Flux Double Test Bypass Switches for both BDMS trains when the switches are manipulated, and to replace the affected switch at the next available opportunity.
4982019001 | South Texas 1 | 02/27/2019 | 05/30/2019 | ML19150A72 | <strong>Unit 1 Condition Prohibited by Technical Specifications due to Inoperable Essential Cooling Water Pump</strong><br /><i>Abstract:&nbsp;</i>On February 27, 2019, Essential Cooling Water (ECW) Pump 1B experienced a lack of packing leak-off that resulted in excessive heat-up of the packing. Smoke was observed at the packing gland and the pump was secured and declared inoperable. A similar lack of packing leak-off condition on ECW Pump 1B had been observed on February 18, 2019 following replacement of the pump and motor. A successful post maintenance run was conducted with additional water (external source) used to cool the stuffing box. On February 19, 2019, the pump was declared operable and was secured for approximately 9 days and 23 hours. <br /><br /> Based on a review of the event conditions, reasonable assurance that the pump could have met its design basis requirements after February 19, 2019, cannot be assured. Therefore, the pump is considered to have been inoperable for longer than the 7 days allowed by the associated Technical Specification. The cause of this event was determined to be less than adequate procedure guidance. Maintenance procedures did not provide sufficient warning or guidance to address packing tolerances to ensure leak-off upon start-up or actions to take for a less than adequate packing leak-off. Maintenance procedures will be revised to address this concern.
4982019002 | South Texas 1 | 07/30/2019 | 11/27/2019 | ML19331A03 | <strong>Condition Prohibited by Technical Specifications and Loss of Safety Function due to Inoperable Reactor Head Vent Throttle Valves</strong><br /><i>Abstract:&nbsp;</i>On December 31, 2018, South Texas Project (STP) Unit 1 reactor vessel head vent throttle valve (RHVTV) 'A' was declared INOPERABLE. On July 30, 2019, STP Unit 1 RHVTV 'B' was declared INOPERABLE. Technical Specifications requires one RHVTVs to be OPERABLE. With two INOPERABLE RHVTVs, entry into a 30-day Technical Specification shutdown ACTION statement is required. The RHVTVs could have been prevented from fulfilling a safety function needed to maintain the reactor in a safe shutdown condition, mitigating a possible condition of inadequate core cooling or impaired natural circulation. Operations did not recognize the loss of safety function and did not request a reportability review as required by station procedure. <br /><br /> On July 31, 2019, following additional investigation, STP Nuclear Operating Company determined that RHVTV 'B' had been INOPERABLE since June 24, 2019. Therefore, the RHVTV was INOPERABLE for longer than the Technical Specification 30-day shutdown ACTION statement, resulting in a condition prohibited by Technical Specifications. On August 1, 2019, RHVTV 'B' was declared OPERABLE. On August 15, 2019, RHVTV 'A' was declared OPERABLE. The event did not result in any offsite release of radioactivity or increase of offsite dose rates, and there were no personnel injuries or damage to any safety-related equipment associated with this event. Therefore, there was no adverse effect on the health and safety of the public.
4992019001 | South Texas 2 | 09/03/2019 | 11/04/2019 | ML19308B38 | <strong>Equipment Clearance Order Error Leads to Loss of Primary Containment Integrity</strong><br /><i>Abstract:&nbsp;</i>On September 5, 2019, it was discovered that an Equipment Clearance Order (ECO) to replace a degraded containment isolation valve on the outside of the Reactor Containment Building (RCB) had an error that resulted in a violation of Technical Specifications. The ECO incorrectly opened a test connection between the containment wall and a containment isolation valve inside the RCB that was required to be closed for Technical Specification compliance. When the degraded containment isolation valve on the outside of containment was removed, a leakage path out of containment was established. This resulted in a loss of one of the three fission product barriers and a violation of two Technical Specifications. Once the ECO error was recognized, Operations corrected the valve lineup to bring Unit 2 back into compliance with Technical Specifications. The root cause of the event was personnel error related. The two Licensed Senior Reactor Operators involved in the technical review and approval of the ECO failed to recognize at-risk behaviors and apply appropriate human performance tools. Corrective actions planned include procedure changes, as well as modifications to the software that controls the ECO process.
4992019002 | South Texas 2 | 10/24/2019 | 12/19/2019 | ML19353C81 | <strong>Incorrect Sequencer Part Replacement Leads to Undervoltage Signal and Valid Actuation of Emergency Diesel Generator</strong><br /><i>Abstract:&nbsp;</i>During a maintenance activity on October 24, 2019, a 24V opto-isolator module was installed in the Unit 2 C-Train Load Sequencer (Sequencer 2C) instead of the required 125V module. Due to the installation and subsequent failure of this incorrect part, Sequencer 2C initiated an electrical bus strip signal and the C-Train 4.16kV bus was deenergized. Consequently, an undervoltage signal was sent to Sequencer 2C which then sent a valid Engineered Safety Features (ESF) actuation signal to Emergency Diesel Generator (EDG) 23. The C-Train ESF loads were shed but EDG 23 did not automatically start because it had been placed in Pull-To-Stop to support Sequencer 2C maintenance activities. EDG was taken out of Pull-To-Stop by the Control Room staff to allow it to auto start and load the bus. This event is reportable as an event that resulted in the automatic actuation of an emergency AC electrical power system. Corrective actions planned include work guideline changes, personnel briefings, and updates to the STP master parts list.<br /><br /> The event did not result in any offsite release of radioactivity or increase of offsite dose rates and there were no personnel injuries or damage to any safety-related equipment associated with this event. Therefore, there was no adverse effect on the health and safety of the public.
5282019001 | Palo Verde 1 | 03/31/2019 | 05/29/2019 | ML19150A32 | <strong>Emergency Core Cooling System Valve Leakage Resulting in an Unanalyzed Condition</strong><br /><i>Abstract:&nbsp;</i>On March 31, 2019, at approximately 20:06 Mountain Standard Time (MST), PVNGS Unit 1 Shift Manager was informed that leakage at static system pressure from the "A" Train Emergency Core Cooling System (ECCS) was measured at approximately 100 milliliters per minute through a High Pressure Safety Injection (HPSI) system drain valve. This value exceeded the Large Break Loss of Coolant Accident (LOCA) analysis value of 3000 milliliters per hour (mL/hour), pressurized ECCS leakage from sources outside of containment. <br /><br /> At 02:30 MST on April 01, 2019, the valve was flushed and the leakage was reduced below the analysis value to 600 mL/hour with the system at static pressure. Troubleshooting efforts continued and the HPSI system drain valve was replaced on April 18, 2018. A pressurized ECCS leak test that was completed on April 23, 2019, confirming zero leakage from the valve. <br /><br /> The apparent cause was the connection of ECCS drain valves located outside of containment to an open-ended drain header that does not limit the potential radiological consequences of seat leakage. A design change is planned to install pipe caps on HPSI system drain valves. <br /><br /> No similar conditions have been reported by PVNGS in the past three years.
5292019001 | Palo Verde 2 | 08/16/2019 | 10/11/2019 | ML19284D67 | <strong>Automatic Actuation of the Reactor Protection System Resulting from a Loss of Reactor Coolant Pumps</strong><br /><i>Abstract:&nbsp;</i>On August 16, 2019, at approximately 0821 Mountain Standard Time, an automatic reactor trip of PVNGS Unit 2 occurred when the Reactor Protection System generated trips on all four channels for low departure from nucleate boiling ratio and high local power density due to the loss of power to all four Reactor Coolant Pumps. All control element assemblies fully inserted into the reactor core. A Main Steam Isolation Signal was manually actuated due to the loss of main condenser cooling water. This required manual actuation of the auxiliary feedwater and essential spray pond systems. <br /><br /> When the main generator is connected to the switchyard grid, a generator under frequency condition is the only electrical fault that opens the output breakers without tripping the turbine and providing the electrical circuit logic needed to initiate a fast bus transfer of PVNGS non-class 1E 13.8 kilovolt (kV) loads. <br /><br /> The direct cause of the reactor trip was attributed to the opening of main generator output breakers inside the Salt River Project (SRP) switchyard. The output breakers opened due to an invalid trip output signal initiated from a Schweitzer Engineering Laboratory relay (SEL-387) within the SRP switchyard protection system. The SEL-387 and cable running from the Unit 2 main generator protection cabinet to the SRP interface cabinet at the switchyard boundary were replaced. Subsequent testing was unable to identify a failure mode. SRP will be implementing a modification to the relay tripping scheme to provide redundancy that will provide required protection to the switchyard while eliminating a plant trip vulnerability. <br /><br /> No previous similar events have been reported by PVNGS in the last 3 years.